| IBC A-2 Type IA | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |
| --- | --- | --- | --- |
|  | Unlimited | Unlimited | Unlimited |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | Unlimited | n/a | n/a | Unlimited |
|  | Basements: Unlimited area |
|  | Specific Fire Resistance: Structural frame = 3 hours; 2 hours (supporting roof only) Bearing walls = 3 hours (exterior); 3 hours (interior); 2 hours (interior, supporting roof only) Interior nonbearing walls & partitions = NR Floors = 2 hours Roofs = 1½ hours; NR or fire-retardant treated wood OK if ≥ 20’ above floor immediately below Fire barriers between fire areas = 2 hours Fire walls = 3 hours (based on occupancy) Corridors = 1 hour (unsprinklered), 0.5 hours (sprinklered) @ occupant load > 30 4-story unenclosed escalator or non-MOE stair allowed |
|  | Specific Fire Alarm Threshold: Manual system @ occupant load ≥ 300 |
|  | Specific Sprinkler Threshold: All A-2 occupancies where fire area > 5000 sq ft; OR occupant load > 100; OR the A-2 is not on the floor of exit discharge Required on all floors between the A-2 and the floor of exit discharge |
|  | Podium Buildings: n/a |

| UBC A-2.1 Type I-F.R. | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |
| --- | --- | --- | --- |
|  | Unlimited | Unlimited | Unlimited |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | Unlimited | n/a | n/a | Unlimited |
|  | Basements: Unlimited area |
|  | Specific Fire Resistance: Structural frame = 3 hours; NR or heavy timber OK for roofs if ≥ 25’ above floor Bearing walls = 4 hours (exterior); 3 hours (interior) Interior nonbearing walls & partitions = 1 hour, fire-retardant treated wood OK Floors = 2 hours Roofs = 2 hours; NR or fire-retardant treated wood OK if ≥ 25’ above floor Area separation walls = 4 hours (based on type of construction) Corridors = 1 hour, triggered by travel distance or >1 intervening room Hallways = non-rated, treated as intervening room |
|  | Specific Fire Alarm Threshold: All A-2.1 occupancies, per Fire Code |
|  | Specific Sprinkler Threshold: Drinking establishments > 5000 sq ft A-2.1’s in basements > 1500 sq ft |
|  | Podium Buildings: n/a |

| IBC A-2 Type IB | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |
| --- | --- | --- | --- |
|  | 11 stories, 160’ | 12 stories, 180’ | 12 stories, 180’ |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | Unlimited | n/a | n/a | Unlimited |
|  | Basements: Unlimited area |
|  | Specific Fire Resistance: Structural frame = 2 hours; 1 hour (supporting roof only) Bearing walls = 2 hours (exterior); 2 hours (interior); 1 hour (interior, supporting roof only) Interior nonbearing walls & partitions = NR Floors = 2 hours Roofs = 1 hour; heavy timber OK; NR or fire-retardant treated wood OK if ≥ 20’ above floor immediately below; Fire barriers between fire areas = 2 hours Fire walls = 3 hours (based on occupancy) Corridors = 1 hour (unsprinklered), 0.5 hours (sprinklered) @ occupant load > 30 4-story unenclosed escalator or non-MOE stair allowed |
|  | Specific Fire Alarm Threshold: Manual system @ occupant load ≥ 300 |
|  | Specific Sprinkler Threshold: All A-2 occupancies where fire area > 5000 sq ft; OR occupant load > 100; OR the A-2 is not on the floor of exit discharge Required on all floors between the A-2 and the floor of exit discharge |
|  | Podium Buildings: Separate bldgs for area & number of stories; A’s occ ld < 300; height measured fr grade plane |

| UBC A-2.1 Type II-F.R. | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |
| --- | --- | --- | --- |
|  | 4 stories, 160’ | 5 stories, 160’ | 5 stories, 160’ (4 stories, 160’ if spr’s used for area) |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 29,900 | 2 | 2 | 239,200 (119,600 if spr’s used for stories) |
|  | Basements: 59,800 (unsprinklered); 179,400 (sprinklered) |
|  | Specific Fire Resistance: Structural frame = 2 hours; NR or heavy timber OK for roofs if ≥ 25’ above floor Bearing walls = 4 hours (exterior); 2 hours (interior); 2 hours (interior, supporting roof only) Interior nonbearing walls & partitions = 1 hour Floors = 2 hours Roofs = 1 hour; NR or fire-retardant treated wood OK if ≥ 25’ above floor Area separation walls = 4 hours (based on type of construction) Corridors = 1 hour, triggered by travel distance or >1 intervening room Hallways = non-rated, treated as intervening room |
|  | Specific Fire Alarm Threshold: All A-2.1 occupancies, per Fire Code |
|  | Specific Sprinkler Threshold: Drinking establishments > 5000 sq ft A-2.1’s in basements > 1500 sq ft |
|  | Podium Buildings: NP |
| IBC A-2 Type IIA | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |
|  | 3 stories, 65’ | 4 stories, 85’ | 4 stories, 85’ |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 15,500 | 1.75 | 2 | 174,375 |
|  | Basements: 27,125 (unsprinklered); 73,625 (sprinklered) |
|  | Specific Fire Resistance: Structural frame = 1 hour Bearing walls = 1 hour (exterior or interior) Interior nonbearing walls & partitions = NR Floors = 1 hour Roofs = 1 hour; heavy timber OK; NR or fire-retardant treated wood OK if ≥ 20’ above floor immediately below; Fire barriers between fire areas = 2 hours Fire walls = 2 hours (based on occupancy, type of construction) Corridors = 1 hour (unsprinklered), 0.5 hours (sprinklered) @ occupant load > 30 4-story unenclosed escalator or non-MOE stair allowed |
|  | Specific Fire Alarm Threshold: Manual system @ occupant load ≥ 300 |
|  | Specific Sprinkler Threshold: All A-2 occupancies where fire area > 5000 sq ft; OR occupant load > 100; OR the A-2 is not on the floor of exit discharge Required on all floors between the A-2 and the floor of exit discharge |
|  | Podium Buildings: Separate bldgs for area & number of stories; A’s occ ld < 300; height measured fr grade plane |

| UBC A-2.1 Type II-1 hour | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |
| --- | --- | --- | --- |
|  | 2 stories, 65’ | 3 stories, 65’ | 3 stories, 65’ (2 stories, 65’ if spr’s used for area) |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 13,500 | 2 | 2 | 108,000 (54,000 if spr’s used for stories) |
|  | Basements: 27,000 (unsprinklered); 81,000 (sprinklered) |
|  | Specific Fire Resistance: Structural frame = 1 hour Bearing walls = 1 hour (exterior or interior) Interior nonbearing walls & partitions = 1 hour Floors = 1 hour Roofs = 1 hour; NR or fire-retardant treated wood OK if ≥ 25’ above floor Area separation walls = 2 hours (based on type of construction) Corridors = 1 hour, triggered by travel distance or >1 intervening room Hallways = non-rated, treated as intervening room A occ's w/ aggregate occ ld ≥ 1000 NP in basement |
|  | Specific Fire Alarm Threshold: All A-2.1 occupancies, per Fire Code |
|  | Specific Sprinkler Threshold: Drinking establishments > 5000 sq ft A-2.1’s in basements > 1500 sq ft |
|  | Podium Buildings: NP |

| IBC A-2 Type IIB | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |
| --- | --- | --- | --- |
|  | 2 stories, 55’ | 3 stories, 75’ | 3 stories, 75’ |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 9,500 | 1.75 | 2 | 106,875 |
|  | Basements: 16,625 (unsprinklered); 45,125 (sprinklered) |
|  | Specific Fire Resistance: Structural frame = NR Bearing walls = NR (exterior or interior) Interior nonbearing walls & partitions = NR Floors = NR Roofs = NR, heavy timber OK Fire barriers between fire areas = 2 hours Fire walls = 2 hours (based on occupancy, type of construction) Corridors = 1 hour (unsprinklered), 0.5 hours (sprinklered) @ occupant load > 30 4-story unenclosed escalator or non-MOE stair allowed |
|  | Specific Fire Alarm Threshold: Manual system @ occupant load ≥ 300 |
|  | Specific Sprinkler Threshold: All A-2 occupancies where fire area > 5000 sq ft; OR occupant load > 100; OR the A-2 is not on the floor of exit discharge Required on all floors between the A-2 and the floor of exit discharge |
|  | Podium Buildings: Separate bldgs for area & number of stories; A’s occ ld < 300; height measured fr grade plane |

| UBC A-2.1 Type II-N | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |
| --- | --- | --- | --- |
|  | ’ |  | NP |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  |  |  |  | NP |
|  | Basements: NP |
|  | Specific Fire Resistance: |
|  | Specific Fire Alarm Threshold: |
|  | Specific Sprinkler Threshold: |
|  | Podium Buildings: NP |

(UBC A-2.1 occupancies not allowed in non-rated buildings)

| IBC A-2 Type IIIA | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |
| --- | --- | --- | --- |
|  | 3 stories, 65’ | 4 stories, 85’ | 4 stories, 85’ |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 14,000 | 1.75 | 2 | 157,500 |
|  | Basements: 24,500 (unsprinklered); 66,500 (sprinklered) |
|  | Specific Fire Resistance: Structural frame = 1 hour Bearing walls = 2 hour (exterior); 1 hour (interior) Interior nonbearing walls & partitions = NR Floors = 1 hour Roofs = 1 hour; heavy timber OK; NR or fire-retardant treated wood OK if ≥ 20’ above floor immediately below; Fire barriers between fire areas = 2 hours Fire walls = 3 hours (based on occupancy) Corridors = 1 hour (unsprinklered), 0.5 hours (sprinklered) @ occupant load > 30 4-story unenclosed escalator or non-MOE stair allowed |
|  | Specific Fire Alarm Threshold: Manual system @ occupant load ≥ 300 |
|  | Specific Sprinkler Threshold: All A-2 occupancies where fire area > 5000 sq ft; OR occupant load > 100; OR the A-2 is not on the floor of exit discharge Required on all floors between the A-2 and the floor of exit discharge |
|  | Podium Buildings: Separate bldgs for area & number of stories; A’s occ ld < 300; height measured fr grade plane |

| UBC A-2.1 Type III-1 hour | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |
| --- | --- | --- | --- |
|  | 2 stories, 65’ | 3 stories, 65’ | 3 stories, 65’ (2 stories, 65’ if spr’s used for area) |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 13,500 | 2 | 2 | 108,000 (54,000 if spr’s used for stories) |
|  | Basements: 27,000 (unsprinklered); 81,000 (sprinklered) |
|  | Specific Fire Resistance: Structural frame = 1 hour Bearing walls = 4 hour NC (exterior); 1 hour (interior) Interior nonbearing walls & partitions = 1 hour Floors = 1 hour Roofs = 1 hour Area separation walls = 4 hours (based on type of construction) Corridors = 1 hour, triggered by travel distance or >1 intervening room Hallways = non-rated, treated as intervening room A occ's w/ aggregate occ ld ≥ 1000 NP in basement |
|  | Specific Fire Alarm Threshold: All A-2.1 occupancies, per Fire Code |
|  | Specific Sprinkler Threshold: Drinking establishments > 5000 sq ft A-2.1’s in basements > 1500 sq ft |
|  | Podium Buildings: NP |
| IBC A-2 Type IIIB | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |
|  | 2 stories, 55’ | 3 stories, 75’ | 3 stories, 75’ |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 9,500 | 1.75 | 2 | 106,875 |
|  | Basements: 16,625 (unsprinklered); 45,125 (sprinklered) |
|  | Specific Fire Resistance: Structural frame = NR Bearing walls = 2 hours (exterior); NR (interior) Interior nonbearing walls & partitions = NR Floors = NR Roofs = NR, heavy timber OK Fire barriers between fire areas = 2 hours Fire walls = 3 hours (based on occupancy) Corridors = 1 hour (unsprinklered), 0.5 hours (sprinklered) @ occupant load > 30 4-story unenclosed escalator or non-MOE stair allowed |
|  | Specific Fire Alarm Threshold: Manual system @ occupant load ≥ 300 |
|  | Specific Sprinkler Threshold: All A-2 occupancies where fire area > 5000 sq ft; OR occupant load > 100; OR the A-2 is not on the floor of exit discharge Required on all floors between the A-2 and the floor of exit discharge |
|  | Podium Buildings: Separate bldgs for area & number of stories; A’s occ ld < 300; height measured fr grade plane |

| UBC A-2.1 Type III-N | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |
| --- | --- | --- | --- |
|  | ’ |  | NP |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  |  |  |  | NP |
|  | Basements: NP |
|  | Specific Fire Resistance: |
|  | Specific Fire Alarm Threshold: |
|  | Specific Sprinkler Threshold: |
|  | Podium Buildings: NP |

(UBC A-2.1 occupancies not allowed in non-rated buildings)

| IBC A-2 Type IV HT | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |
| --- | --- | --- | --- |
|  | 3 stories, 65’ | 4 stories, 85’ | 4 stories, 85’ |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 15,000 | 1.75 | 2 | 168,750 |
|  | Basements: 26,250 (unsprinklered); 71,250 (sprinklered) |
|  | Specific Fire Resistance: Structural frame = HT Bearing walls = 2 hour (exterior); 1 hour or HT (interior) Interior nonbearing walls & partitions = 1 hour or solid wood Floors = HT Roofs = HT Fire barriers between fire areas = 2 hours Fire walls = 3 hours (based on occupancy) Corridors = 1 hour (unsprinklered), 0.5 hours (sprinklered) @ occupant load > 30 4-story unenclosed escalator or non-MOE stair allowed |
|  | Specific Fire Alarm Threshold: Manual system @ occupant load ≥ 300 |
|  | Specific Sprinkler Threshold: All A-2 occupancies where fire area > 5000 sq ft; OR occupant load > 100; OR the A-2 is not on the floor of exit discharge Required on all floors between the A-2 and the floor of exit discharge |
|  | Podium Buildings: Separate bldgs for area & number of stories; A’s occ ld < 300; height measured fr grade plane |

| UBC A-2.1 Type IV HT | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |
| --- | --- | --- | --- |
|  | 2 stories, 65’ | 3 stories, 65’ | 3 stories, 65’ (2 stories, 65’ if spr’s used for area) |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 13,500 | 2 | 2 | 108,000 (54,000 if spr’s used for stories) |
|  | Basements: 27,000 (unsprinklered); 81,000 (sprinklered) |
|  | Specific Fire Resistance: Structural frame = 1 hour or HT Bearing walls = 4 hour NC (exterior); 1 hour (interior) Interior nonbearing walls & partitions = 1 hour or HT Floors = HT Roofs = HT Area separation walls = 4 hours (based on type of construction) Corridors = 1 hour, triggered by travel distance or >1 intervening room Hallways = non-rated, treated as intervening room A occ's w/ aggregate occ ld ≥ 1000 NP in basement |
|  | Specific Fire Alarm Threshold: All A-2.1 occupancies, per Fire Code |
|  | Specific Sprinkler Threshold: Drinking establishments > 5000 sq ft A-2.1’s in basements > 1500 sq ft |
|  | Podium Buildings: NP |
| IBC A-2 Type VA | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |
|  | 2 stories, 50’ | 3 stories, 70’ | 3 stories, 70’ |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 11,500 | 1.75 | 2 | 129,375 |
|  | Basements: 20,125 (unsprinklered); 54,625 (sprinklered) |
|  | Specific Fire Resistance: Structural frame = 1 hour Bearing walls = 1 hour (exterior or interior) Interior nonbearing walls & partitions = NR Floors = 1 hour Roofs = 1 hour; heavy timber OK; NR or fire-retardant treated wood OK if ≥ 20’ above floor immediately below; Fire barriers between fire areas = 2 hours Fire walls = 2 hours (based on occupancy, type of construction) Corridors = 1 hour (unsprinklered), 0.5 hours (sprinklered) @ occupant load > 30 4-story unenclosed escalator or non-MOE stair allowed |
|  | Specific Fire Alarm Threshold: Manual system @ occupant load ≥ 300 |
|  | Specific Sprinkler Threshold: All A-2 occupancies where fire area > 5000 sq ft; OR occupant load > 100; OR the A-2 is not on the floor of exit discharge Required on all floors between the A-2 and the floor of exit discharge |
|  | Podium Buildings: Separate bldgs for area & number of stories; A’s occ ld < 300; height measured fr grade plane |

| UBC A-2.1 Type V-1 hour | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |
| --- | --- | --- | --- |
|  | 2 stories, 50’ | 3 stories, 50’ | 3 stories, 50’ (2 stories, 50’ if spr’s used for area) |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 10,500 | 2 | 2 | 84,000 (42,000 if spr’s used for stories) |
|  | Basements: 21,000 (unsprinklered); 63,000 (sprinklered) |
|  | Specific Fire Resistance: Structural frame = 1 hour Bearing walls = 1 hour (exterior or interior) Interior nonbearing walls & partitions = 1 hour Floors = 1 hour Roofs = 1 hour Area separation walls = 2 hours (based on type of construction) Corridors = 1 hour, triggered by travel distance or >1 intervening room Hallways = non-rated, treated as intervening room A occ's w/ aggregate occ ld ≥ 1000 NP in basement |
|  | Specific Fire Alarm Threshold: All A-2.1 occupancies, per Fire Code |
|  | Specific Sprinkler Threshold: Drinking establishments > 5000 sq ft A-2.1’s in basements > 1500 sq ft |
|  | Podium Buildings: NP |

| IBC A-2 Type VB | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |
| --- | --- | --- | --- |
|  | 1 story, 40’ | 2 stories, 60’ | 2 stories, 60’ |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 6,000 | 1.75 | 2 | 45,000 |
|  | Basements: 10,500 (unsprinklered); 28,500 (sprinklered) |
|  | Specific Fire Resistance: Structural frame = NR Bearing walls = NR (exterior & interior) Interior nonbearing walls & partitions = NR Floors = NR Roofs = NR Fire barriers between fire areas = 2 hours Fire walls = 2 hours (based on occupancy, type of construction) Corridors = 1 hour (unsprinklered), 0.5 hours (sprinklered) @ occupant load > 30 4-story unenclosed escalator or non-MOE stair allowed |
|  | Specific Fire Alarm Threshold: Manual system @ occupant load ≥ 300 |
|  | Specific Sprinkler Threshold: All A-2 occupancies where fire area > 5000 sq ft; OR occupant load > 100; OR the A-2 is not on the floor of exit discharge Required on all floors between the A-2 and the floor of exit discharge |
|  | Podium Buildings: Separate bldgs for area & number of stories; A’s occ ld < 300; height measured fr grade plane |

| UBC A-2.1 Type V-N | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |
| --- | --- | --- | --- |
|  | ’ |  | NP |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  |  |  |  | NP |
|  | Basements: NP |
|  | Specific Fire Resistance: |
|  | Specific Fire Alarm Threshold: |
|  | Specific Sprinkler Threshold: |
|  | Podium Buildings: NP |

(UBC A-2.1 occupancies not allowed in non-rated buildings)