## Table 1
This document provides a comparison of the regulations applicable to most hospitals. It is important to verify the editions of the codes and standards that are applicable in your jurisdiction. Some jurisdictions may have adopted a different edition of the building code for construction. Many states have adopted other editions of the NFPA’s Life Safety Code®. For additional information, contact your state agency responsible for licensing hospitals. This resource represents CMS form 2786R Fire Safety Survey Report 2012 Code – Health Care, available at the time of this publication (April 2017). Errors in the CMS form have been identified and CMS has been notified. CMS is currently working on updating this form, but has not projected a time frame for the release of an update. | [9 empty] | Proposal Needed
Minor Change Needed
Complete
CMS Tag | Group | CMS Language | TJC EP Reference1 | NFPA 101 Reference 2012 Edition2 | ICC Reference 2015 Edition | ICC Reference 2018 Edition | ICC Reference 2021 Edition | Resource | Comments | Priority | Responsibility
K100 | General | General Requirements – Other List in the REMARKS section, any LSC Section 18.1 and 19.1 General Requirements that are not addressed by the provided K- tags, but are deficient. This information, along with the applicable Life Safety Code or NFPA standard citation, should be included on Form CMS-2567. | LS.02.01.10: EP 15 | NFPA 101 18/19.1 |  |  |  |  | No work at this time | Y
K111 | General | Building Rehabilitation |  |  | IEBC 102.2, 301.1; 301.1.1; 301.1.2; 301.1.3, 302.1; 302.2; 302.3; 302.4; 302.5; | IEBC [A] 101.2 Scope. IEBC 301.1 General. IEBC 301.2 Repairs. IEBC 301.3 Alteration, change of occupancy, addition or relocation. IFC 1101.1 Scope. IFC 1101.2 Intent. | IEBC 101.2 Scope 301.1 Applicability 301.3.1 Prescriptive compliance method 301.3.2 Work area compliance method 301.3.3 Performance compliance method 302.2 Additional codes 302.3 Existing materials 302.4 New and replacement materials 302.5 Occupancy and use IFC 1101.1 Scope. 1101.2 Intent. | NFPA 101: Chapter 43 Building | Minimal work needed. Review IEBC to address changes in function (I.e. care recipient room to storage) (5/7/20) NFPA 101 and ICC-IBC include significant fundamental differences in structure and methodology for code application. While both the IEBC and NFPA 101 Chapter 43 provide scoping criteria for building rehabilitation, there are inherent differences and limited ability for direct comparison for their application to existing building rehabilitation work. (5/1/20 Dan P./ Ajay P./ Jeff O./ Shaine G. meeting): Conclusion of subgroup is that no changes should be pursued here due to both codes being conceptually somewhat different. Impact of differences are generally acceptable. Any potential changes could be be difficult to correlate between both codes. (3/25/25 Ktag Spreadsheet version Comment inserted by DCP) Minimal work required. This is essentially a scoping document instructing surveyors to acknowledge the existing requirements (IFC), renovation scoping requirements (IEBC) and new construction requirements (IBC). Conceptually both code families are consistent. We should review and monitor the approaches. Update IEBC to address changes of function (storage in a hospital). Review nursing home application (group I-2, condition 1) (DCP 4/18/20) This analysis could be too complicated to make the codes match, wouldn’t it? For example, NFPA 101 18.1 Rehab states threshold 4500 SF or not more than 50% of smoke compartment. IEBC says that depending on level prescriptively starting at Level 1 replacing existing w new, Level II remodeling existing up to 50%, and level III over 50%.
|  | Repair, Renovation, Modification, or Reconstruction Any building undergoing repair, renovation, modification, or reconstruction complies with both of the following:  Requirements of Chapter 18 and 19  Requirements of the applicable Sections 43.3, 43.4, 43.5, and 43.6 18.1.1.4.3, 19.1.1.4.3, 43.1.2.1 | LS.02.01.10: EP 2 | NFPA 101 3.3.229; 3.3.228; 3.3.178; 3.3.222 18/19.4.3 Chapter 43 | IEBC 202, 401.1, 401.1, 701.1, 801.1, 901.1 IFC 1101.1; 1101.2, 1105, 1105.1 | IEBC 202 Definitions REPAIR. [A] ALTERATION. IEBC 401.1 Scope. (Repair) IEBC 501.1 Scope. (Prescriptive method) IEBC 701.1 Scope. (Level 1 alterations ) IEBC 801.1 Scope. (Level 2 alterations ) IEBC 901.1 Scope. (Level 3 alterations) IFC 1101.1 Scope. IFC 1101.2 Intent. IFC SECTION 1105 CONSTRUCTION REQUIREMENTS FOR EXISTING GROUP I-2 IFC 1105.1 General. | IEBC 202 General Definitions REPAIR ALTERATION IEBC 401.1 Scope. (Repair) IEBC 501.1 Scope. (Prescriptive method) IEBC 701.1 Scope. (Level 1 alterations ) IEBC 801.1 Scope. (Level 2 alterations ) IEBC 901.1 Scope. (Level 3 alterations) IFC 1101.1 Scope 1101.2 Intent 1105 Construction requirements for existing group I-2 1105.2 Applicability |  | Minimal work needed. Review IEBC to address changes in function (I.e. care recipient room to storage) (5/1/20 Dan P./ Ajay P./ Jeff O./ Shaine G. meeting): Conclusion of subgroup is that no changes should be pursued here due to both codes being conceptually somewhat different. Impact of differences are generally acceptable. Any potential changes could be be difficult to correlate between both codes. | Y
|  | Change of Use or Change of Occupancy Any building undergoing change of use or change of occupancy classification complies with the requirements of Section 43.7, unless permitted by 18.1.1.4.2 or 19.1.1.4.2 18.1.1.4.2 (4.6.7 and 4.6.11), 19.1.1.4.2 (4.6.7 and 4.6.11), 43.1.2.2 (43.7) | LS.02.01.10: EP 3 | NFPA 101 3.3.42, 3.3.43, 19.1.1.4.2, 43.7 | IEBC 202; 401.1; 1001.1; 1002.1 | IEBC 202 Definitions [A] CHANGE OF OCCUPANCY. IEBC 501.1 Scope. (Prescriptive method) IEBC 1001.1 Scope. (change of occupancy) IEBC SECTION 1002 SPECIAL USE AND OCCUPANCY IEBC 1002.1 Compliance with the building code. | IEBC 202 General Definitions CHANGE OF OCCUPANY IEBC 501.1 Scope. (Prescriptive method) IEBC 1001.1 Scope. (change of occupancy) 1002.1 Compliance with the building code |  | (5/1/20 Dan P./ Ajay P./ Jeff O./ Shaine G. meeting): Conclusion of subgroup is that no changes should be pursued here due to both codes being conceptually somewhat different. Impact of differences are generally acceptable. Any potential changes could be be difficult to correlate between both codes. (3/25/25 Ktag Spreadsheet version Comment inserted by DCP) Minimal work needed. We addressed change of occupancy clearly and consistently with these concepts. High level review of scoping language needed. Change of use (actual use of space ie. Bedroom to storage room) is not consistent with these requirements. (DCP 4/18/20) This analysis could also be too complicated to make the codes match, wouldn’t it? They both have different approaches and thresholds. There are issues that could be correlated in both NEW and REHAB in both family of codes. 1.) How Group occupancy is classified on plans can be different between the different code families (ICC vs. NFPA. IBC would have the B area be a B occupancy colored on the plans, in a nursing dining area example, but then call it accessory to the major occupancy or non-separated w no separation. NFPA 101 Appendix, by inference, states this area is generally for the public. So a SNF dining area is classified as Health Care. Both get to a similar place but differently. I am not sure if this causes differences in certain instances. 2.) It seems that both family of codes require absolute 2 hour separation now. 3.) It seems that both codes get to the same place with the bedroom to storage example above. NFPA 101 Hazard 18.3.2 and 19.3.2 get you to the 1 hour separation. IBC does the same in Incidental uses 509. | Y
|  | Additions Any building undergoing an addition shall comply with the requirements of Section 43.8. If the building has a common wall with a nonconforming building, the common wall is a fire barrier having at least a 2-hour fire resistance rating constructed of materials as required for the addition. Communicating openings occur only in corridors and are protected by approved self-closing fire doors with at least a 1 1/2-hour fire resistance rating. Additions comply with the requirements of Section 43.8 (additions). 18.1.1.4.1 (4.6.7 and 4.6.11), 18.1.1.4.1.1 (8.3), 18.1.1.4.1.2, 18.1.1.4.1.3, 19.1.1.4.1 (4.6.7 and 4.6.11), 19.1.1.4.1.1 (8.3), 19.1.1.4.1.2, 19.1.1.4.1.3, 43.1.2.3(43.8) | LS..02.01.10-EP 4 LS.02.01.10- EP 7 | NFPA 101 3.3.5 43.8 NFPA 101 18/19.1.1.4.1 NFPA 101 18/19.1.1.4.1.1; 18/19.1.1.4.1.2; 18/19.1.1.4.1.3 | IEBC 202; 401.1; 402.1; 1101.1 | IEBC 202 Definitions ADDITION. IEBC 501.1 Scope. (Prescriptive method) IEBC 502.1 General. IEBC 1101.1 Scope. (addition) | IEBC 202 General Definitions ADDITION IEBC 501.1 Scope. (Prescriptive method) IEBC 502.1 General. IEBC 1101.1 Scope. (addition) |  | Commentary: IBC requirements do not address common wall with a nonconforming building nor communicating openings in corridors. (5/1/20 Dan P./ Ajay P./ Jeff O./ Shaine G. meeting): Conclusion of subgroup is that no changes should be pursued here due to both codes being conceptually somewhat different. Impact of differences are generally acceptable. Any potential changes could be be difficult to correlate between both codes. Also see K111 D comments. (3/25/25 Ktag Spreadsheet version Comment inserted by DCP) IEBC: No work needed. IBC 508 I-2 Condition 2. Some work needed. This portion of the KTAG is worded in a challenging way. Conceptually, the Ktag tries to acknowledge that non-compliant buildings (i.e. other occupancies) that are not compliant with the bare minimum requirements for the occupancy (IFC chapter 11requirements) are separated from a new healthcare occupancy with a two hour separation. The building code works the same way – if you add an I-2 to another occupancy you will get a minimum 2 hour separation. With non-separated mixed uses, it’s more difficult to state. We added a section into 2018 IBC 508 to deal with some of the opening protection issues – but this needs to be added into the chapter 11 IFC. Review nursing home application (group I-2, condition 1) (DCP 4/18/20) This seems comprehensive. Not sure where to start; The following identifies what sections of each code will need to be analyzed: IBC: 508.3.1.2 Non-separated Use exceptions I-2 IFC 1103.4.1 Interior vertical openings IEBC Chapters 7, 8, and 9. These ICC codes need to be more specifically reviewed in comparison to NFPA 101 Sections 8.6.6, 8.6.7, and 8.6.8
|  | If the building has a common wall with a nonconforming building, the common wall is a fire barrier having at least a 2-hour fire resistance rating constructed of materials as required for the addition. Communicating openings occur only in corridors and are protected by approved self-closing fire doors with at least a 1 1/2-hour fire resistance rating. Additions comply with the requirements of Section 43.8 (additions). 18.1.1.4.1 (4.6.7 and 4.6.11), 18.1.1.4.1.1 (8.3), 18.1.1.4.1.2, 18.1.1.4.1.3, 19.1.1.4.1 (4.6.7 and 4.6.11), 19.1.1.4.1.1 (8.3), 19.1.1.4.1.2, 19.1.1.4.1.3, 43.1.2.3(43.8) |  |  |  | IBC 508.3.1.2 Group I-2, Condition 2 occupancies. | IBC 508.3.1.2 Group I-2, Condition 2 occupancies. |  | (5/1/20 Dan P./ Ajay P./ Jeff O./ Shaine G. meeting): Conclusion of subgroup is the comments below are correct. No changes should be pursued despite both codes having nuaced differences (i.e. IBC also allows a fire wall as separation while NFPA 101 and IBC allows a 2 hour fire barrier. The subgroup generally agrees that the designer will have to show compliance with the most stringent requirements of both codes in the minor differences that exist. G148-15 AMPC1 Conceptually, the Ktag tries to acknowledge that non-compliant buildings (i.e. other occupancies) that are not compliant with the bare minimum requirements for the occupancy (IFC chapter 11requirements) are separated from a new healthcare occupancy with a two hour separation. The building code works the same way – if you add an I-2 to another occupancy you will get a minimum 2 hour separation. With non-separated mixed uses, it’s more difficult to state. We added a section into 2018 IBC 508 to deal with some of the opening protection issues – but this needs to be added into the chapter 11 IFC. Review nursing home application (group I-2, condition 1) (DCP 4/18/20) This seems comprehensive. Not sure where to start; The following identifies what sections of each code will need to be analyzed: IBC: 508.3.1.2 Non-separated Use exceptions I-2 IFC 1103.4.1 Interior vertical openings IEBC Chapters 7, 8, and 9. These ICC codes need to be more specifically reviewed in comparison to NFPA 101 Sections 8.6.6, 8.6.7, and 8.6.8
K112 | Fire | Sprinkler Requirements for Major Rehabilitation If a non-sprinklered smoke compartment has undergone major rehabilitation, the automatic sprinkler requirements of 18.3.5 have been applied to the smoke compartment. In cases where the building is not protected throughout by a sprinkler system, the requirements of 18.4.3.2, 18.4.3.3, and 18.4.3.8 are also met. Note: Major rehabilitation involves the modification of more than 50 percent, or more than 4500 square feet of the area of the smoke compartment. 18.1.1.4.3.3,19.1.1.4.3.3 | LS.02.01.10 EP 5 | NFPA 101 19.1.1.4.3; 19.1.1.4.3.1 18.4.3; 18.4.3.1; 18.4.3.2; 18.4.3.3; 18.4.3.4; 18.4.3.4.1; 18.4.3.4.2; 18.4.3.5 | N/A | N/A | IFC 1103.5 Sprinkler systems 1103.5.2 Group I-2. 1103.5.3 Group I-2, Condition 2. (by date) 1105.9 Group I-2 automatic sprinkler system. |  | HealthCareCommentary 2021-803.2.3 Group I-2. In Group I-2 occupancies, an automatic sprinkler system installed in accordance with Section 903.3.1.1 of the International Fire Code shall be provided in the following: 1. In Group I-2, Condition 1, throughout the work area . 2. In Group I-2, Condition 2, throughout the work area where the work area is 50 percent or less of the smoke compartment. 3. In Group I-2, Condition 2, throughout the smoke compartment in which the work occurs where the work area exceeds 50 percent of the smoke compartment 2018 IFC 1105.9 Group I-2 automatic sprinkler system. An automatic sprinkler system installed in accordance with Section 903.3.1.1 shall be provided throughout the floor containing the Group I-2 fire area. The sprinkler system shall be provided throughout the floor where the Group I-2 occupancy is located, on all floors between the Group I-2 occupancy fire area and the level of exit discharge, the level of exit discharge, and all floors below the level of exit discharge. Exception: Floors classified as an open parking garage are not required to be sprinklered. | Andrew/Justin | Andrew/Justin
K131 | General | Multiple Occupancies – Sections of Health Care Facilities Sections of health care facilities classified as other occupancies meet all of the following: | LS.02.01.10- EP 7 LS.02.01.10- EP 8 LS.03.01.10- EP 4 | NFPA 101 18/19.1.3.1; 18/19.1.3.2; 18/19.1.3.3 | IBC 202; 304.1; 304.2; 308.1; 308.4.1; 308.4.1.1; 308.4.1.2; 422.2; 508.1 IFC 903.3; 903.3.1; 903.3.1.1 | IBC 202 Definitions 24-HOUR BASIS. CARE SUITE. CLINIC, OUTPATIENT. CUSTODIAL CARE. DETOXIFICATION FACILITIES. HOSPITALS AND PSYCHIATRIC HOSPITALS. INCAPABLE OF SELF-PRESERVATION. MEDICAL CARE. NURSING HOMES. PERSONAL CARE SERVICE. IBC SECTION 308 INSTITUTIONAL GROUP I IBC 308.1 Institutional Group I. IBC 308.2 Institutional Group I-1. IBC 308.2.1 Condition 1. IBC 308.2.2 Condition 2. IBC 308.2.3 Six to 16 persons receiving custodial care. IBC 308.3 Institutional Group I-2. IBC 308.3.1 Occupancy conditions. IBC 308.3.1.1 Condition 1. IBC 308.3.1.2 Condition 2. | IBC 202 Definitions 24-HOUR BASIS. CARE SUITE. CLINIC, OUTPATIENT. CUSTODIAL CARE. DETOXIFICATION FACILITIES. HOSPITALS AND PSYCHIATRIC HOSPITALS. INCAPABLE OF SELF-PRESERVATION. MEDICAL CARE. NURSING HOMES. PERSONAL CARE SERVICE. 304.1 Business Group B 304.3 Ambulatory care facilities 308.1 Institutional Group I 308.2 Institutional Group I-1. 308.2.1 Condition 1. 308.2.2 Condition 2. 308.2.3 Six to 16 persons receiving custodial care. 308.3 Institutional Group I-2. 308.3.1 Occupancy conditions. 308.3.1.1 Condition 1. 308.3.1.2 Condition 2. | Comparison chart of business and ambulatory occupancy requirements When is my ASC an ambulatory health care occupancy? HITF Interpretations, December 2008 | (5/7/20) Uses that are considered as a Health Care occupancy per NFPA 101 may be classified as different occupancies (i.e. Group I-1 or I-2 with Condition 1 or 2) per the IBC. These differences in the occupancy definition do not allow for direct comparison between codes. (5/1/20 Dan P./ Ajay P./ Jeff O./ Shaine G. meeting): Conclusion of subgroup is that no changes should be pursued here due to both codes being conceptually somewhat different. Impact of differences are generally acceptable. Any potential changes could be be difficult to correlate between both codes. Ajay and Shaine stated some other differences and may add additional detailed comments on this item. G13-18 AS, G90-18 AS
|  | They are not intended to serve four or more inpatients. |  |  |  | IBC 308.2.4 Five or fewer persons receiving custodial care. IBC 308.3.2 Five or fewer persons receiving medical care. IBC 308.5.3 Five or fewer persons receiving care. IBC 308.5.4 Five or fewer persons receiving care in a dwelling unit. | IBC 308.2.4 Five or fewer persons receiving custodial care. 308.3.2 Five or fewer persons receiving medical care. 308.5.3 Five or fewer persons receiving care. 308.5.4 Five or fewer persons receiving care in a dwelling unit. |  | (5/1/20 Dan P./ Ajay P./ Jeff O./ Shaine G. meeting): Conclusion of subgroup isthat this is one area the HCC should consider reviewing and proposing changes since there are differences between Federal enforcement, NFPA and ICC families. Jeff, Ajay, and Shaine may have additional detailed comments on this topic. [JTO] Recommend proposing a code change to bring the nubers to actually match. the difference between "five or fewer" and "four or more" still has a difference of one patient, which can man a great deal to smaller ambulatory facilities. i believe this is a key element of allignment.
|  | They are separated from areas of health care occupancies by construction having a minimum 2-hour fire resistance rating in accordance with Chapter 8. |  |  |  | IBC SECTION 508 MIXED USE AND OCCUPANCY IBC 508.1 General. | IBC 422.2 Separation SECTION 508 MIXED USE AND OCCUPANCY 508.1 General. |  | (5/1/20 Dan P./ Ajay P./ Jeff O./ Shaine G. meeting): Conclusion of subgroup is the comments below are correct. No changes should be pursued despite both codes having nuaced differences (i.e. IBC also allows a fire wall as separation while NFPA 101 and IBC allows a 2 hour fire barrier. The subgroup generally agrees that the designer will have to show compliance with the most stringent requirements of both codes in the minor differences that exist.
|  | The entire building is protected throughout by an approved, supervised automatic sprinkler system in accordance with Section 9.7. |  |  |  | IFC 903.3 Installation requirements. IFC 903.3.1 Standards. IFC 903.3.1.1 NFPA 13 sprinkler systems. | IFC 903.3 Installation requirements 903.3.1 Standards 903.3.1.2 NFPA 13R sprinkler systems |  | (5/7/20) These references for sprinkler coverage per NFPA 13 are in general agreement. However, there are some specific cases where certain instances where local or state requirements prohibit sprinkler protection in elevator related spaces. It is our understanding that in Massachusetts and New York City, the local or state code prohibit sprinklers in elevator related spaces (including the hoistways and machine rooms) which creates a conflict with consideration of these facilities being considered fully sprinklered per Federal requirements. (5/1/20 Dan P./ Ajay P./ Jeff O./ Shaine G. meeting): Conclusion of subgroup is that no changes should be pursued here due to bothessentially being the same. Shaine stated some other differences that individual states require, that is beyond the scope of this committee and may ahve some additional detailed comments on this item.
|  | Hospital outpatient surgical departments are required to be classified as an Ambulatory Health Care Occupancy regardless of the number of patients served. 18.1.3.3, 19.1.3.3, 42 CFR 482.41, 42 CFR 485.623 |  |  |  | IBC 202 DEFINITIONS 24-HOUR BASIS. AMBULATORY CARE FACILITY. CLINIC, OUTPATIENT. IBC 304.1 Business Group B. IBC 422.2 Separation. | IBC 202 DEFINITIONS 24-HOUR BASIS. AMBULATORY CARE FACILITY. CLINIC, OUTPATIENT. IBC 304.1 Business Group B. IBC 422.2 Separation. |  | (5/7/20) – The IBC Ambulatory Care definition does not include a four (4) or more threshold as does NFPA 101 for an Ambulatory Health Care occupancy classification. CMS includes provisions for Hospital Outpatient Surgical Departments and Ambulatory Surgical Centers that apply Ambulatory Health Care occupancy provisions per NFPA 101 regardless of the number of patients served. It is recommended to provide additional review to consider code alignment of the Ambulatory Care occupancy classification. (5/1/20 Dan P./ Ajay P./ Jeff O./ Shaine G. meeting): Conclusion of subgroup isthat this is an area the HCC should consider reviewing and proposing changes since there are differences between the various codes. Jeff, Ajay, and Shaine may have additional detailed comments on this topic.
K132 | General | Multiple Occupancies – Contiguous Non-Health Care Occupancies Non-health care occupancies that are located immediately next to a Health Care Occupancy, but are primarily intended to provide outpatient services are permitted to be classified as Business or Ambulatory Health Care Occupancies, provided the facilities are simultaneously for four or more inpatients. Outpatient surgical departments must be classified as Ambulatory Health Care Occupancy regardless of the number of patients served. 18.1.3.4.1, 19.1.3.4.1 | LS.02.01.10- EP 7 LS.03.01.10- EP 4 | NFPA 101 18.1.3.4; 18.1.3.4.1; 18.1.3.4.2 | IBC 202; 302.1; 302.2; 304.1; 422.2 TABLE 508.4 | IBC 202; 302.1; 302.2; 304.1; 422.2 TABLE 508.4 | IBC 202 Definitions 24-HOUR BASIS. AMBULATORY CARE FACILITY. CLINIC, OUTPATIENT 302.1 Occupancy classification 302.2 Use designation 304.1 Business Group B 422.2 Separation IBC TABLE 508.4f REQUIRED SEPARATION OF OCCUPANCIES (HOURS) | HITF Interpretations, June 2010 | G13-18 AS
K133 | General | Multiple Occupancies – Construction Type Where separated occupancies are in accordance with 18/19.1.3.2 or 18/19.1.3.4, the most stringent construction type is provided throughout the building, unless a 2-hour separation is provided in accordance with 8.2.1.3, in which case the construction type is determined as follows:  The construction type and supporting construction of the health care occupancy is based on the story in which it is located in the building in accordance with 18/19.1.6 and Tables 18/19.1.6.1  The construction type of the areas of the building enclosing the other occupancies shall be based on the applicable occupancy chapters. 18.1.3.5, 19.1.3.5, 8.2.1.3 | LS.02.01.10- EP 8 | NFPA 101 18/19.1.3.5 18/19.1.6 6.1.14.; 6.1.14.3; 6.1.14.4 | IBC 508.1 | IBC 508.1 IFC 1105.2 Construction. | IBC SECTION 508 MIXED USE AND OCCUPANCY 508.1 General. |  | G90-18 AS
K161 | General | Building Construction Type and Height 2012 EXISTING Building construction type and stories meets Table 19.1.6.1, unless otherwise permitted by 19.1.6.2 through 19.1.6.7 19.1.6.4, 19.1.6.5 Construction Type 1. I (442), I (332), II (222) -- Any number of stories (non-sprinklered and sprinklered) 2. II (111) -- One story (non-sprinklered) -- ≤ 3 stories (sprinklered) 3. II (000) -- No stories (non-sprinklered) -- ≤ 2 stories (sprinklered) 4. III (211) -- No stories (non-sprinklered) -- ≤ 2 stories (sprinklered) 5. IV (2HH) -- No stories (non-sprinklered) -- ≤ 2 stories (sprinklered) 6. V (111) -- No stories (non-sprinklered) -- ≤ 2 stories (sprinklered) 7. III (200) -- No stories (non-sprinklered) -- ≤ 1 story (sprinklered) 8. V (000) -- No stories (non-sprinklered) -- ≤ 1 story (sprinklered) Sprinklered stories must be sprinklered throughout by an approved, supervised automatic system in accordance with section 9.7. (See 19.3.5) Give a brief description, in REMARKS, of the construction, the number of stories, including basements, floors on which patients are located, location of smoke or fire barriers and dates of approval. Complete sketch or attach small floor plan of the building as appropriate. | LS.02.01.10- EP 1 | NFPA 101 Table 19.1.6.1 19.1.6.2; 19.1.6.3; 19.1.6.4; 19.1.6.5 | IFC 1105.2 TABLE 1105.2 | IFC 1105.3 TABLE 1105.3 | IFC 1105.3 Construction TABLE 1105.3 FLOOR LEVEL LIMITATIONS FOR GROUP I-2, CONDITION 2 |  | Type II conflict above 4 stories
|  | Building Construction Type and Height 2012 NEW Building construction type and stories meets Table 18.1.6.1, unless otherwise permitted by 18.1.6.2 through 18.1.6.7. 18.1.6.4, 18.1.6.5 Construction Type 1. I (442), I (332), II (222) -- No stories (non-sprinklered), Any number of stories (sprinklered) 2. II (111) -- No stories (non-sprinklered) -- ≤ 3 stories (sprinklered) 3. II (000) -- No stories (non-sprinklered) -- ≤ 1 story (sprinklered) 4. III -- (211) No stories (non-sprinklered) -- ≤ 1 story (sprinklered) 5. IV -- (2HH) No stories (non-sprinklered) -- ≤ 1 story (sprinklered) 6. V (111) -- No stories (non-sprinklered) -- ≤ 1 story (sprinklered) 7. III (200) -- Not allowed non-sprinklered 8. V (000) -- Not allowed non-sprinklered Sprinklered stories must be sprinklered throughout by an approved, supervised automatic system in accordance with section 9.7. (See 18.3.5) Give a brief description, in REMARKS, of the construction, the number of stories, including basements, floors on which patients are located, location of smoke or fire barriers and dates of approval. Complete sketch or attach small floor plan of the building as appropriate. | LS.02.01.10- EP 1 | NFPA 101 Table 18.1.6.1 18.1.6.2; 18.1.6.3; 18.1.6.4; 18.1.6.5 | IBC 414; 415; 504; 506; 509; 903.2.6 | IBC 414; 415; 504; 506; 509; 903.2.6 | IBC 414 Hazardous Materials 415 Groups H-1, H-2, H-3, H-4 and H-5 504 Building Height and Number of Stories 506 Building Area 509 Incidental Uses 903.2.6 Group I.
K162 | General | Roofing Systems Involving Combustibles 2012 EXISTING Buildings of Type I (442), Type I (332), Type II (222), or Type II (111) having roof systems employing combustible roofing supports, decking or roofing meet the following: 1. roof covering meets Class C requirements. 2. roof is separated from occupied building portions with 2 hour fire resistive noncombustible floor assembly using not less than 2½ inches concrete or gypsum fill. 3. attic or other space is either unoccupied or protected throughout by an approved automatic sprinkler system. 19.1.6.2, ASTM E108, ANSI/UL 790 | LS.02.01.10: EP 15 | NFPA 101 19.1.6.2 | IBC Chapter 15 | IBC Chapter 15 | IBC Chapter 15 ROOF ASSEMBLIES AND ROOFTOP STRUCTURES |  | G113-18 AS - Gypsum concrete separation
|  | Roofing Systems Involving Combustibles 2012 NEW Buildings of Type I (442), (332) or Type II (222), or Type II (111) having roof systems employing combustible roofing supports, decking or roofing meet the following: 1. roof covering meets Class A requirements 2. roof is separated from occupied building portions with 2-hour fire resistive noncombustible floor assembly using not less than 2-1/2 inches concrete or gypsum fill 3. the structural elements supporting the rated floor assembly meet the required fire resistance rating of the building 18.1.6.2, ASTM E108, ANSI/UL 790 | LS.02.01.10: EP 15 | NFPA 101 18.1.6.2 | IBC Chapter 15 | IBC Chapter 15 | IBC Chapter 15 ROOF ASSEMBLIES AND ROOFTOP STRUCTURES
K163 | General | Interior Non-Bearing Wall Construction Interior non-bearing walls in Type I or II construction are constructed of noncombustible or limited-combustible materials. Interior non-bearing walls required to have a minimum 2-hour fire resistance rating are fire-retardant-treated wood enclosed within noncombustible or limited-combustible materials, provided they are not used as shaft enclosures. 18.1.6.4, 18.1.6.5, 19.1.6.4, 19.1.6.5 | LS.02.01.10: EP 15 | NFPA 101 18/19.1.6.4; 18/19.1.6.5 | IBC CHAPTER 6 602; 602.2 | IBC CHAPTER 6 602; 602.2 | IBC CHAPTER 6 Types of Construction 602 Construction Classification 602.2 Types I and II |  | IBC allows FT wood in shaft construction where NFPA 101 does not. Henry feels that the construction of a shaft would never be seen in the survey process so would never be cited. Jeff feels it should be fixed to maintain alignment.
K200 | General | Means of Egress Requirements – Other List in the REMARKS section any LSC Section 18.2 and 19.2 Means of Egress requirements that are not addressed by the provided K-tags, but are deficient. This information, along with the applicable Life Safety Code or NFPA standard citation, should be included on Form CMS-2567. 18.2, 19.2 | LS.02.01.20- EP 42 | NFPA 101 18/19.2 | IBC Chapter 10 IFC Chapter 10 | IBC Chapter 10 IFC Chapter 10 | IBC Chapter 10 Means of Egress IFC Chapter 10 Means of egress
K211 | General | Means of Egress – General Aisles, passageways, corridors, exit discharges, exit locations, and accesses are in accordance with Chapter 7, and the means of egress is continuously maintained free of all obstructions to full instant use in case of emergency, unless modified by 18/19.2.2 through 18/19.2.11. 18.2.1, 19.2.1, 7.1.10.1 | LS.02.01.20 EP 14 | NFPA 101 18/19.2.1 7.1.10.1 | IBC[F] 1001.3 | IBC 1002, 1003.3, 1005, 1006, 1007, 1018, 1020, 1028 IFC 1031.1; 1031.2, 1105.5 | IBC 1002 Maintenance and Plans 1003.3 Protruding objects 1005 Means of Egress Sizing 1006 Number of Exits and Exit Access Doorways 1007 Exit and Exit Access Doorway Configuration 1018 Aisles 1020 Corridors 1028 Exit Discharge IFC 1031.1 General 1031.2 Reliability 1105.5 Corridor construction | LS.02.01.20 Obstructions of the Means of Egress [EP 13] | F180-18 AMPC1
K221 | General | Patient Sleeping Room Doors Locks on patient sleeping room doors are not permitted unless the key-locking device that restricts access from the corridor does not restrict egress from the patient room, or the locking arrangement is permitted for patient clinical, security or safety needs in accordance with 18.2.2.2.5 or 19.2.2.2.5. 18.2.2.2, 19.2.2.2, TIA 12-4 | LS.02.01.20- EP 2 | NFPA 101 18/19.2.2.2; 18/19.2.2.2.1; 18/19.2.2.2.2 | IBC 407.4.1.1 1010.1.9.3 | IBC 407.4.1.1 1010.1.9.4 | IBC 407.4.1.1 Locking devices 1010.2.9.2 Rooms with electrical equipment | HITF Interpretations, June 2011 | E55-18 AS, E57-18 AS, E64-18 AMPC1
K222 | General | Egress Doors Doors in a required means of egress shall not be equipped with a latch or a lock that requires the use of a tool or key from the egress side unless using one of the following special locking arrangements: | LS.02.01.20- EP 1 | NFPA 101 18/19.2.2.2.3 | IFC 1031.2.1 | IFC 1031.2.1 | IFC 1031.2.1 Security device and egress locks | Complying with Locking Arrangement Requirements (2017) Lennon Peake and Rebecca Morgenstern
|  | CLINICAL NEEDS OR SECURITY THREAT LOCKING Where special locking arrangements for the clinical security needs of the patient are used, only one locking device shall be permitted on each door and provisions shall be made for the rapid removal of occupants by: remote control of locks; keying of all locks or keys carried by staff at all times; or other such reliable means available to the staff at all times. 18.2.2.2.5.1, 18.2.2.2.6, 19.2.2.2.5.1, 19.2.2.2.6 | LS.02.01.20- EP 2 | NFPA 101 18/19.2.2.2.5; 18/19.2.2.2.5.1; 18/19.2.2.2.6 | IBC 1010.1.9.7 | IBC 1010.1.9.8 | IBC 1010.2.4 Locks and latches (Item 1 and 2, Exp. 1 and 2) 1010.2.13 Delayed egress |  | E37-18 AM, E58-18 AMPC1, E52-18 AMPC1
|  | SPECIAL NEEDS LOCKING ARRANGEMENTS Where special locking arrangements for the safety needs of the patient are used, all of the Clinical or Security Locking requirements are being met. In addition, the locks must be electrical locks that fail safely so as to release upon loss of power to the device; the building is protected by a supervised automatic sprinkler system and the locked space is protected by a complete smoke detection building is protected by a supervised automatic sprinkler system and the locked space is protected by a complete smoke detection system (or is constantly monitored at an attended location within the locked space); and both the sprinkler and detection systems are arranged to unlock the doors upon activation. 18.2.2.2.5.2, 19.2.2.2.5.2, TIA 12-4 | LS.02.01.20- EP 2 | NFPA 101 18/19.2.2.2.5.2 | IBC 1010.1.9.6 Commentary: IBC requirements for locking where patient special needs require specialized protective measures for their safety differ from NFPA 101 requirements. | IBC 1010.1.9.7 | IBC 1010.2.14 Controlled egress doors in Groups I-1 and I-2 |  | E67-12 AM, E69-12 AMPC1, E52-18 AMPC1, E37-18 AM, E55-18 AS, E57-18 AS - Infant Abduction conflict? - John talk to Nancy John will review 2021 IBC and 2021 NFPA to compare against 2012 NFPA 101 to see differences and confirm if anything needs to be changed
|  | DELAYED-EGRESS LOCKING ARRANGEMENTS Approved, listed delayed-egress locking systems installed in accordance with 7.2.1.6.1 shall be permitted on door assemblies serving low and ordinary hazard contents in buildings protected throughout by an approved, supervised automatic fire detection system or an approved, supervised automatic sprinkler system. 18.2.2.2.4, 19.2.2.2.4 | LS.02.01.20- EP 1 | NFPA 101 19.2.2.2.4 | IBC 1010.1.9.7 1010.1.9.8.1 Commentary: IBC still limits delayed egress locking arrangement to two per egress path (or 30 seconds delay) in I-2 occupancies. CMS, TJC, and NFPA allow unlimited delayed egress devices in egress path. | IBC 1010.1.9.8 1010.1.9.8.1 | IBC 1010.2.13 Delayed egress 1010.2.13.1 Delayed egress locking system | HITF Interpretations June 2005 | E70-12 AM, E72-12 AM, E74-12 AMPC, E37-18 AM, E58-18 AMPC1, E59-18 AMPC1
|  | ACCESS-CONTROLLED EGRESS LOCKING ARRANGEMENTS Access-Controlled Egress Door assemblies installed in accordance with 7.2.1.6.2 shall be permitted. 18.2.2.2.4, 19.2.2.2.4 | LS.02.01.20- EP 1 | NFPA 101 18/19.2.2.2.4 7.2.1.6.2 | IBC 1010.1.9.8 | IBC 1010.1.9.8 1010.1.9.9 | IBC 1010.2.13 Delayed egress 1010.2.12 Sensor release of electrically locked egress doors. |  | E78-12 AM, E37-18 AM, E58-18 AMPC1
|  | ELEVATOR LOBBY EXIT ACCESS LOCKING ARRANGEMENTS Elevator lobby exit access door locking in accordance with 7.2.1.6.3 shall be permitted on door assemblies in buildings protected throughout by an approved, supervised automatic fire detection system and an approved, supervised automatic sprinkler system. 18.2.2.2.4, 19.2.2.2.4 | LS.02.01.20- EP 1 | NFPA 101 18/19.2.2.2.4 7.2.1.6.3 | IBC 3006.4 IFC 1031.2.1 | IBC 3006.4 IFC 1031.2.1 | IBC 1016.2 Egress through intervening spaces. 3006.4 Means of egress. (Elevator lobbies) IFC 1031.2.1 Security devices and egress locks |  | Needs to be studied for fire protection/sprinkler related items
K223 | General | Doors with Self-Closing Devices Doors in an exit passageway, stairway enclosure, or horizontal exit, smoke barrier, or hazardous area enclosure are self- closing and kept in the closed position, unless held open by a release device complying with 7.2.1.8.2 that automatically closes all such doors throughout the smoke compartment or entire facility upon activation of:  Required manual fire alarm system; and  Local smoke detectors designed to detect smoke passing through the opening or a required smoke detection system; and  Automatic sprinkler system, if installed; and  Loss of power 18.2.2.2.7, 18.2.2.2.8, 19.2.2.2.7, 19.2.2.2.8 | LS.02.01.20- EP 15 LS.02.01.20- EP 23 LS.02.01.30- EP 2 LS.02.01.30- EP 3 Commentary: TJC requirement addresses stair doors only. | NFPA 101 18/19.2.2.2.7, 18/19.2.2.2.8 7.2.1.8 | IBC 716.5.9.3. | IBC 716.2.6.6 | IBC 716.2.6.6 Smoke-activated doors IFC 1105.5.2 Group I-2 occupancies.
K224 | General | Horizontal Sliding Doors Horizontal-sliding doors permitted by 7.2.1.14 that are not automatic-closing are limited to a single leaf and shall have a latch or other mechanism to ensure the door will not rebound. Horizontal-sliding doors serving an occupant load fewer than 10 shall be permitted, providing all of the following criteria are met:  Area served by the door has no hazards  Door is operable from either side without special knowledge or effort  Force required to operate the door in the direction of travel is ≤ 30 lbf to set the door in motion and ≤ 15 lbf to close or open to the required width  Assembly is appropriately fire rated, and where rated is self-or automatic-closing by smoke detection per 7.2.1.8, and installed per NFPA 80  Where required to latch, the door has a latch or other mechanism to ensure the door will not rebound. 18.2.2.2.10, 19.2.2.2.10 | LS.02.01.20- EP 3 LS.02.01.20- EP 4 | NFPA 101 18/19.2.2.2.10; 18/19.2.2.2.10.1; 18/19.2.2.2.10.2 7.2.1.14 | IBC 1010.1.2 1010.1.4.3. | IBC 1010.1.2 1010.1.4.3. | IBC 407.6 Automatic-closing doors 407.6.1 Activation of automatic-closing doors. 1010.1.2 Egress door types 1010.1.4 Manual horizontal slding doors 1010.1.3.3 Special purpose horizontal sliding, accordian or folding doors |  | E4-18 AM, E45-18 AS, E37-18 AM, E42-18 AS, E47-18 AS G46-18 AS
K225 | General | Stairways and Smokeproof Enclosures Stairways and Smokeproof enclosures used as exits are in accordance with 7.2. 18.2.2.3, 18.2.2.4, 19.2.2.3, 19.2.2.4, 7.2 | LS.02.01.20- EP 8 LS.02.01.20- EP 9 LS.02.01.20- EP 10 LS.02.01.20- EP 13 | NFPA 101 18/19.2.2.3; 18/19.2.2.4 | IBC 403.5.4 1011 1019; 1019.4 1023; 1023.11; 1023.11.1; 1023.11.2 | IBC 403.5.4 1011 1019; 1019.4 1023; 1023.11; 1023.11.1; 1023.11.2 | IBC 403.5.4 Smokeproof enclosures 1011 Stairways 1019 Exit Access Stairways and Ramps 1019.4 Group I-2 and I-3 occupancies 1023 Interior Exit Stairways and Ramps 1023.12 Smokeproof enclosures 1023.12.1 Termination and extension 1023.12.2 Enclosure access |  | G44-18 AS
K226 | General | Horizontal Exits Horizontal exits, if used, are in accordance with 7.2.4 and the provisions of 18.2.2.5.1 through 18.2.2.5.7, or 19.2.2.5.1 through 19.2.2.5.4. 18.2.2.5, 19.2.2.5 | LS.02.01.20- EP 5 LS.02.01.20- EP 6 LS.02.01.20- EP 7 | NFPA 101 18/19.2.2.5; 18/19.2.2.5.1; 18/19.2.2.5.2; 18/19.2.2.5.3; 18/19.2.2.5.4; 18.2.2.5.5; 18.2.2.5.6; 18.2.2.5.7 7.2.4 | IBC 1026 | IBC 1026 | IBC 1026 Horizontal Exits IFC 1105.6.1 Two means of egress |  | F189-18 AS
K227 | General | Ramps and Other Exits Ramps, exit passageways, fire and slide escapes, alternating tread devices, and areas of refuge are in accordance with the provisions 7.2.5 through 7.2.12. 18.2.2.6 to 18.2.2.10 or 19.2.2.6 to 19.2.2.10 | LS.02.01.20- EP 9 LS.02.01.20- EP 42 | NFPA 101 18/19.2.2.6; 18/19.2.2.7; 18/19.2.2.8; 18/19.2.2.9; 18/19.2.2.10 | IBC 1009.6. 1011.14 1019; 1019.4 1023 | IBC 1009.6, 1011.14, 1019; 1019.4, 1023, 1024, 1-27 IFC 1104.16 IEBC 504 | IBC 1009.6 Areas of refuge 1011.14 Alternating tread devices 1019 Exit Access Stairways and Ramps 1019.4 Group I-2 and I-3 occupancies 1023 Interior Exit Stairways and Ramps 1024 Exit Passageways SECTION 1027 EXIT STAIRWAYS AND RAMPS IFC 1104.16 Fire escape stairways IEBC 504 Fire escapes
K231 | General | Means of Egress Capacity The capacity of required means of egress is in accordance with 7.3. 18.2.3.1, 19.2.3.1 | LS.02.01.20- EP 11 | NFPA 101 18/19.2.3.1
K232 | General | Aisle, Corridor or Ramp Width 2012 EXISTING The width of aisles or corridors (clear or unobstructed) serving as exit access shall be at least 4 feet and maintained to provide the convenient removal of nonambulatory patients on stretchers, except as modified by 19.2.3.4, exceptions 1-5. 19.2.3.4, 19.2.3.5 | LS.02.01.20- EP 14 LS.02.01.20- EP 19 | NFPA 101 19.2.3.4, 19.2.3.5 | IFC 1031.3.1 1104.15 1105.5.4; 1105.5.5; 1105.5.8 | IFC 1031.3.1, 1104.15, 1105.5.4; 1105.5.5; 1105.6.7 Commentary: IFC does not include provisions for fixed furniture or non-continuous projections above handrail height. IFC 1104.15 permits ramps to be a minimum of 30 inches wide. NFPA 101, 19.2.3.4 (1) requires ramps in adjunct areas to be a minimum of 44 inches wide. | IFC 1031.3.1 Group I-2 1104.15 Width of ramps 1105.6.4 Ramps (width) 1105.6.5 Corridor width 1105.6.8 Aisles (width) | Frequently asked questions on the new CMS regulations (June 7, 2016) HITF Interpretations, January 2014 | Issue: Width of circulating space in suite. Is it 8ft or 3 ft?
|  | Aisle, Corridor or Ramp Width 2012 NEW The width of aisles or corridors (clear and unobstructed) serving as exit access in hospitals and nursing homes shall be at least 8 feet. In limited care facility and psychiatric hospitals, width of aisles or corridors shall be at least 6 feet, except as modified by the 18.2.3.4 or 18.2.3.5 exceptions. 18.2.3.4, 18.2.3.5 | LS.02.01.20- EP 14 LS.02.01.20- EP 18 | NFPA 101 18.2.3.4, 18.2.3.5 | IBC 407.4.3 1018.5 1020.2; 1020.3. IFC 1031.3 | IBC 407.4.3, 1018.5, 1020.2; 1020.3. IFC 1031.3 Commentary: IBC projection provisions in section 407.4.3 apply in nursing homes only. IFC does not include provisions for fixed furniture or non-continuous projections above handrail height. | IBC 407.4.3 Projections in nursing home corridors 1018.5 Aisles in other than assembly spaces and Groups B and M 1020.3 Width and Capacity 1020.4 Obstruction IFC 1031.3 Obstructions | Frequently asked questions on the new CMS regulations (June 7, 2016) HITF Interpretations, December 2007 HITF Interpretations, January 2014 | E118-12 D, E112-12 AS
K233 | General | Clear Width of Exit and Exit Access Doors 2012 EXISTING Exit access doors and exit doors are of the swinging type and are at least 32 inches in clear width. Exceptions are provided for existing 34-inch doors and for existing 28-inch doors where the fire plan does not require evacuation by bed, gurney, or wheelchair. 19.2.3.6, 19.2.3.7 | LS.02.01.20- EP 20 | NFPA 101 19.2.3.6, 19.2.3.7 | IBC 1010.1.1 | IBC 1010.1.1 | IBC 1010.1.1 Size of doors |  | G46-18 AS, 37-18 AM, 38-18 AS, 40-18 AMPC1 Commentary: IBC requirements differ for existing doors. No allowance for 32 inch doors in existing health care occupancies or 28 inch doors in existing adjunct areas.
|  | Clear Width of Exit and Exit Access Doors 2012 NEW Exit access doors and exit doors are of the swinging type and are at least 41-1/2 inches in clear width. In psychiatric hospitals or limited care facilities, doors are at least 32 inches wide. Doors not subject to patient use, in exit stairway enclosures, or serving newborn nurseries shall be no less than 32 inches in clear width. If using a pair of doors, the doors shall be provided with a rabbet, bevel, or astragal at the meeting edge, at least one of the doors shall provide 32 inches in clear width, and the inactive leaf of the pair shall be secured with automatic flush bolts. 18.2.3.6, 18.2.3.7 | LS.02.01.20- EP 21 | NFPA 101 18.2.3.6, 18.2.3.7 | IBC 1010.1.1 | IBC 1010.1.1 | IBC 1010.1.1 Size of doors |  | 37-18 AM, 39-18 AS, 40-18 AMPC1
K241 | General | Number of Exits – Story and Compartment Not less than two exits, remote from each other, and accessible from every part of every story are provided for each story. Each smoke compartment shall likewise be provided with two distinct egress paths to exits that do not require the entry into the same adjacent smoke compartment. 18.2.4.1-18.2.4.4, 19.2.4.1-19.2.4.4 | LS.02.01.20- EP 16 | NFPA 101 18/19.2.4.1; 18/19.2.4.2; 18/19.2.4.3; 18/19.2.4.4 | IBC 407.5; 407.5.2 1006.3, Table 1006.3.1 1007.1; 1007.1.1 IFC 1105.6; 1105.6.1 | IBC 407.5; 407.5.3, 1006.3.2, Table 1006.3.2 1007.1; 1007.1.1 IFC 1105.6; 1105.6.1 | IBC 407.5 Smoke barriers 407.5.3 Refuge area 1006.2.1 Egress based on occupant load and common path of egress travel distance Table 1006.2.1 Spaces with one exit or exits access doorway 1007.1 General 1007.1.1 Two exits or exit access doorways IFC 1105.6 Means of egress 1105.6.1 Two means of egress 1105.6.2 Size of doors |  | F189-18 AS
K251 | General | Dead-End Corridors and Common Path of Travel 2012 EXISTING Dead-end corridors shall not exceed 30 feet. Existing dead-end corridors greater than 30 feet shall be permitted to be continued to be used if it is impractical and unfeasible to alter them. 19.2.5.2 | LS.02.01.20- EP 25 | NFPA 101 19.2.5.2 | IFC 1104.18; TABLE 1104.18 1104.20 1105.5.6 | IFC 1104.18; TABLE 1104.18, 1104.20, 1105.6.5 IEBC 805.6 | IFC 1104.18 Dead ends TABLE 1104.18 COMMON PATH, DEAD-END AND TRAVEL DISTANCE LIMITS (by occupancy) 1104.20 Common path of egress travel 1105.6.6 Dead-end corridors IEBC 804.7 Dead-end corridors |  | Phil B - No Changes recommended
|  | Dead-End Corridors and Common Path of Travel 2012 NEW Dead-end corridors shall not exceed 30 feet. Common path of travel shall not exceed 100 feet. 18.2.5.2, 18.2.5.3 | LS.02.01.20- EP 25 | NFPA 101 18.2.5.2, 18.2.5.3 | IBC 1006.2 1020.4 | IBC 1006.2, 1020.4 | IBC 1006.2 Egress from spaces 1020.6 Air movement in corridors 1020.5 Dead ends (Exception 4) |  | E91-18 AS Phil B - No changes recommended
K252 | General | Number of Exits – Corridors Every corridor shall provide access to not less than two approved exits in accordance with Sections 7.4 and 7.5 without passing through any intervening rooms or spaces other than corridors or lobbies. 18.2.5.4, 19.2.5.4 | LS.02.01.20- EP 17 | NFPA 101 18/19.2.5.4 | IBC 407.2 1016.2 1020.6 | IBC 407.2, 1016.2, 1020.6 | IBC 407.2 Corridors continuity and separation 1016.2 Egress through intervening spaces 1020.7 Corridor continuity |  | Phil B - No Changes recommended
K253 | General | Number of Exits – Patient Sleeping and Non-Sleeping Rooms Patient sleeping rooms of more than 1,000 square feet or nonsleeping rooms of more than 2,500 square feet have at least two exit access doors remotely located from each other. 18.2.5.5.1, 18.2.5.5.2, 19.2.5.5.1, 19.2.5.5.2 | LS.02.01.20- EP 27 | NFPA 101 18/19.2.5.5.1; 18/19.2.5.5.2 | IBC 1006 407.4.4.5.2 407.4.4.6.2 | IBC 1006, 407.4.4.5.2, 407.4.4.6.2 | IBC 1006 Number of Exits and Exit Access Doorways 407.4.4.5.2 Exit access (Care suites containting sleeping room areas) 407.4.4.6.2 Exit access (Care suites not containing sleeping rooms) |  | Phil B - No Changes recommended
K254 | General | Corridor Access. All habitable rooms not within suites have a door leading directly outside to grade or have a door leading to an exit access corridor. Patient sleeping rooms with less than eight patient beds may have one room intervening to reach an exit access corridor provided the intervening room is equipped with an approved automatic smoke detection system. 18.2.5.6.1 through 18.2.5.6.4, 19.2.5.6.1 through 19.2.5.6.4 | LS.02.01.20- EP 26 | NFPA 101 18/19.2.5.6.1; 18/19.2.5.6.2; 18/19.2.5.6.3; 18/19.2.5.6.4 | IBC 407.4.1 407.4.4.5 Commentary: IBC does not contain requirement for smoke detection of intervening room. | IBC 407.4.1 407.4.4.5 | IBC 407.4.1 Direct access to a corridor 407.4.4.5 Care suites containing sleeping rooms areas |  | Phil B - No Changes recommended
K255 | General | Suite Separation, Hazardous Content, and Subdivision All suites are separated from the remainder of the building (including from other suites) by construction meeting the separation provisions for corridor construction (18.3.6.2-18.3.6.5 or 19.3.6.2-19.3.6.5). Existing approved barriers shall be allowed to continue to be used provided they limit the transfer of smoke. Intervening rooms have no hazardous areas and hazardous areas within suites comply with 18/19.2.5.7.1.3. Subdivision of suites shall be by noncombustible or limited-combustible construction. 18.2.5.7.1.2 through 18.2.5.7.1.4, 19.2.5.7.1.2, 19.2.5.7.1.3, 19.2.5.7.1.4 | LS.02.01.20 - EP 28 LS.02.01.20 - EP 29 | NFPA 101 18/19.2.5.7.1.2; 18/19.2.5.7.1.3; 18/19.2.5.7.1.4 18.3.6.2; 18.3.6.3; 18.3.6.4; 18.3.6.5 | IBC 407.4.4.2 | IBC 407.4.4.2 | IBC 407.4.4.2 Separation | LS.02.01.20 Improper Use or Designation of Suites [EP 13] | G70-12 AS - Phil B - No changes recommended
K256 | General | Sleeping Suites Occupants shall have exit access to a corridor or direct access to a horizontal exit. Where ≥ 2 exits are required, one exit access door may be to a stairway, passageway or to the exterior. Suites shall be provided with constant staff supervision. Staff shall have direct visual supervision of patient sleeping rooms, from a constantly attended location or the room shall be provided with an automatic smoke detection system. Suites more than 1,000 square feet shall have 2 or more remote exits. One means of egress from the suite shall be to a corridor and one may be into an adjacent suite separated in accordance with corridor requirements. Suites shall not exceed the following size limitations:  5,000 square feet if the suite is not fully smoke detected or fully sprinklered  7,500 square feet if the suite is either fully smoke detected or fully sprinklered  10,000 square feet if the suite is both fully smoke detected and fully sprinklered and the sleeping rooms have direct supervision from a constantly attended location Travel distance between any point in a suite to exit access shall not exceed 100 ft. and distance to an exit shall not exceed 150 ft. (200 ft. if building is fully sprinklered). 18.2.5.7.2, 19.2.5.7.2 | LS.02.01.20 - EP 30 LS.02.01.20 - EP 32 LS.02.01.20 - EP 33 LS.02.01.20 - EP 35 LS.02.01.20 - EP 36 Commentary: TJC requirements do not directly address access to a suite must have access to either a door to an exit access corridor or a horizontal exit. | NFPA 101 18/19.2.5.7.2.1; 18/19.2.5.7.2.2 NFPA 101 18/19.2.5.7.2.3; 18/19.2.5.7.2.4 | IBC 1006 407.4.1; 407.4.4.1; 407.4.4.5.1; 407.4.4.5.2; 407.4.4.6.2 IBC 407.4.4; 407.4.4.3; 407.4.4.5; 407.4.4.5.1; Commentary: IBC requirements do not permit access to a horizontal exit in lieu of direct access to a corridor. | IBC 1006 407.4.1; 407.4.4.1; 407.4.4.5.1; 407.4.4.5.2; 407.4.4.6.2 IBC 407.4.4; 407.4.4.3; 407.4.4.5; 407.4.4.5.1; | IBC 1006 Number of Exits and Exit Access Doorways 407.4.1 Direct access to a corridor 407.4.4.1 Exit access through care suites 407.4.4 Group I-2 care suites 407.4.4.3 Access to corridor 407.4.4.5 Care suites containing sleeping rooms areas 407.4.4.5.1 Area 407.4.4.5.2 Exit access (care suites containing sleeping room areas) 407.4.4.6.2 Exit access (care suites not containing sleep rooms) | Frequently asked questions on the new CMS regulations (June 7, 2016) | G70-12 AS, G43-18 AMPC1, G43-18 AS PC,G44-18 D - Phil B - No changes recommended
K257 | General | Non-Sleeping Suites Occupants shall have exit access to a corridor or direct access to a horizontal exit. Where ≥ 2 exits are required, one exit access door may be to a stairway, passageway or to the exterior. Suites more than 2,500 square feet shall have 2 or more remote exits. One means of egress from the suite shall be to a corridor and one may be into an adjacent suite separated in accordance with corridor requirements. Suites shall not exceed 10,000 square feet. Travel distance between any point in a suite to exit access shall not exceed 100 ft. and distance to an exit shall not exceed 150 ft. (200 ft. if building is fully sprinklered). 18.2.5.7.3, 19.2.5.7.3 | LS.02.01.20 - EP 31 LS.02.01.20 - EP 34 LS.02.01.20 - EP 35 LS.02.01.20 - EP 36 Commentary: TJC requirements do not directly address access to a suite must have access to either a door to an exit access corridor or a horizontal exit. | NFPA 101 18/19.2.5.7.3; 18/19.2.5.7.3.1; 18/19.2.5.7.3.2; 18/19.2.5.7.3.3; 18/ 19.2.5.7.3.4; 18/19.2.5.7.4 | IBC 1006 407.4.4.6; 407.4.4.6.1; 407.4.4.6.2 | IBC 1006 407.4.4.6; 407.4.4.6.1; 407.4.4.6.2 | IBC 1006 Number of Exits and Exit Access Doorways 407.4.4.6 Care suites not containing sleeping rooms 407.4.4.6.1 Area 407.4.4.6.2 Exit access | HITF Interpretations, June 2007 HITF Interpretations, June 2010 | G43-18 AMPC1 - Phil B - No changes recommended
K261 | General | Travel Distance to Exits Travel distance (excluding suites) to exits are measured in accordance with 7.6.  From any point in the room or suite to exit ≤ 150 feet (≤ 200 ft. if the building is fully sprinklered)  Point in a room to room door ≤ 50 ft. 18.2.6, 19.2.6 | LS.02.01.20 - EP 37 | NFPA 101 18/19.2.6; 18/19.2.6.1; 18/19.2.6.2; 18.2.6.2.3; 19.2.6.2.1; 19.2.6.2.2; 18/19.2.6.2.3; 18/19.2.6.2.4 | IBC | IBC 407.4.2, 1017; 1017.1; 1017.2, Table 1017.2 IFC 1104.19, Table 1104.18 | IBC 407.4.2 Distance of travel 1017 Exit Access Travel Distance 1017.1 General 1017.2 Limitations Table 1017.2 Exit Access Travel Distance IFC 1104.19 Exit access travel distance Table 1104.18 COMMON PATH, DEAD-END AND TRAVEL DISTANCE LIMITS (by occupancy) |  | G31-18 AS, G48-18 AS - Phil B - No Changes recommended
K271 | General | Discharge from Exits. Exit discharge is arranged in accordance with 7.7, provides a level walking surface meeting the provisions of 7.1.7 with respect to changes in elevation and shall be maintained free of obstructions. Additionally, the exit discharge shall be a hard packed all- weather travel surface in accordance with CMS Survey and Certification Letter 05-38. 18.2.7, 19.2.7, S&C 05-38 | LS.02.01.20 - EP 12 | NFPA 101 18/19.2.7 7.1.7 7.7. | IBC 1003.4; 1003.5; 1003.6 1006.3 1028.5 | IBC 1003.4; 1003.5; 1003.6, 1006.3, 1028.5 | IBC 1003.4 Slip-resistant surface 1003.5 Elevation change 1003.6 Means of egress continuity 1006.3 Egress from stories or occupied roofs 1028.5 Access to a public way | HITF Interpretations, June 2009 | IBC requires exterior door needs to be visible, 101 is path of travel is apparent E4-18 AM, E37-18 AM, E18-18 ASPC2
K281 | MEP | Illumination of Means of Egress Illumination of means of egress, including exit discharge, is arranged in accordance with 7.8 and shall be either continuously in operation or capable of automatic operation without manual intervention. 18.2.8, 19.2.8 PZ comment Section 7.8 indicates failure of lamp OK to reduce to .2 fc which applies to both normal and emerg power. | LS.02.01.20- EP 38 LS.02.01.20- EP 39 | NFPA 101 18/19.2.8 7.8; 7.8.1.2; 7.8.1.2.2; 7.8.1.2.3 | IBC 1008;1008.1 1008.2; 1008.2.1; 1008.2.2; 1008.2.3 1008.3; 1008.3.1; 1008.3.2; 1008.3.3 | IBC 1008;1008.1, 1008.2; 1008.2.1; 1008.2.2; 1008.2.3, 1008.3; 1008.3.1; 1008.3.2; 1008.3.3 IFC 1104.5 IEBC 805.7,805.7.1,905.2 | IBC 1008 Means of Egress Illumination 1008.1 Means of egress illumination 1008.2 Illumination required 1008.2.1 Illumination level under normal power 1008.2.2 Group I-2 1008.2.3 Exit discharge 1008.3 Emergency power for illumination 1008.3.1 General 1008.3.2 Buildings 1008.3.3 Rooms and spaces IFC 1104.5 Illumination emergency power | HITF Interpretations, June 2009 | E27-12 D, E33-12 AS, E27-18 AS, 37-18 AM, 28-18 AS, I-2 Occupancies failure of one lamp | Complete | Pier
K291 | MEP | Emergency Lighting Emergency lighting of at least 1½-hour duration is provided automatically in accordance with 7.9. 18.2.9.1, 19.2.9.1 | LS.02.01.20- EP 39 Commentary: No specific TJC requirement. Reference is to General 18/19.2 citation. | NFPA 101 18/19.2.9; 18/19.2.9.1 7.9.2; 7.9.2.1 | IBC 1008.3.4 IFC 1104.5 | IBC 1008.3.4 IFC 1104.5 | IBC 1008.3.4 Duration IFC 1104.5 Illumination emergency power | EC.02.05.01 Lack of Emergency Lighting [EP1] |  | Complete | Pier
K292 | MEP | Life Support Means of Egress (New). Buildings equipped with or requiring the use of life support systems (electro-mechanical or inhalation anesthetics) have illumination of means of egress, emergency lighting equipment, exit, and directional signs supplied by the life safety branch of the electrical system described in NFPA 99. (Indicate N/A if life support equipment is for emergency purposes only.) 18.2.9.2, 18.2.10.5 2018 IBC 2702.2.8 Group I-2 occupancies. Essential electrical systems for Group I-2 occupancies shall be in accordance with Section 407.11. F] 407.11 Electrical systems. In Group I-2 occupancies, the essential electrical system for electrical components, equipment and systems shall be designed and constructed in accordance with the provisions of Chapter 27 and NFPA 99. F] 2702.2.1 Ambulatory care facilities. Essential electrical systems for ambulatory care facilities shall comply with Section 422.6. | LS.02.01.20- EP 42 | NFPA 101 18.2.9.2 18.2.10.5 18.5.1.3 | IFC 1105.10; 1105.10.1; 1105.10.2 IBC 407.10 2702.2.1; 2702.2.6 | IFC 1105.11; 1105.11.1; 1105.11.2 IBC 407.10, 422.6, 2702.2.1; 2702.2.6 | IFC 1105.11 Essential electrical systems 1105.11.1 Where required 1105.11.2 Installation and duration IBC 407.11 Electrical systems 422.6 Electrical systems 2702.2.1 Ambulatory care facilities 2702.2.6 Exit signs |  |  | Complete | Pier
K293 | MEP | Exit Signage 2012 EXISTING Exit and directional signs are displayed in accordance with 7.10 with continuous illumination also served by the emergency lighting system. 19.2.10.1 (Indicate N/A in one-story existing occupancies with less than 30 occupants where the line of exit travel is obvious.) 19.2.10.2 2015 IFC1104.5.1 Emergency power duration and installation. Emergency power for means of egress illumination shall be provided in accordance with Section 604. In other than Group I-2, the emergency power system shall provide power be provided for not less than 60 minutes and consist of storage batteries, unit equipment or an on-site generator. for systems requiring emergency power. In Group I-2, the emergency power system essential electrical systems shall provide power for not less than 90 minutes and consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance comply with Section 604. Sections 1105.5.1 and 1105.5.2. | LS.02.01.20- EP 40 | NFPA 101 19.2.10; 19.2.10.1; 19.2.10.2; 19.2.10.3; 19.2.10.4 7.10 | IFC 1104.3; 1104.4; 1031.4 | IFC 1104.3, 1104.4, 1031.4 IEBC 805.8; 805.8.1; 805.8.2, 905.3 | IFC 1104.3 Exit sign illumination 1104.4 Power source 1031.4 Exit signs IEBC 804.9 Exit signs 804.9.1 Work areas 804.9.2 Supplemental requirements for exit signs 905.3 Exit signs | HITF Interpretations, November 1998 | NFPA 101 19.2.10.4 exit signage in sleepg ste rqd if staff .. Yes exit signage in IIC must be illum in normal & emerg mode. 1104.3 Exit sign illumination. Exit signs shall be internally or externally illuminated. The face of an exit sign illuminated from an external source shall have an intensity of not less than 5 footcandles (54 lux). Internally illuminated signs shall provide equivalent luminance and be listed for the purpose. Exception: Approved self-luminous signs that provide evenly illuminated letters shall have a minimum luminance of 0.06 foot-lamberts (0.21 cd/m2). 1104.4 Power source. Where emergency illumination is required in Section 1104.5, exit signs shall be visible under emergency illumination conditions. Exception: Approved signs that provide continuous illumination independent of external power sources are not required to be connected to an emergency electrical system. 1104.5 Illumination emergency power. The Where means of egress illumination is provided, the power supply for means of egress illumination shall normally be provided by the premises' electrical supply. in the evnt of power supply failure, illumination shalll be automatically provided from an emergency system for the following occupancies where such occupancies require two or more means of egress: | Complete | Pier
|  | Exit Signage 2012 NEW Exit and directional signs are displayed in accordance with 7.10 with continuous illumination also served by the emergency lighting system. 18.2.10.1 | LS.02.01.20- EP 40 | NFPA 101 18.2.10; 18.2.10.1; 18.2.10.3; 18.2.10.4; 18.2.10.5 7.10 | IEBC 805.8; 805.8.1;805.8.2 905.3 | IBC 1013 | IBC 1013 Exit signs |  | E103-12 AMPC Review against 2021 version of NFPA 99 | Complete | Pier
K300 | General | Protection – Other List in the REMARKS section any LSC Section 18.3 and 19.3 Protection requirements that are not addressed by the provided K- tags, but are deficient. This information, along with the applicable Life Safety Code or NFPA standard citation, should be included on Form CMS-2567. | LS.02.01.30- EP 26 | N/A | N/A | N/A | N/A | Focus on Compliance: Life safety protection (LS.02.01.30) (June/July 2016)
K311 | Fire | Vertical Openings – Enclosure 2012 EXISTING Stairways, elevator shafts, light and ventilation shafts, chutes, and other vertical openings between floors are enclosed with construction having a fire resistance rating of at least 1 hour. An atrium may be used in accordance with 8.6. 19.3.1.1, through 19.3.1.6 If all vertical openings are properly enclosed with construction providing at least a 2-hour fire resistance rating, also check this box. | LS.02.01.30- EP 1 | NFPA 101 19.3.1; 19.3.1.1; 19.3.1.2;19.3.1.3; 19.3.1.4; 19.3.1.5; 19.3.1.6 | IEBC 501.2 803.2; 803.2.1; 803.2.2; 803.2.3 903.1 IFC 1103.4; 1103.4.1 | IEBC 501.2 802.2; 802.2.1; 802.2.2; 802.2.3 903.1 IFC 1103.4; 1103.4.1 | IEBC 501.2 Fire-resistance ratings 802.2 Vertical openings 802.2.1 Existing vertical openings 802.2.2 Supplemental shaft and floor opening enclosure requirements 802.2.3 Supplemental stairway enclosure requirements 903.1 Existing shafts and vertical openings IFC 1103.4 Vertical openings 1103.4.1 Group I-2 and I-3 occupancies |  |  |  | Wayne/Ed
|  | Vertical Openings – Enclosures 2012 NEW Stairways, elevator shafts, light and ventilation shafts, chutes, and other vertical openings between floors are enclosed with construction having a fire resistance rating of at least 2 hours connecting four or more stories. (1 hour for single story building and buildings up to three stories in height.) An atrium may be used in accordance with 8.6.7. 18.3.1 through 18.3.1.5 | LS.02.01.30- EP 1 | NFPA 101 18.3.1; 18.3.1.2; 18.3.1.3; 18.3.1.4; 18.3.1.5 8.6 | IBC 712; 713 | IBC 712; 713 | IBC 712 Vertical Openings 713 Shaft Enclosures |  | G54-12 AM Is there is an allowance for an atrium as long as it is not open to patient care or sleeping room in Group I-2. 18.3.7.3 FS38-18-AS Add a proposal to restrict patient rooms from being open to atrium and 2) allow for wetted glass wall to serve as smoke baerier (instead of 1 hour). Secion 709.4.1 and 709.4.2 or Section 407 or atrium provisions? 10-19-2020: Wayne to look at atriums |  | Wayne/Ed
K321 | Fire | Hazardous Areas – Enclosure 2012 EXISTING Hazardous areas are protected by a fire barrier having 1-hour fire resistance rating (with 3/4-hour fire rated doors) or an automatic fire extinguishing system in accordance with 8.7.1. When the approved automatic fire extinguishing system option is used, the areas shall be separated from other spaces by smoke resisting partitions and doors in accordance with 8.4. Doors shall be self-closing or automatic-closing and permitted to have nonrated or field-applied protective plates that do not exceed 48 inches from the bottom of the door. Describe the floor and zone locations of hazardous areas that are deficient in REMARKS. 19.3.2.1 Area Automatic Sprinkler Separation N/A a. Boiler and Fuel-Fired Heater Rooms b. Laundries (larger than 100 square feet) c. Repair, Maintenance, and Paint Shops d. Soiled Linen Rooms (exceeding 64 gallons) e. Trash Collection Rooms (exceeding 64 gallons) f. Combustible Storage Rooms/Spaces (over 50 square feet) g. Laboratories (if classified as Severe Hazard - see K322) | LS.02.01.30- EP 3 | NFPA 101 19.3.2; 19.3.2.1; 19.3.2.1.1; 19.3.2.1.2; 19.3.2.1.3; 19.3.2.1.4; 19.3.2.1.5 8.4 | IFC 1105.3; 1105.3.1; 1105.3.2; 1105.3.3; 1105.3.3.1; 1105.3.3.2; 1105.3.3.2.1; TABLE 1105.3 IEBC 902.2 | IFC 1105.4; 1105.4.1; 1105.4.2; 1105.4.3; 1105.4.3.1; 1105.4.3.2; 1105.4.3.2.1; TABLE 1105.3 IEBC 902.2 | IFC 1105.4 Incidental uses in existing Group I-2 1105.4.1 Occupancy classification 1105.4.2 Area limitations 1105.4.3 Separation and protection 1105.4.3.1 Separation 1105.4.3.2 Protection 1105.4.3.2.1 Protection limitation TABLE 1105.3 FLOOR LEVEL LIMITATIONS FOR GROUP I-2, CONDITION 2 IEBC 902.2 Boiler and furnace equipment rooms | HITF Interpretations, June 2008 | Boiler room commentary Table 1105.4 includes specifications about the specific equipment in the room which are required to be enclosed or have a sprinkler (steam of 15 psig or more, water of 170 psig or more, furnace with 400,000 BTUs or more). Laundry room (over 100sf) Table 1105.4 is consistent Paint shops Table 115.4 not classified as Gour H require 2 hours; or 1 hour and provide automatic sprinkler system Physical Plant maintenance shops Table 1105.4 language is consistent Soiled linen rooms & Waste collection rooms: Table 1105.4 waste and linen collection rooms with containers that have an aggregate volume of 10 cubic feet or greater (vs 64 gallons) do not have the automatic sprinkler exception. 64 gallons = 8.66 ft3 Combustible Storage Room: Table 1105.4 lists the following: Stationary storage battery systems having a liquid electrolyte capacity of more than 50 gallons for flooded lead-acid, nickel cadmium or VRLA, or more than 1,000 pounds for lithium-ion and lithium metal polymer used for facility standby power, emergency power or uninterruptable power supplies: requires 2 hours separation I did not see anything for laboratories that are High Hazardous areas: Table 1105.4 lists laboratories NOT classified as Group H to have 1 hour or sprinkler system. 10-19-2020:Incidential use group table for consistency for rating and sprinkler |  | Maggie Bill
|  | Hazardous Areas – Enclosure 2012 NEW Hazardous areas are protected in accordance with 18.3.2.1. The areas shall be enclosed with a 1-hour fire-rated barrier, with a 3/4- hour fire-rated door without windows (in accordance with 8.7.1.1). Doors shall be self-closing or automatic-closing in accordance with 7.2.1.8. Hazardous areas are protected by a sprinkler system in accordance with 9.7, 18.3.2.1, and 8.4. Describe the floor and zone locations of hazardous areas that are deficient in REMARKS. 18.3.2.1, 7.2.1.8, 8.4, 8.7, 9.7 Area Automatic Sprinkler Separation N/A a. Boiler and Fuel-Fired Heater Rooms b. Laundries (larger than 100 square feet) c. Repair, Maintenance, and Paint Shops d. Soiled Linen Rooms (exceeding 64 gallons) e. Trash Collection Rooms (exceeding 64 gallons) f. Combustible Storage Rooms/Spaces (over 50 and less than 100 sq ft) g. Combustible Storage Rooms/Spaces (over 50 square feet) h. Laboratories (if classified as Severe Hazard - see K322) | LS.02.01.30- EP 2 | NFPA 101 18.3.2.1 | IBC 509 TABLE 509 | IBC 509, TABLE 509 | IBC 509 Incidental Uses TABLE 509 Incidental Uses |  | G130-12 AS IBC 2018 Boiler room commentary Table 509 includes specifications about the specific equipment in the room which are not required to be enclosed (steam of 15 psig or less, water of 170 psig or less, furnace with 400,000 BTUs or less) or have a sprinkler. Laundry room (over 100sf) Table 509 does not allow automatic sprinkler exception in Group I-2 Paint shops Table 509: in occupancies other than Group F require 2 hours; or 1 hour and provide automatic sprinkler system Physical Plant maintenance shops Table 509 require 1 hour separation (does not permit automatic sprinkler system as an option) Soiled linen rooms: Table 509 In ambulatory care facilities or Group I-2 occupancies, waste and linen collection rooms with containers that have an aggregate volume of 10 cubic feet or greater (vs 64 gallons) do not have the automatic sprinkler exception. 64 gallons = 8.66 ft3 In other than ambulatory care facilities and Group I-2 match the language (1 hour or sprinkler system) I did not see anything for laboratories that are High Hazardous areas: Table 509 lists laboratories NOT classified as Group H to have 1 hour or sprinkler system. Section 307/High Hazard Group H does not mention laboratories. Section 414/Hazardous Materials (doesn’t address rooms, only materials and quantities). Section 428 is laboratories in higher education use group. |  | Maggie Bill
K322 | Fire | Laboratories Laboratories employing quantities of flammable, combustible, or hazardous materials that are considered a severe hazard are protected by 1-hour fire resistance-rated separation, automatic sprinkler system, and are in accordance with 8.7 and with NFPA 99. Laboratories not considered a severe hazard are protected as hazardous areas (see 0321). Laboratories using chemicals are in accordance with NFPA 45. Gas appliances are of appropriate design and installed in accordance with NFPA 54. Shutoff valves are marked to identify material they control. Devices requiring medical grade oxygen from the piped distribution system meet the requirements under 11.4.2.2 (NFPA 99). 18.3.2.2, 19.3.2.2, 8.7, 8.7.4.1 (LSC) 9.3.1.2, 11.4.3.2, 15.4 (NFPA 99) | LS.02.01.30- EP 2 LS.02.01.30- EP 3 LS.02.01.30- EP 4 | NFPA 101 9.3.1.2, 11.4.3.2, 15.4 (NFPA 99) 8.7.4; 8.7.4.1; 8.7.4.2 NFPA 99 9.3.1.2; 11.4.3.2; 15.4 | IFC 907.5.2.2.5 | IFC 5003.8; 5003.8.1; 5003.8.3; 5003.8.3.1; 5003.8.3.2; 5003.8.3.3; 5003.8.3.4; 5003.9.2; 5704.3; 5704.3.1; 5704.3.1.1; 5704.3.2; 5704.3.2.1; 5704.3.2.1.1; 5704.3.2.1.2; 5704.3.2.1.3; 5704.3.2.1.4 ; 5704.3.2.2; 603; 603.1; 603.1.1 IMC 510; 510.1; 510.2 IPC 411; 411.1; 411.2; 411.3 IBC 509; TABLE 509 ICCPC 2201.3.10 | IFC 5003.8 Construction requirements 5003.8.1 Buildings 5003.8.3 Control areas 5003.8.3.1 Construction requirements 5003.8.3.2 Percentage of maximum allowable quantities 5003.8.3.3 Number 5003.8.3.4 Fire-resistance rating requirements 5003.9.2 Security 5704.3 Container and portable tank storage 5704.3.1 Design, construction and capacity of containers and portable tanks 5704.3.1.1 Approved containers 5704.3.2 Liquid storage cabinets 5704.3.2.1 Design and construction of storage cabinets 5704.3.2.1.1 Materials 5704.3.2.1.2 Labeling 5704.3.2.1.3 Doors 5704.3.2.1.4 Bottom 5704.3.2.2 Capacity 603 Electrical equipment, wiring and systems 603.1 General 603.1.1 Equipment and wiring IMC 510 HAZARDOUS EXHAUST SYSTEMS 510.1 General 510.2 Where required IPC 411 EMERGENCY SHOWERS AND EYEWASH STATIONS 411.1 Approval 411.2 Waste connection 411.3 Water supply IBC 509 Incidental Uses TABLE 509 Incidental Uses ICCPC 2201.3.10 Ventilation |  | Allowance to use educational lab facilities in IFC, alignment in 101 F192-18 AS P42-19 AS 10-5-2020: Jeff working with BCAC for clinical and research labs 10-19-2020: Labs - in progress with BCAC |  | Jeff
K323 | MEP | Anesthetizing Locations Areas designated for administration of general anesthesia (i.e., inhalation anesthetics) are in accordance with 8.7 and NFPA 99. Zone valves are: located immediately outside each anesthetizing location for medical gas or vacuum; readily accessible in an emergency; and arranged so shutting off any one anesthetizing location will not affect others. Area alarm panels are provided to monitor all medical gas, medical-surgical vacuum, and piped WAGD systems. Panels are at locations that provide for surveillance, indicate medical gas pressure decreases of 20% and vacuum decreases of 12 inch gauge HgV, and provide visual and audible indication. Alarm sensors are installed either on the source side of individual room zone valve box assemblies or on the patient/use side of each of the individual zone box valve assemblies. The EES critical branch supplies power for task illumination, fixed equipment, select receptacles, and select power circuits, and EES equipment system supplies power to ventilation system. Heating, cooling, and ventilation are in accordance with ASHRAE 170. Medical supply and equipment manufacturer’s instructions for use are considered before reducing humidity levels to those allowed by ASHRAE, per S&C 13-58. Supply and exhaust systems for windowless anesthetizing locations have smoke control system(s) to automatically vent smoke, prevent the recirculation of smoke originating within the surgical suite, and prevent the circulation of smoke entering the system intake, without interfering with exhaust function, per 79 FR 21551. 18.3.2.3, 19.3.2.3 (LSC) 5.1.4.8.7, 5.1.4.8.7.2, 5.1.9.3, 5.1.9.3.4, 6.4.2.2.4.2 (NFPA 99) | LS.02.01.30- EP 26 Commentary: No specific TJC requirement. Reference is to General 18/19.3 citation. | NFPA 101 18/19.3.2.3 8.7 NFPA 99 5.1.4.8.7; 5.1.4.8.7.2; 5.1.9.3; 5.1.9.3.4; 6.4.2.2.4.2 | IFC 5306.5 | IFC 5306.5 | IFC 5306.5 Medical gas systems and equipment | CMS Adoption of ASHRAE 170- 2008 (2016) Chris P. Rousseau, Jonathan Flannery ASHE Advocacy Alert on new guidance on OR humidity, temperature, and ventilation requirements Pressure relationship between operating rooms and other areas Frequently asked questions on the new CMS regulations (June 7, 2016) ASHRAE 170 Interpretations-2013 Outdoor Air Supply | EB49-19 AS ASHRAE 170 referenced IMC 407.1 consider add 170 reference to IEBC 808.2 | Minor Change Needed | JF
K324 | MEP | Cooking Facilities Cooking equipment is protected in accordance with NFPA 96, Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations , unless: • residential cooking equipment (i.e., small appliances such as microwaves, hot plates, toasters) are used for food warming or limited cooking in accordance with 18.3.2.5.2, 19.3.2.5.2 • cooking facilities open to the corridor in smoke compartments with 30 or fewer patients comply with the conditions under 18.3.2.5.3, 19.3.2.5.3, or • Cooking facilities in smoke compartments with 30 or fewer patients comply with conditions under 18.3.2.5.4, 19.3.2.5.4. Cooking facilities protected according to NFPA 96 per 9.2.3 are not required to be enclosed as hazardous areas, but shall not be open to the corridor. 18.3.2.5.1 through 18.3.2.5.4, 19.3.2.5.1 through 19.3.2.5.5, 9.2.3, TIA 12-2 | LS.02.01.30- EP 5 LS.02.01.35- EP 11 LS.02.01.35- EP 12 LS.02.01.35- EP 13 | NFPA 101 18/19.3.2.5; 18/19.3.2.5.1; 18/19.3.2.5.2; 18/19.3.2.5.3; 18/19.3.2.5.4; 18/19.3.2.5.5 | IMC 507.1 IFC 904.13 | IMC 507.1 IFC 904.13 | IMC 507 COMMERCIAL KITCHEN HOODS 507.1 General. IFC 904.14 Domestic cooking systems IBC 407.2.6 Nursing home cooking facilities 407.2.7 Domestic cooking appliances | HITF Interpretations, December 2007 | G40-18 AS , G41-18 | Complete | JF
K325 | Fire | Alcohol Based Hand Rub Dispenser (ABHR) ABHRs are protected in accordance with 8.7.3.1, unless all conditions are met: Corridor is at least 6 feet wide Maximum individual dispenser capacity is 0.32 gal. (0.53 gal. in suites) of fluid and 18 oz. of Level 1 aerosols Dispensers shall have a minimum of 4-foot horizontal spacing Not more than an aggregate of 10 gallons of fluid or 135 oz. aerosol are used in a single smoke compartment outside a storage cabinet, excluding one individual dispenser per room Storage in a single smoke compartment greater than 5 gallons complies with NFPA 30 Dispensers are not installed within 1 inch of an ignition source Dispensers over carpeted floors are in sprinklered smoke compartments ABHR does not exceed 95% alcohol Operation of the dispenser shall comply with Section 18.3.2.6(11) or 19.3.2.6(11) ABHR is protected against inappropriate access 18.3.2.6, 19.3.2.6, 42 CFR Parts 403, 418, 460, 482, 483, and 485 | LS.02.01.30- EP 6 | NFPA 101 18/19.3.2.6 8.7.3.1 | IFC 5705.5; 5705.5.1 IBC 407.4.3 1003.3.3 | IFC 5705.5; 5705.5.1 IBC 407.4.3, 1003.3.3 | IFC 5705.5 Alcohol-based hand rubs classified as Class I or II liquids 5705.5.1 Corridor installations IBC 407.4.3 Projections in nursing home corridors 1003.3.3 Horizontal projections | What you need to know about the CMS adoption of the 2012 Life Safety Code® (May 17, 2016) Video: Changes to the Conditions of Participation impacting health care facilities (June 27, 2016) |  |  | Maggie
K331 | Fire | Interior Wall and Ceiling Finish 2012 EXISTING Interior wall and ceiling finishes, including exposed interior surfaces of buildings such as fixed or movable walls, partitions, columns, and have a flame spread rating of Class A or Class B. The reduction in class of interior finish for a sprinkler system as prescribed in 10.2.8.1 is permitted. 10.2, 19.3.3.1, 19.3.3.2 Indicate flame spread rating(s). | LS.02.01.30- EP 7 | NFPA 101 19.3.3.2 10.2.4 10.2.8.1 | IFC 803.3; Table 803.3 1031.6 IEBC 803.4; 803.4.1 903.3 | IFC 803.3; Table 803.3, 1031.6 IEBC 802.4; 802.4.1, 903.3 | IFC 803.3 Interior finish requirements based on occupancy Table 803.3 INTERIOR WALL AND CEILING FINISH REQUIREMENTS BY OCCUPANCY 1031.6 Finishes, furnishings and decorations IEBC 802.4 Interior finish 802.4.1 Supplemental interior finish requirements 903.3 Interior finish |  | Interior finishes - Further work in nursing homes |  | Maggie
|  | Interior Wall and Ceiling Finish 2012 NEW Interior wall and ceiling finishes, including exposed interior surfaces of buildings such as fixed or movable walls, partitions, columns, and have a flame spread rating of Class A. The reduction in class of interior finish for a sprinkler system as prescribed in 10.2.8.1 is permitted. Individual rooms not exceeding four persons may have a Class A or B finish. Lower half of corridor walls, not exceeding 4 feet in height, may have a Class A or B flame spread rating. 10.2, 18.3.3.1, 18.3.3.2 Indicate flame spread rating(s). | LS.02.01.30- EP 7 | NFPA 101 18.3.3.2; 18.3.3.2.1; 18.3.3.2.2; 10.2.8.1 | IBC 803 IFC 803.3; Table 803.3 1031.6 | IBC 803 IFC 803.3; Table 803.3; 1031.6 | IBC 803 Wall and Ceiling Finishes IFC 803.3 Interior finish requirements based on occupancy Table 803.3 INTERIOR WALL AND CEILING FINISH REQUIREMENTS BY OCCUPANCY 1031.6 Finishes, furnishings and decorations |  |  |  | Maggie
K332 | Fire | Interior Floor Finish 2012 NEW (Indicate N/A for 2012 EXISTING) Interior finishes shall comply with 10.2. Floor finishes in exit enclosures and exit access corridors and spaces not separated by walls that resist the passage of smoke shall be Class I or II. 18.3.3.3.1, 18.3.3.3.2, 18.3.3.3.3, 10.2, 10.2.7.1, 10.2.7.2 | LS.02.01.30- EP 8 | NFPA 101 18.3.3.3; 18.3.3.3.1; 18.3.3.3.2; 18.3.3.3.3 10.2.7.1; 10.2.7.2 | IBC 804 IFC 804.3; 804.3.1; 804.3.3.2 | IBC 804 IFC 804.3; 804.3.1; 804.3.3.2 | IBC 804 Interior Floor Finish IFC 804.3 New interior floor finish 804.3.1 Classification 804.3.3.2 Minimum critical radiant flux |  |  |  | Maggie
K341 | Fire | Fire Alarm System – Installation A fire alarm system is installed with systems and components approved for the purpose in accordance with NFPA 70, National Electric Code, and NFPA 72, National Fire Alarm Code to provide effective warning of fire in any part of the building. In areas not continuously occupied, detection is installed at each fire alarm control unit. In new occupancy, detection is also installed at notification appliance circuit power extenders, and supervising station transmitting equipment. Fire alarm system wiring or other transmission paths are monitored for integrity. 18.3.4.1, 19.3.4.1, 9.6, 9.6.1.8 | LS.02.01.34- EP 1 LS.02.01.34- EP 2 Commentary: No specific CMS requirement for fire- rated enclosure of master fire alarm control panel room. | NFPA 101 18/19.3.4; 18/19.3.4.1 9.6.1.3; 9.6.1.4 9.6.1.8; 9.6.1.8.1; 9.6.1.8.1.1; 9.6.1.8.1.2 NFPA 70 NFPA 72 | IBC 407.7 | IBC 407.7 IFC 907.4.2.1,907.6.2; 907.6.6; 907.6.6.1; 907.6.6.2, 907.8.5, 1103.7; 1103.7.2; 1103.7.3, 1105.9 IEBC 803.4.1.4, 904.2.1 | IBC 407.7 Automatic sprinkler system IFC 907.4.2.1 Location 907.6.2 Power supply 907.6.6 Monitoring 907.6.6.1 Transmission of alarm signals 907.6.6.2 MIY monitoring 907.8.4 Inspection, testing and maintenance 1103.7 Fire alarm systems 1103.7.2 Group I-1 1103.7.3 Group I-2 1105.9 Group I-2 automatic sprinkler system IEBC 803.4.1.4 Group I-3 904.2.1 Manual fire alarm systems | HITF Interpretations, June 2008 | 2018 IFC - 907.4.1 Protection of fire alarm control unit. In areas that are not continuously occupied, a single smoke detector shall be provided at the location of each fire alarm control unit, notification appliance circuit power extenders and supervising station transmitting equipment. Exception: Where ambient conditions prohibit installation of smoke detector, a heat detector shall be permitted. | Andrew/Justin | Andrew/Justin
K342 | Fire | Fire Alarm System – Initiation Initiation of the fire alarm system is by manual means and by any required sprinkler system alarm, detection device, or detection system. Manual alarm boxes are provided in the path of egress near each required exit. Manual alarm boxes in patient sleeping areas shall not be required at exits if manual alarm boxes are located at all nurse’s stations or other continuously attended staff location, provided alarm boxes are visible, continuously accessible, and 200 feet travel distance is not exceeded. 18.3.4.2.1, 18.3.4.2.2, 19.3.4.2.1, 19.3.4.2.2, 9.6.2.5 | LS.02.01.34- EP 3 | NFPA 101 18/19.3.4.2; 18/19.3.4.2.1; 18/19.3.4.2.2 | IFC 907.4; 907.4.2.1 | IFC 907.4; 907.4.2.1 | IFC 907.4 Initiating devices 907.4.2.1 Location |  | HealthCareCommentary 2021- 803.4.1.3 Group I-2. A An automatic fire alarm system shall be installed throughout Group I-2 occupancies as required by Chapter 11 of the International Fire Code.  A manual fire alarm system is required to be provided in the entire Group I-2 occupancy where there is a Level 2 alteration. This is consistent with IFC retroactive provisions that require the entire existing Group I-2 occupancies to be provided with an automatic fire alarm system (see Sections 907.2.6.2 and 1105.10 of the IFC). 2018 IFC 1105.10 Group I-2 automatic fire alarm system. An automatic fire alarm system shall be installed in existing Group I-2 occupancies in accordance with Section 907.2.6.2. Exception: Manual fire alarm boxes in patient sleeping areas shall not be required at exits if located at all nurses’ control stations or other constantly attended staff locations, provided such that manual fire alarm boxes are visible, are provided with ready access, and travel distances required in Section 907.4.2.1 are not exceeded. | Andrew/Justin | Andrew/Justin
K343 | Fire | Fire Alarm – Notification 2012 EXISTING Positive alarm sequence in accordance with 9.6.3.4 are permitted in buildings protected throughout by a sprinkler system. Occupant notification is provided automatically in accordance with 9.6.3 by audible and visual signals. In critical care areas, visual alarms are sufficient. The fire alarm system transmits the alarm automatically to notify emergency forces in the event of a fire. 19.3.4.3, 19.3.4.3.1, 19.3.4.3.2, 9.6.4, 9.7.1.1(1) | LS.02.01.34- EP 5 | NFPA 101 19.3.4.3; 19.3.4.3.1; 19.3.4.3.2; 19.3.4.3.2.1; 19.3.4.3.2.2 | IFC 907.5.2.2.5 | IFC 907.2; 907.2.6.2; 907.5, 907.5.2.1 | IFC 907.2 Where required -- new buildings and structures 907.2.6.2 Group I-2 907.5 Occupant notification 907.5.2.1 Audible alarms |  | This section is addressed. | Andrew/Justin | Andrew/Justin
|  | Fire Alarm – Notification 2012 NEW Positive alarm sequence in accordance with 9.6.3.4 are permitted. Occupant notification is provided automatically in accordance with 9.6.3 by audible and visual signals. In critical care areas, visual alarms are sufficient. The fire alarm system transmits the alarm automatically to notify emergency forces in the event of a fire. Annunciation and annunciation zoning for fire alarm and sprinklers shall be provided by audible and visual indicators and zones shall not be larger than 22,500 square feet per zone. 18.3.4.3 through 18.3.4.3.3, 9.6.4 | LS.02.01.34- EP 4 | NFPA 101 18.3.4.3; 18.3.4.3.1 18.3.4.3.2; 18.3.4.3.2.1 18.3.4.3.3; 18.3.4.3.3.1; 18.3.4.3.3.2; 18.3.4.3.3.3 | IBC 407.8 IFC 907.2.6.2 907.5.2; 907.5.2.1; 907.5.2.2; 907.5.2.2.1; 907.5.2.2.2; 907.5.2.2.3 907.5.2.3; 907.5.2.3.1 | IBC 407.7 IFC 907.2.6.2 907.5.2; 907.5.2.1; 907.5.2.2; 907.5.2.2.1; 907.5.2.2.2; 907.5.2.2.3 907.5.2.3; 907.5.2.3.1 | IBC 407.7 Automatic sprinkler system IFC 907.2.6.2 Group I-2 907.5.2 Alarm notification appliances 907.5.2.1 Audible alarms 907.5.2.2 Emergency voice/alarm communication systems 907.5.2.2.1 Manual override 907.5.2.2.2 Live voice messages 907.5.2.2.3 Alternative uses 907.5.2.3 Visible alarms 907.5.2.3.1 Public use areas and common use areas |  | F144-18 AS, F147-18 AS, F148-18 AS Zones are addressed in 2018 IFC 907.6.4 and references the zone size to be no more than 22,500 sf. | Andrew/Justin | Andrew/Justin
K344 | Fire | Fire Alarm – Control Functions The fire alarm automatically activates required control functions and is provided with an alternative power supply in accordance with NFPA 72. 18.3.4.4, 19.3.4.4, 9.6.1, 9.6.5, NFPA 72 | LS.02.01.34-EP 6 LS.02.01.20- EP 15 | NFPA 101 18/19.3.4.4 9.6.5; 9.6.5.1; 9.6.5.2 NFPA 72 | IFC 907.5.2.2.5 | IFC 907.5.2.2.5 | IFC 907.5.2.2.5 Standby power | . | F149-18 AM 2018 IFC - 907.6.3.1 states that the initiating device shall be announced at an approved onsite location. This location is where the main FACP is locatd along with requested announciator panels. Alternative power supply is required per 2018 IFC 907.6.2 | Andrew/Justin | Andrew/Justin
K345 | Fire | Fire Alarm System – Testing and Maintenance A fire alarm system is tested and maintained in accordance with an approved program complying with the requirements of NFPA 70, National Electric Code, and NFPA 72, National Fire Alarm and Signaling Code. Records of system acceptance, maintenance and testing are readily available. 9.7.5, 9.7.7, 9.7.8, and NFPA 25 9.6.1.3, 9.6.1.5, NFPA 70, NFPA 725 | EC.02.03.05- EPs 1-5 EC.02.03.05- EP 28 | NFPA 101 9.7.5; 9.7.7; 9.7.8 NFPA 25 4.3; 4.4 NFPA 70 NFPA 72 Chapter 14 | IFC 907.6.5 904.4.2 907.8 | IFC 907.6.5 904.4.2 907.8 | IFC 907.6.5 Access 904.4.2 Alarm testing 907.8 Inspection, testing and maintenance | Focus on Compliance: Fire Protection (EC.02.03.05) (February/March 2016) | 2018 IFC - 901.6 & T.901.6.1 reference NFPA 72 as a reference standard to be followed for inspection, testing, & maintainece. | Andrew/Justin | Andrew/Justin
K346 | Fire | Fire Alarm – Out of Service Where required fire alarm system is out of service for more than 4 hours in a 24-hour period, the authority having jurisdiction shall be notified, and the building shall be evacuated or an approved fire watch shall be provided for all parties left unprotected by the shutdown until the fire alarm system has been returned to service. 9.6.1.6 | LS.01.02.01- EP 2 | NFPA 101 9.6.1.6 | IFC 901.7 | IFC 901.7 | IFC 901.8 Systems out of service | HITF Interpretations, June 2009 | Out of service systems 2018 IFC 901.7. States, "immediately". This is more restrictive and can be easily accomplished by the building management individual/staff by calling the fire departments non-emergency number. Which should be listed with the building management important numbers. | Andrew/Justin | Andrew/Justin
K347 | Fire | Smoke Detection 2012 EXISTING Smoke detection systems are provided in spaces open to corridors as required by 19.3.6.1. 19.3.4.5.2 | LS.02.01.34- EP 8 | NFPA 101 19.3.4.5.2; 19.3.6.1 | IBC 407.2 IFC 907.2.6.2 | IBC 407.2 IFC 907.2.6.2 | IBC 407.2 Corridors continuity and separation IFC 907.2.6.2 Group I-2 |  | This is addressed in 2018 IFC section 907.2.6.2. Only thing that needs addressing is the Occupancy "Conditions" and should just state "I-2." | Andrew/Justin | Andrew/Justin
|  | Smoke Detection 2012 NEW Smoke detection systems are provided in spaces open to corridors as required by 18.3.6.1 In nursing homes, an automatic smoke detection system is installed in the corridors of all smoke compartments containing resident sleeping rooms, unless the resident sleeping room has:  smoke detection, or  Automatic door closing devices with integral smoke detectors on the room side that provide occupant notification. Such detectors are electrically interconnected to the fire alarm system. 18.3.4.5.2, 18.3.4.5.3 | LS.02.01.34- EP 8 | NFPA 101 18.3.4.5.2; 18.3.4.5.3 | IBC 407.2 IFC 907.2.6.2 | IBC 407.2 IFC 907.2.6.2 | IBC 407.2 Corridors continuity and separation IFC 907.2.6.2 Group I-2 |  | This is addressed in 2018 IFC section 907.2.6.2. Only thing that needs addressing is the Occupancy "Conditions" and should just state "I-2." | Andrew/Justin | Andrew/Justin
K351 | Fire | Sprinkler System – Installation 2012 EXISTING Nursing homes, and hospitals where required by construction type, are protected throughout by an approved automatic sprinkler system in accordance with NFPA 13, Standard for the Installation of Sprinkler Systems. In Type I and II construction, alternative protection measures are permitted to be substituted for sprinkler protection in specific areas where State or local regulations prohibit sprinklers. In hospitals, sprinklers are not required in clothes closets of patient sleeping rooms where the area of the closet does not exceed 6 ft² and sprinkler coverage covers the closet footprint as required by NFPA 13, Standard for Installation of Sprinkler Systems. 19.3.5.1, 19.3.5.2, 19.3.5.3, 19.3.5.4, 19.3.5.5, 19.4.2, 19.3.5.10, 9.7, 9.7.1.1(1) | LS.02.01.35- EP 8 LS.02.01.35- EP 14 | NFPA 101 19.3.5; 19.3.5.1; 19.3.5.2; 19.3.5.3; 19.3.5.4; 19.3.5.5 19.4.2; 19.4.2.1; 19.4.2.2 19.3.5.10 9.7.1.1 | IFC 1103.5; 1103.5.1; 1103.5.2 1105.8 | IFC 1103.5; 1103.5.1; 1103.5.2, 1105.9 | IFC 1103.5 Sprinkler systems 1103.5.2 Group I-2 1103.5.3 Group I-2, Condition 2 1105.9 Group I-2 automatic sprinkler system | Focus on Compliance: Automated suppression systems (LS.02.01.35) (August/September 2016) HITF Interpretations, December 2008 HITF Interpretations, June 2009 HITF Interpretations, June 2010 | This is addressed in 2018 IFC with requiring I-2 to be sprinklered and with the 2021 proposed 803.2.3 Group I-2. In Group I-2 occupancies, an automatic sprinkler system installed in accordance with Section 903.3.1.1 of the International Fire Code shall be provided in the following: 1. In Group I-2, Condition 1, throughout the work area . 2. In Group I-2, Condition 2, throughout the work area where the work area is 50 percent or less of the smoke compartment. 3. In Group I-2, Condition 2, throughout the smoke compartment in which the work occurs where the work area exceeds 50 percent of the smoke compartment. 2018 IFC 903.2 addresses "alternative protection measures. | Andrew/Justin | Andrew/Justin
|  | 2012 NEW Buildings are to be protected throughout by an approved automatic sprinkler system in accordance with NFPA 13, Standard for the Installation of Sprinkler Systems. In Type I and II construction, alternative protection measures are permitted to be substituted for sprinkler protection in specific areas where State and local regulations prohibit sprinklers. Listed quick-response or listed residential sprinklers are used throughout smoke compartments with patient sleeping rooms. In hospitals, sprinklers are not required in clothes closets of patient sleeping rooms where the area of the closet does not exceed 6 ft² and sprinkler coverage covers the closet footprint as required by NFPA 13, Standard for Installation of Sprinkler Systems. 18.3.5.1, 18.3.5.4, 18.3.5.5, 18.3.5.6, 9.7, 9.7.1.1(1), 18.3.5.10 | LS.02.01.35- EP 8 LS.02.01.35- EP 9 LS.02.01.35- EP 14 | NFPA 101 18.3.5; 18.3.5.1; 18.3.5.4; 18.3.5.5; 18.3.5.6; 18.3.5.10 9.7.1; 9.7.1.1 | IBC 407.6 | IBC 407.7 IFC 903.3; 903.3.1; 903.3.1.1 | IBC 407.7 Automatic sprinkler system IFC 907.2.6.2 Group I-2 907.5.2 Alarm notification appliances 907.5.2.1 Audible alarms 907.5.2.2 Emergency voice/alarm communication systems 907.5.2.2.1 Manual override 907.5.2.2.2 Live voice messages 907.5.2.2.3 Alternative uses 907.5.2.3 Visible alarms 907.5.2.3.1 Public use areas and common use areas | HITF Interpretations, December 2008 | F147-18 AS This is addressed in 2018 IFC section 903.3.2 | Andrew/Justin | Andrew/Justin
K352 | Fire | Sprinkler System – Supervisory Signals Automatic sprinkler system supervisory attachments are installed and monitored for integrity in accordance with NFPA 72, National Fire Alarm and Signaling Code, and provide a signal that sounds and is displayed at a continuously attended location or approved remote facility when sprinkler operation is impaired. 9.7.2.1, NFPA 72 | LS.02.01.35- EP 1 EC.02.03.05- EP 1 | NFPA 101 9.7.2.1 NFPA 72 14.2.1; 14.2.2; 14.2.3; 14.2.4 Table 14.3.1 | IFC 903.4.1; 903.4.2 | IFC 903.4.1; 903.4.2 | IFC 903.4.1 Monitoring 903.4.2 Alarms |  | This is addressed in the 2019 IFC 903.4.1, by stating that "supervisory & trouble signals shall be transmitted to an approved supervisory station", ie FACP | Andrew/Justin | Andrew/Justin
K353 | Fire | Sprinkler System – Maintenance and Testing Automatic sprinkler and standpipe systems are inspected, tested, and maintained in accordance with NFPA 25, Standard for the Inspection, Testing, and Maintaining of Water-based Fire Protection Systems. Records of system design, maintenance, inspection and testing are maintained in a secure location and readily available. a) Date sprinkler system last checked b) Who provided system test c) Water system supply source Provide in REMARKS information on coverage for any non-required or partial automatic sprinkler system. 9.7.5, 9.7.7, 9.7.8, and NFPA 25 | EC.02.03.05- EPs 2, 6-12, and 17 EC.02.03.05- EP 28 | NFPA 101 9.7.5; 9.7.7; 9.7.8 NFPA 25 | IFC 903.5 901.4 | IFC 903.5 901.4 | IFC 903.5 Testing and maintenance 901.4 Fire protection and Life safety systems | Focus on Compliance: Fire protection (EC.02.03.05) (February/March 2016) HITF Interpretations, June 2011 | This is addressed in 2018 IFC 901.6.1. Table 901.6.1. | Andrew/Justin | Andrew/Justin
K354 | Fire | Sprinkler System – Out of Service Where the sprinkler system is impaired, the extent and duration of the impairment has been determined, areas or buildings involved are inspected and risks are determined, recommendations are submitted to management or designated representative, and the fire department and other authorities having jurisdiction have been notified. Where the sprinkler system is out of service for more than 10 hours in a 24-hour period, the building or portion of the building affected are evacuated or an approved fire watch is provided until the sprinkler system has been returned to service. 18.3.5.1, 19.3.5.1, 9.7.5, 15.5.2 (NFPA 25) |  | NFPA 101 9.7.6 NFPA 25 15.5.2 | IFC 901.7 | IFC 901.7 | IFC IFC 901.7 Systems out of service. | What you need to know about the CMS adoption of the 2012 Life Safety Code® (May 17, 2016) Video: Changes to the Conditions of Participation impacting health care facilities (June 27, 2016) | This is addressed in 2018 IFC 901.7.4 & 901.7.5 |  | Andrew/Justin
K355 | Fire | Portable Fire Extinguishers Portable fire extinguishers are selected, installed, inspected, and maintained in accordance with NFPA 10, Standard for Portable Fire Extinguishers. 18.3.5.12, 19.3.5.12, NFPA 10 | LS.02.01.35- EP 10 LS.02.01.35- EP 11 EC.02.03.05 – EP 15 EC.02.03.05 – EP 16 | NFPA 101 18/19.3.5.12 NFPA 10 | IFC 906.1; 906.2; 906.2.1 | IFC 906.1; 906.2; 906.2.1 | IFC 906.1 Where required 906.2 General requirements 906.2.1 Certification of service personnel for portable fire extinguishers | HITF Interpretations, November 1999 HITF Interpretations, June 2008 | Monitor |  | Andrew/Justin
K361 | General | Corridors – Areas Open to Corridor Spaces (other than patient sleeping rooms, treatment rooms and hazardous areas), waiting areas, nurse’s stations, gift shops, and cooking facilities, open to the corridor are in accordance with the criteria under 18.3.6.1 and 19.3.6.1. 18.3.6.1, 19.3.6.1 | LS.02.01.30-EP 9 | NFPA 101 18/19.3.6.1 | IBC 407.2; 407.2.1; 407.2.2; 407.2.3; 407.2.4; 407.2.5; 407.2.6 | IBC 407.2; 407.2.1; 407.2.2; 407.2.3; 407.2.4; 407.2.5; 407.2.6 | IBC 407.2 Corridors continuity and separation 407.2.1 Waiting and similar areas 407.2.2 Care providers' stations 407.2.3 Psychiatric treatment areas 407.2.4 Gift shops 407.2.5 Nursing home housing units 407.2.6 Nursing home cooking facilities 407.2.7 Domestic cooking appliances 422.7 Domestic cooking (ambulatory care) | HITF Interpretations, June 2008 | G40-18 AS, G41-18 AS, G58-18 AS. NFPA 101 18.3.6.1 Limits waiting rooms open to the corridor size to 600 sq ft. IBC 407.2.1 does not limit size.
K362 | Fire | Corridors – Construction of Walls 2012 EXISTING Corridors are separated from use areas by walls constructed with at least ½-hour fire resistance rating. In fully sprinklered smoke compartments, partitions are only required to resist the transfer of smoke. In nonsprinklered buildings, walls extend to the underside of the floor or roof deck above the ceiling. Corridor walls may terminate at the underside of ceilings where specifically permitted by Code. Fixed fire window assemblies in corridor walls are in accordance with Section 8.3, but in sprinklered compartments there are no restrictions in area or fire resistance of glass or frames. If the walls have a fire resistance rating, give the rating if the walls terminate at the underside of the ceiling, give brief description in REMARKS, describing the ceiling throughout the floor area. 19.3.6.2, 19.3.6.2.7 | LS.02.01.30-EP 9 LS.02.01.30-EP 10 LS.02.01.30-EP 11 | NFPA 101 19.3.6.2; 19.3.6.2.1; 19.3.6.2.2; 19.3.6.2.3; 19.3.6.2.4; 19.3.6.2.5; 19.3.6.2.6; 19.3.6.2.7; 19.3.6.2.8 | IFC 1104.17 1105.4; 1105.4.1; 1105.4.2; 1105.4.3 | IFC 1104.17; 1105.5; 1105.5.1; 1105.5.2; 1105.5.3 | IFC 1104.17 Corridor construction 1105.5 Corridor construction 1105.5.1 Materials 1105.5.2 Fire-resistance rating 1105.5.3 Corridor wall continuity | HITF Interpretations June 2005 HITF Interpretations, June 2006 HITF Interpretations, June 2009 | G42-18 AS |  | Jeff/Jim
|  | Corridors – Construction of Walls 2012 NEW Corridor walls shall form a barrier to limit the transfer of smoke. Such walls shall be permitted to terminate at the ceiling where the ceiling is constructed to limit the transfer of smoke. No fire resistance rating is required for the corridor walls. 18.3.6.2 | LS.02.01.30-EP 9 LS.02.01.30-EP 11 | NFPA 101 18.3.6.2; 18.3.6.2.1; 18.3.6.2.2; 18.3.6.2.3 | IBC 407; 407.1; 407.3 1020 1020.5 | IBC 407; 407.1; 407.3; 1020; 1020.5 | IBC 407 Group I-2 407.1 General 407.3 Corridor wall construction 1020 Corridors 1020.6 Air movement in corridors (Exp. 4) 1020.6.1 Corridor ceiling 1020.7 Corridor continuity | HITF Interpretations June 2005 HITF Interpretations, June 2006 HITF Interpretations, June 2009 | E92-18 AMPC1 10-19-2020: rework drop in ceiling allowances; working with other supporters |  | Jeff/Jim
K363 | Fire | Corridor – Doors 2012 EXISTING Doors protecting corridor openings in other than required enclosures of vertical openings, exits, or hazardous areas shall be substantial doors, such as those constructed of 1¾ inch solid-bonded core wood, or capable of resisting fire for at least 20 minutes. Doors in fully sprinklered smoke compartments are only required to resist the passage of smoke. Doors shall be provided with a means suitable for keeping the door closed. There is no impediment to the closing of the doors. Clearance between bottom of door and floor covering is not exceeding 1 inch. Roller latches are prohibited by CMS regulations on corridor doors and rooms containing flammable or combustible materials. Powered doors complying with 7.2.1.9 are permissible. Hold open devices that release when the door is pushed or pulled are permitted. Nonrated protective plates of unlimited height are permitted. Dutch doors meeting 19.3.6.3.6 are permitted. Door frames shall be labeled and made of steel or other materials in compliance with 8.3, unless the smoke compartment is sprinklered. Fixed fire window assemblies are allowed per 8.3. In sprinklered compartments there are no restrictions in area or fire resistance of glass or frames in window assemblies. 19.3.6.3, 42 CFR Parts 403, 418, 460, 482, 483, and 485 Show in REMARKS details of doors such as fire protection ratings, automatics closing devices, etc. | LS.02.01.30-EP 13 LS.02.01.30- EP 14 | NFPA 101 19.3.6.3; 19.3.6.3.1; 19.3.6.3.4; 19.3.6.3.5; 19.3.6.3.7; 19.3.6.3.10; 19.3.6.3.12; 19.3.6.3.13, 19.3.6.3.16; 19.3.6.3.14; 19.3.6.3.15; 19.3.6.3.17 | IBC 407.3.1 IFC 1105.4.4.2 1105.4.4.2.2 1105.4.4.2.3 | IBC 407.3.1 IFC 1105.5.4.2; 1105.5.4.2.2; 1105.5.4.2.3 | IBC 407.3.1 Corridor doors 407.3.1.1 Door construction 407.6 Automatic-closing doors 407.6.1 Activation of automatic-closing doors. IFC 1105.5.4.2 Doors 1105.5.4.2.2 Corridor doors 1105.5.4.2.3 Dutch doors 1105.5.4.2.4 Self- or automatic-closing doors. 1105.5.4.2.5 Protective plates. | Frequently asked questions on the new CMS regulations (June 7, 2016) Video: Changes to the Conditions of Participation impacting health care facilities (June 27, 2016) HITF Interpretations, December 2006 | F188-18 AS, G42-18 AS, G46-18 AS Commentary: IBC requirements do not address the following items: - Powered doors - Corridor doors held open - Protective plates - Corridor door frames |  | Jeff/Jim
|  | 2012 NEW Doors protecting corridor openings shall be constructed to resist the passage of smoke. Clearance between bottom of door and floor covering is not exceeding 1 inch. There is no impediment to the closing of the doors. Hold open devices that release when the door is pushed or pulled are permitted. Doors shall be provided with self-latching and positive latching hardware. Nonrated protective plates of unlimited height are permitted. Dutch doors meeting 18.3.6.3.6 are permitted. Roller latches are prohibited by CMS regulations on corridor doors and rooms containing flammable or combustible materials. 18.3.6.3, 42 CFR Parts 403, 418, 460, 482, 483, and 485 Show in REMARKS details of doors such as fire protection ratings, automatic closing devices, etc. | LS.02.01.30-EP 12 | NFPA 101 18.3.6.3.1; 18.3.6.3.5; 18.3.6.4; 18.3.6.5; 18.3.6.3.11 | IBC 407.3.1 IFC 1105.4.4.2 1105.4.4.2.2 1105.4.4.2.3 | IBC 407.3.1 IFC 1105.5.4.2; 1105.5.4.2.2; 1105.5.4.2.3 | IBC 407.3.1 Corridor doors 407.3.1.1 Door construction 407.6 Automatic-closing doors 407.6.1 Activation of automatic-closing doors. IFC 1105.5.4.2 Doors 1105.5.4.2.2 Corridor doors 1105.5.4.2.3 Dutch doors 1105.5.4.2.4 Self- or automatic-closing doors. 1105.5.4.2.5 Protective plates. | HITF Interpretations, December 2006 | F188-18 AS, G42-18 AS, G46-18 AS Commentary: IBC requirements do not address the following items: - Powered doors - Corridor doors held open - Protective plates - Corridor door frames |  | Jeff/Jim
K364 | Fire | Corridor – Openings Transfer grilles are not used in corridor walls or doors. Auxiliary spaces that do not contain flammable or combustible materials are permitted to have louvers or be undercut. In other than smoke compartments containing patient sleeping rooms, miscellaneous openings are permitted in vision panels or doors, provided the openings per room do not exceed 20 in² and are at or below half the distance from floor to ceiling. In sprinklered doors, provided the openings per room do not exceed 20 in² and are at or below half the distance from floor to ceiling. In sprinklered rooms, the openings per room do not exceed 80 in². Vision panels in corridor walls or doors shall be fixed window assemblies in approved frames. (In fully sprinklered smoke compartments, there are no restrictions in the area and fire resistance of glass and frames.) 18.3.6.5.1, 19.3.6.5.2, 8.3 | LS.02.01.30-EP 12 LS.02.01.30-EP 13 LS.02.01.30-EP 14 LS.02.01.30-EP 15 Commentary: TJC requirement for vision panels in fixed window assemblies differs from CMS and NFPA requirement. | NFPA 101 18/19.3.6.4; 18/19.3.6.4.1; 18/19.3.6.4.2 18/19.3.6.5; 18/19.3.6.5.1; 19.3.6.5.2 19.3.6.2.7; 19.3.6.2.8 | IEBC 805.5.2 IFC 1105.4.4.2; 1105.4.4.2.1; 1105.4.4.2.2; 1105.4.4.2.4 | IEBC 805.5.2 IFC 1105.5.4.2; 1105.5.4.2.1; 1105.5.4.2.2; 1105.5.4.2.4 | IEBC 804.6.2 Transoms IFC 1105.5.4.2 Doors 1105.5.4.2.1 Louvers 1105.5.4.2.2 Corridor doors 1105.5.4.2.4 Self or automatic-closing doors |  | FS39-18 AMPC1 |  | Jeff/Jim
K371 | Fire | Subdivision of Building Spaces – Smoke Compartments 2012 EXISTING Smoke barriers shall be provided to form at least two smoke compartments on every sleeping floor with a 30 or more patient bed capacity. Size of compartments cannot exceed 22,500 square feet or a 200-foot travel distance from any point in the compartment to a door in the smoke barrier. 19.3.7.1, 19.3.7.2 Detail in REMARKS zone dimensions including length of zones and dead-end corridors. | LS.02.01.30- EP 18 | NFPA 101 19.3.7; 19.3.7.1; 19.3.7.2 | IFC 1105.6; 1105.6.1; 1105.6.1.1; 1105.6.2 | IFC 1105.7; 1105.7.1; 1105.7.1.1; 1105.7.2 | IFC 1105.7 Smoke compartments 1105.7.1 Design 1105.7.1.1 Refuge areas 1105.7.2 Smoke barriers | Focus on Compliance: Life safety protection (LS.02.01.30) (June/July 2016) |  |  | Wayne/Ed
|  | Subdivision of Building Spaces – Smoke Compartments 2012 NEW Smoke barriers shall be provided to form at least two smoke compartments on every floor used by inpatients for sleeping or treatment, and on every floor with an occupant load of 50 or more persons, regardless of use. Size of compartments cannot exceed 22,500 square feet or a 200-foot travel distance from any point in the compartment to a door in the smoke barrier. Smoke subdivision requirements do not apply to any of the stories or areas described in 18.3.7.2. 18.3.7.1, 18.3.7.2 Detail in REMARKS zone dimensions including length of zones and dead-end corridors. | LS.02.01.30- EP 17 | NFPA 101 18.3.7; 18.3.7.1; 18.3.7.2 | IBC 407.5; 407.5.1; 407.5.2 | IBC 407.5; 407.5.1; 407.5.2 | IBC 407.5 Smoke barriers 407.5.1 Smoke compartment size 407.5.2 Exit access travel distance |  | G76-12 AMPC1 |  | Wayne/Ed
K372 | Fire | Subdivision of Building Spaces – Smoke Barrier Construction 2012 EXISTING Smoke barriers shall be constructed to a ½-hour fire resistance rating per 8.5. Smoke barriers shall be permitted to terminate at an atrium wall. Smoke dampers are not required in duct penetrations in fully ducted HVAC systems where an approved sprinkler system is installed for smoke compartments adjacent to the smoke barrier. 19.3.7.3, 8.6.7.1(1) Describe any mechanical smoke control system in REMARKS. | LS.02.01.30- EP 19 LS.02.01.30- EP 22 LS.02.01.30- EP 23 | NFPA 101 19.3.7.3 | IFC 1105.6.2; 1105.6.6 | IFC 1105.7.2; 1105.7.6 | IFC 1105.6.1 Two means of egress 1105.7.2 Smoke barriers 1105.7.6 Duct and air transfer openings | HITF Interpretations, June 2009 | FS114-12 |  | Wayne/Ed
|  | 2012 NEW Smoke barriers shall be constructed to provide at least a 1-hour fire resistance rating and constructed in accordance with 8.5. Smoke barriers shall be permitted to terminate at an atrium wall. Smoke dampers are not required in duct penetrations of fully ducted HVAC systems. 18.3.7.3, 18.3.7.4, 18.3.7.5, 8.3 Describe any mechanical smoke control system in REMARKS. | LS.02.01.30- EP 19 LS.02.01.30- EP 22 LS.02.01.30- EP 23 | NFPA 101 18.3.7.3; 18.3.7.4 | IBC 407.5 717.5.5 | IBC 407.5, 717.5.5 IMC 607.5.4 | IBC 407.5 Smoke barriers 717.5.5 Smoke barriers IMC 607.5.4 Corridors/smoke barriers | HITF Interpretations, June 2009 |  |  | Wayne/Ed
K373 | General | Subdivision of Building Spaces – Accumulation Space Space shall be provided on each side of smoke barriers to adequately accommodate the total number of occupants in adjoining compartments 18.3.7.5.1, 18.3.7.5.2, 19.3.7.5.1, 19.3.7.5.2 | LS.02.01.20- EP 17 LS.02.01.30- EP 18 | NFPA 101 18/19.3.7.5; 18/19.3.7.5.1; 18/19.3.7.5.2 | IBC 407.5.1 IFC 1105.6.1.1 | IBC 407.5.1 IFC 1105.7.1.1 | IBC 407.5.1 Smoke compartment size IFC 1105.7.1.1 Refuge areas |  | NFPA 101 18.3.7.2 limits smoke compartment size to 22,500 sq ft, with 200 ft travel distance. OBC 407.5.1 has exceptions permitting 40,000 sq ft smoke compartments. Change is needed, as 101 is more stringent. I have language for smoke compartment sizes and locations that match 101 that I can give you from CBC. This was intentionally changed to 40,000 for hospitals by the Health care committee.
K374 | Fire | Subdivision of Building Spaces – Smoke Barrier Doors 2012 EXISTING Doors in smoke barriers are 1¾-inch thick solid bonded wood-core doors or of construction that resists fire for 20 minutes. Nonrated protective plates of unlimited height are permitted. Doors are permitted to have fixed fire window assemblies per 8.5. Doors are self- closing or automatic-closing, do not require latching, and are not required to swing in the direction of egress travel. Door opening provides a minimum clear width of 32 in for swinging or horizontal doors. 19.3.7.6, 19.3.7.8, 19.3.7.9 | LS.02.01.30- EP 20 | NFPA 101 19.3.7.6, 19.3.7.8, 19.3.7.9 | IBC 407.6; 709.5; 709.5.1 IFC 909.5.3; 909.5.3.1 | IBC 407.7; 709.5; 709.5.1 IFC 909.5.3; 909.5.3.1 IMC 513.5.3; 513.5.3.1 | IBC 407.7 Automatic sprinkler system 709.5 Openings 709.5.1 Group I-2 and ambulatory care facilities IFC 909.5.3 Opening protection 909.5.3.1 Group I-1, Condition 2; Group I-2; and ambulatory care facilities IMC 513.5.3 Opening protection 513.5.3.1 Group I-1 Condition 2; Group I-2 and ambulatory care facilities |  |  |  | Wayne/Ed
|  | Subdivision of Building Spaces – Smoke Barrier Doors 2012 NEW Doors in smoke barriers have at least a 20-minute fire protection rating or are at least 1¾-inch thick solid bonded core wood. Required clear widths are provided per 18.3.7.6(4) and (5). Nonrated protective plates that do not exceed 48 inches from the bottom of the door are permitted. Horizontal-sliding doors comply with 7.2.1.14. Swinging doors shall be arranged so that each door swings in an opposite direction. Doors shall be self-closing and rabbets, bevels, or astragals are required at the meeting edges. Positive latching is not required. 18.3.7.6, 18.3.7.7, 18.3.7.8 | LS.02.01.30- EP 20 | NFPA 101 18.3.7.6; 18.3.7.7; 18.3.7.8 | IBC 407.6; 709.5; 709.5.1 IFC 909.5.3; 909.5.3.1 IMC 513.5.3; 513.5.3.1 | IBC 407.7; 709.5; 709.5.1 IFC 909.5.3; 909.5.3.1 IMC 513.5.3; 513.5.3.1 | IBC 407.7 Automatic sprinkler system 709.5 Openings 709.5.1 Group I-2 and ambulaotry care facilites IFC 909.5.3 Opening protection 909.5.3.1 Group I-1, Condition 2; Group I-2; and ambulatory care facilities IMC 513.5.3 Opening protection 513.5.3.1 Group I-1 Condition 2; Group I-2 and ambulatory care facilities |  |  |  | Wayne/Ed
K379 | General | Smoke Barrier Door Glazing 2012 EXISTING Openings in smoke barrier doors shall be fire-rated glazing or wired glass panels in steel frames. 19.3.7.6, 19.3.7.6.2, 8.5 | LS.02.01.30- EP 21 | NFPA 101 19.3.7.6; 19.3.7.6.1; 19.3.7.6.2 8.5.4.5. | IFC 1105.6.3 | IFC 1105.7.3 | IFC 1105.7.3 Opening protectives |  | NFPA 101-19.3.7.6- Requires glazing in SB doors to be fire rated glazing or wired glazing in steel frames. IBC 716.1(2)-Requires 3/4 glazing. Safety glazing is required per 716.1.2.1. No change should be needed, as IBC is more stringent, in regards to wired vs safety glazing.
|  | 2012 NEW Windows in smoke barrier doors shall be installed in each cross corridor swinging or horizontal-sliding door protected by fire- rated glazing or by wired glass panels in approved frames. 18.3.7.9 | LS.02.01.30- EP 26 Commentary: No specific TJC requirement. Reference is to General 18/19.3 citation. | NFPA 101 18.3.7.9; 18.3.7.9.1; 18.3.7.10 Commentary: Wired glass panels are not permitted in new smoke barriers by LSC. No | IBC 716.5.3.2; 716.5.6 | IBC 716.2.5.3; 716.5.7 | IBC 716.2.5.3 Glazing in door assemblies ain corridors and smoke barriers 716.5.7 Smoke partitions |  | NFPA 101 18.3.7.9-Requires vision panels in cross corridor SB doors, and fire rated glazing in approved frames. IBC 716.1(2), 716.3.4, 716.1.2.1-Requires vision panel with size to max tested, fire reated glazing, and safety glazing. No change should be needed, as IBC matches and is more stringent with safety glazing. NFPA 101-19.3.7.6- Requires glazing in SB doors to be fire rated glazing or wired glazing in steel frames. IBC 716.1(2)-Requires 3/4 glazing. Safety glazing is required per 716.1.2.1. No change should be needed, as IBC is more stringent, in regards to safety glazing.
K381 | General | Sleeping Room Outside Windows and Doors Every patient sleeping room has an outside window or outside door. In new occupancies, sill height does not exceed 36 in. above the floor. Windows in atrium walls are considered outside windows. Newborn nurseries and rooms intended for occupancy less than 24 hours have no outside window or door requirements. Window sills in special nursing care areas (e.g., ICU, CCU, hemodialysis, neonatal) do not exceed 60 inches above the floor. 42 CFR 403, 418, 460, 482, 483, and 485 | LS.02.01.30 - EP 24 LS.02.01.30 - EP 25 | N/A Commentary: This requirement was removed from the 2009 Edition of the Life Safety Code. Requirement likely comes from FGI guidelines. | N/A | N/A | N/A | What you need to know about the CMS adoption of the 2012 Life Safety Code® (May 17, 2016) Video: Changes to the Conditions of Participation impacting health care facilities (June 27, 2016) | IBC 1204.2-Requires minimum net glazed area not less than 8%of the floor area of the room served, for natural light. I have additional language for patient/resident room windows from CBC 1224/1225 that I can share, if wanted. Needs more study
K400 | General | Special Provisions – Other List in the REMARKS section any LSC Section 18.4 and 19.4 Special Provisions requirements that are not addressed by the provided K-tags, but are deficient. This information, along with the applicable Life Safety Code or NFPA standard citation, should be included on Form CMS-2567. | LS.02.01.40: EP 2 | N/A | N/A | N/A | N/A |  | I will need additional time to compare NFPA 18.4 sections with IBC.
K421 | General | High-Rise Buildings 2012 EXISTING High-rise buildings are protected throughout by an approved, supervised automatic sprinkler system in accordance with Section 9.7 within 12 years of LSC final rule effective date. 19.4.2 | LS.02.01.40- EP 1 | NFPA 101 19.4.2; 19.4.2.1; 19.4.2.2; 19.4.2.3 | IBC 403.3 | IBC 403.3 IFC K102.3.2 Commentary: Retroactive installation of sprinklers not required by IBC. | IBC 403.3 Automatic sprinkler system IFC K102.3.2 High-rise buildings. (ambulatory care) | Video: Changes to the Conditions of Participation impacting health care facilities (June 27, 2016) | IFC 1109 - IFC 1105.9 does not require sprinkler protection throughout an existing building containing a Group I-2 occupancy. It requires the story of the Group I-2 and all stories below. IEBC does not require sprinkler protection throughout the building for alterations (work area approach). IEBC 1011.2.1 triggers IBC Ch. 9 for change of occupancy classification which would require sprinklers throughout the COO area.
|  | High-Rise Buildings 2012 NEW High-rise buildings comply with section 11.8. 18.4.2 | LS.02.01.40- EP 1 | NFPA 101 18.4.2 | IBC 403 | IBC 403 | IBC 403 High-Rise Buildings |  | No changes to be made.
K500 | General | Building Services – Other List in the REMARKS section any LSC Section 18.5 and 19.5 Building Services requirements that are not addressed by the provided K-tags, but are deficient. This information, along with the applicable Life Safety Code or NFPA standard citation, should be included on Form CMS-2567. | LS.02.01.50: EP 14 | N/A | N/A | N/A | N/A |  | No changes to be made.
K511 | MEP | Utilities – Gas and Electric Equipment using gas or related gas piping complies with NFPA 54, National Fuel Gas Code, electrical wiring and equipment complies with NFPA 70, National Electric Code. Existing installations can continue in service provided no hazard to life. 18.5.1.1, 19.5.1.1, 9.1.1, 9.1.2 | LS.02.01.50: EP 1 | NFPA 101 19.5.1; 19.5.1.1; 19.5.1.2 | IBC 2701.1 | IBC 2701.1 IEBC 302.4 IFGC CHAPTER 4 | IBC Chapter 27 Electrical 2701.1 Scope IEBC 302.3 Existing materials IFGC CHAPTER 4 GAS PIPING INSTALLATIONS |  |  | Complete | TP
K521 | MEP | HVAC Heating, ventilation, and air conditioning shall comply with 9.2 and shall be installed in accordance with the manufacturer’s specifications. 18.5.2.1, 19.5.2.1, 9.2 | LS.02.01.50- EP 2 | NFPA 101 18/19.5.2; 18/19.5.2.1 NFPA 99 Chapter 6 and Chapter 9 | IFC 603; 603.1; 603.1.1 IBC 1203.1 IMC 401.2 407; 407.1 | IFC 603; 603.1; 603.1.1 IBC 1202.1 IMC 401.2 407; 407.1 | IFC 605 Fuel-Fired Appliances and Systems 605.1 Installation of nonportable fuel fire appliances 605.1.1 Installation of nonportable fuel fire appliances IBC 1202.1 General (Ventilation) IMC 401.2 Ventilation required 407 AMBULATORY CARE FACILITIES AND GROUP I-2 OCCUPANCIES | ASHE Publication: | M20-18 AS | Proposal Needed | GH/JF
K522 | MEP | HVAC – Any Heating Device Any heating device, other than a central heating plant, is designed and installed so combustible materials cannot be ignited by device, and has a safety features to stop fuel and shut down equipment if there is excessive temperature or ignition failure. If fuel fired, the device also: • is chimney or vent connected takes air for combustion from outside combustion system separate from occupied area atmosphere 18.5.2.2, 19.5.2.2 | LS.02.01.50- EP 3 | NFPA 101 18/19.5.2.2 | IMC CHAPTER 9 | IMC CHAPTER 407.1 | IMC |  | Change the name for ASHRAE 170 to ASHRAE/ASHE170 | Minor Change Needed | GH/JF
K523 | MEP | HVAC – Suspended Unit Heaters Suspended unit heaters are permitted provided the following are met:  Not located in means of egress or in patient rooms  Located high enough to be out of reach of people in the area  Has a safety feature to stop fuel and shut down equipment if there is excessive temperature or ignition failure. 18.5.2.3(1), 19.5.2.3(1) | LS.02.01.50- EP 4 . | NFPA 101 18/19.5.2.3 (1) | IMC 920.1; 920.2; 920.3 | IMC 920.1; 920.2; 920.3 | IMC SECTION 920 UNIT HEATERS 920.1 General 920.2 Support 920.3 Ductwork 920.4 Prohibited uses. |  | M81-18 AS | Complete | GH/JF
K524 | MEP | HVAC – Direct-Vent Gas Fireplaces Direct-vent gas fireplaces, as defined in NFPA 54, inside of all smoke compartments containing patient sleeping areas comply with the requirements of 18.5.2.3(2), 19.5.2.3(2). 18.5.2.3(2), 19.5.2.3(2), NFPA 54 | LS.02.01.50- EP 5 | NFPA 101 18/19.5.2.3 (2) | IMC CHAPTER 9 | IMC CHAPTER 9 | IMC CHAPTER 9 SPECIFIC APPLIANCES, FIREPLACES AND SOLID FUEL-BURNING EQUIPMENT |  | FG3-12 Part 1 and 2 D/D; F122-18 Part 1 and 2 AS/AS. IMC more restrictive | Complete | GH/JF
K525 | MEP | HVAC – Solid Fuel-Burning Fireplaces Solid fuel-burning fireplaces are permitted in other than patient sleeping areas provided:  Areas are separated by 1-hour fire resistance construction  Fireplace complies with 9.2.2  Fireplace enclosure resists breakage up to 650°F and has heat-tempered glass  Room has supervised CO detection per 9.8 18.5.2.3(3) and 19.5.2.3(3) | LS.02.01.50- EP 6 | NFPA 101 18/19.5.2.3 (3) | IMC 904.1 | IMC 901.4 | IMC 901.4 Solid fuel-burning fireplaces and appliances in Group I-2, Condition 2 |  | FG3-12 Part 1 and 2 D/D. IMC more restrictive | Complete | GH/JF
K531 | General | Elevators 2012 EXISTING Elevators comply with the provision of 9.4. Elevators are inspected and tested as specified in ASME A17.1, Safety Code for Elevators and Escalators. Firefighter’s Service is operated monthly with a written record. Existing elevators conform to ASME/ANSI A17.3, Safety Code for Existing Elevators and Escalators. All existing elevators, having a travel distance of 25 ft. or more above or below the level that best serves the needs of emergency personnel for firefighting purposes, conform with Firefighter’s Service Requirements of ASME/ANSI A17.3. (Includes firefighter’s service Phase I key recall and smoke detector automatic recall, firefighter’s service Phase II emergency in-car key operation, machine room smoke detectors, and elevator lobby smoke detectors.) 19.5.3, 9.4.2, 9.4.3 | LS.02.01.50- EP 7 | NFPA 101 19.5.3 9.4.2.2; 9.4.3.2 | IBC 3001.2; TABLE 3001.3 IEBC 902.1.2 IFC 607.1; 607.2; 607.2.1; 607.2.2; 607.2.3 1103.3; 1103.3.1; 1103.3.2 | IBC 3001.3; TABLE 3001.3 IEBC 902.1.2 IFC 606.1; 606.2; 606.2.1; 606.2.2; 606.2.3 1103.3; 1103.3.1; 1103.3.2 | IBC 3001.3 Referenced standards TABLE 3001.3 Elevators and conveying systems and components IEBC 902.1.2 Elevators IFC 604.2 Emergency operation 604.3 Standby power 604.3.1 Manual transfer 604.3.2 One elevator 604.3.3 Two or more elevators 1103.3 Existing elevators 1103.3.1 Elevators, escalators and moving walks 1103.3.2 Elevator emergency operation |  | IFC 1103.3.2 has an exception for buildings without occupied floors more than 55 ft above or 25 ft below the LLFDVA. These exceptions are not in K531.
|  | 2012 NEW Elevators comply with the provision of 9.4. Elevators are inspected and tested as specified in ASME A17.1, Safety Code for Elevators and Escalators. Firefighter’s Service is operated monthly with a written record. New elevators conform to ASME/ANSI A17.1, Safety Code for Elevators and Escalators, including Firefighter’s Service Requirements. (Includes firefighter’s Phase I key recall and smoke detector automatic recall, firefighter’s service Phase II emergency in-car key operation, machine room smoke detectors, and elevator lobby smoke detectors.) 18.5.3, 9.4.2, 9.4.3 | LS.02.01.50- EP 7 EC.02.03.05- EP 27 | NFPA 101 18.5.3 9.4.2; 9.4.3 | IBC 3001.2; TABLE 3001.3 IEBC 902.1.2 IFC 607.1; 607.2; 607.2.1; 607.2.2; 607.2.3 1103.3; 1103.3.1; 1103.3.2 | IBC 3001.3; TABLE 3001.3 IEBC 902.1.2 IFC 606.1; 606.2; 606.2.1; 606.2.2; 606.2.3 1103.3; 1103.3.1; 1103.3.2 | IBC 3001.3 Referenced Standards TABLE 3001.3 Elevators and conveying systems and components IEBC 902.1.2 Elevators IFC 604.2 Emergency operation 604.3 Standby power 604.3.1 Manual transfer 604.3.2 One elevator 604.3.3 Two or more elevators 1103.3 Existing elevators 1103.3.1 Elevators, escalators and moving walks 1103.3.2 Elevator emergency operation |  | No changes to be made.
K532 | General | Escalators, Dumbwaiters, and Moving Walks 2012 EXISTING Escalators, dumbwaiters, and moving walks comply with the provisions of 9.4. All existing escalators, dumbwaiters, and moving walks conform to the requirements of ASME/ANSI A17.3, Safety Code for Existing Elevators and Escalators. (Includes escalator emergency stop buttons and automatic skirt obstruction stop. For power dumbwaiters, includes hoistway door locking to keep doors closed except for floor where car is being loaded or unloaded.) 19.5.3, 9.4.2.2 | LS.02.01.50- EP 8 | NFPA 101 19.5.3 9.4.2.2 | IFC 1103.3; 1103.3.1 | IFC 1103.3; 1103.3.1 | IFC 1103.3 Existing elevators 1103.3.1 Elevators, escalators and moving walks |  | NFPA 82, IFC, IEBC have differences - No changes to be made.
|  | Escalators, Dumbwaiters, and Moving Walks 2012 NEW Escalators, dumbwaiters, and moving walks comply with the provisions of 9.4. 18.5.3, 9.4.2.2 | LS.02.01.50- EP 8 | NFPA 101 18.5.3 9.4.2.1 | IBC 3004.1 | IBC 3004.1 | IBC 3004.1 General |  | No changes to be made.
K541 | General | Rubbish Chutes, Incinerators, and Laundry Chutes 2012 EXISTING (1) Any existing linen and trash chute, including pneumatic rubbish and linen systems, that opens directly onto any corridor shall be sealed by fire resistive construction to prevent further use or shall be provided with a fire door assembly having a fire protection rating of 1 hour. All new chutes shall comply with 9.5. (2) Any rubbish chute or linen chute, including pneumatic rubbish and linen systems, shall be provided with automatic extinguishing protection in accordance with 9.7. (3) Any trash chute shall discharge into a trash collection room used for no other purpose and protected in accordance with 8.4 (Existing laundry chutes permitted to discharge into same room are protected by automatic sprinklers in accordance with 19.3.5.9 or 19.3.5.7.) (4) Existing fuel-fed incinerators shall be sealed by fire resistive construction to prevent further use. 19.5.4, 9.5, 8.4, NFPA 82 | LS.02.01.50- EP 9 LS.02.01.50- EP 10 | NFPA 101 19.5.4; 19.5.4.1; 19.5.4.3; 19.5.4.4; 19.5.4.5; 19.5.4.6 | IEBC 904.1.2 | IEBC 904.1.2 | IEBC 904.1.2 Rubbish and linen chutes | HITF Interpretations, November 1999 | IEBC for Level 3 alterations (work area > 50% of building area) requires fire suppression for chutes located in the work area where protection is required by the IBC. No change to be made.
|  |  | LS.02.01.50- EP 11 LS.02.01.50- EP 12 LS.02.01.50- EP 13 LS.02.01.50- EP 14 | 9.5; 9.5.1; 9.5.1.1; 9.5.1.2; 9.5.1.3; 9.5.1.4; 9.5.1.5; 9.5.2 | IFC 1103.4.9; 1103.4.9.1; 1103.4.9.2; 1103.4.9.2.1; 1103.4.9.2.2; 1103.4.9.3; 1103.4.9.4; 1103.4.9.5; 1103.4.10 | IFC 1103.4.9; 1103.4.9.1; 1103.4.9.2; 1103.4.9.2.1; 1103.4.9.2.2; 1103.4.9.3; 1103.4.9.4; 1103.4.9.5; 1103.4.10 | IFC 1103.4.9 Waste and linen chutes 1103.4.9.1 Enclosure 1103.4.9.2 Chute intakes 1103.4.9.2.1 Chute intake direct from corridor 1103.4.9.2.2 Chute intake via a chute-intake room 1103.4.9.3 Automatic sprinkler system 1103.4.9.4 Chute discharge rooms 1103.4.9.5 Chute discharge protection 1103.4.10 Flue-fed incinerators | HITF Interpretations, June 2006 | No changes to be made.
|  | Rubbish Chutes, Incinerators, and Laundry Chutes 2012 NEW Rubbish chutes, incinerators, and laundry chutes shall comply with the provisions of Section 9.5, unless otherwise specified in 18.5.4.2.  The fire resistance rating of chute charging room shall not be required to exceed 1 hour.  Any rubbish chute or linen chute shall be provided with automatic extinguishing protection in accordance with Section 9.7.  Chutes shall discharge into a trash collection room used for no other purpose and shall be protected in accordance with 8.7. 18.5.4.2, 8.7, 9.5, 9.7, NFPA 82 | LS.02.01.50- EP 9 LS.02.01.50- EP 10 | NFPA 101 18.5.4; 18.5.4.1 18.5.4.2; 18.5.4.3; 18.5.4.4; 18.5.4.6 | IBC 713.13; 713.13.1 ; 713.13.2 ; 713.13.3; 713.13.4; 713.13.5; 713.13.6 | IBC 713.13; 713.13.1 ; 713.13.2 ; 713.13.3; 713.13.4; 713.13.5; 713.13.6 | IBC 713.13 Waste, recycle and linen chutes and incinerator rooms 713.13.1 Waste, recycle and linen chute enclosures 713.13.2 Materials 713.13.3 Chute access rooms 713.13.4 Chute discharge room 713.13.5 Incinerator room 713.13.6 Automatic sprinkler system | HITF Interpretations, June 2006 | FS44-18 AS. No changes to be made.
|  |  | LS.02.01.50- EP 11 LS.02.01.50- EP 12 LS.02.01.50- EP 13 LS.02.01.50- EP 14 | 9.5; 9.5.1; 9.5.1.1; 9.5.1.2; 9.5.1.3 9.5.1.4; 9.5.1.5; 9.5.2 | IFC 903.2.11.2 | IFC 903.2.11.2 | IFC 903.2.11.2 Rubbish and linen chutes |  | No changes to be made.
K700 | General | Operating Features – Other List in the REMARKS section any LSC Section 18.7 and 19.7 Operating Features requirements that are not addressed by the provided K-tags, but are deficient. This information, along with the applicable Life Safety Code or NFPA standard citation, should be included in Form CMS-2567. | LS.02.01.70- EP 9 | N/A | N/A | N/A | N/A
K711 | Fire | Evacuation and Relocation Plan There is a written plan for the protection of all patients and for their evacuation in the event of an emergency. Employees are periodically instructed and kept informed with their duties under the plan, and a copy of the plan is readily available with telephone operator or with security. The plan addresses the basic response required of staff per 18/19.7.2.1.2 and provides for all of the fire safety plan components per 18/19.2.2. 18.7.1.1 through 18.7.1.3, 18.7.2.1.2, 18.7.2.2, 18.7.2.3, 19.7.1.1 through 19.7.1.3, 19.7.2.1.2, 19.7.2.2, 19.7.2.3 | EC.02.03.01- EP 9 | NFPA 101 18/19.7.1; 18/19.7.1.1; 18/19.7.1.2; 18/19.7.1.3 18/19.7.2.1.2; 18/19.7.2.2 18/19.7.2.3; 18/19.7.2.3.1; 18/19.7.2.3.2; 18/19.7.2.3.3 | IBC 1001.4 IFC 403.8; 403.8.1.2 403.8.2; 403.8.2.1; 403.8.2.2; 403.8.2.3 | IBC 1002.2 IFC 403.8; 403.8.1.2 403.8.2; 403.8.2.1; 403.8.2.2; 403.8.2.3 | IBC 1002.2 Fire safety and evacuation plans IFC 403.7 Group I Occupancies 403.7.2 Group I-2 Occupancies 403.7.2.1 Fire safety and evacuation plan 403.7.2.2 Fire safety plan 403.7.2.3 Staff training 403.7.2.4 Emergency evacuation drills 403.7.2.5 Fire loss prevention in operating rooms |  | F24-18 AS, F25-18 AS, F26-18 AMPC1, F27-18 AS, F28-18 AMPC1, F33-18 AS, F39-18 AM IFC 403.3.1 Ambulatory care facilities 403.7.1 Group I-1 occupancies 403.9.3 Group R-4 occupancies |  | Nanci/Mark
K712 | Fire | Fire Drills Fire drills include the transmission of a fire alarm signal and simulation of emergency fire conditions. Fire drills are held at unexpected times under varying conditions, at least quarterly on each shift. The staff is familiar with procedures and is aware that drills are part of established routine. Responsibility for planning and conducting drills is assigned only to competent persons who are qualified to exercise leadership. Where drills are conducted between 9:00 PM and 6:00 AM, a coded announcement may be used instead of audible alarms. 18.7.1.4 through 18.7.1.7, 19.7.1.4 through 19.7.1.7 | EC.02.03.03 EP 1 EC.02.03.03 EP 2 EC.02.03.03 EP 3 EC.02.03.03 EP 4 EC.02.03.03 EP 5 | NFPA 101 18/19.7.1.4; 18/19.7.1.5; 18/19.7.1.6; 18/19.7.1.7; 18/19.7.1.8 | IFC 403.8.2.3; 405.2; TABLE 405.2; 405.3; 405.4; 406.1 | IFC 403.8.2.3; 405.2; TABLE 405.2; 405.3; 405.4; 406.1 | IFC 403.7.2.4 Emergency evacuation drills 405.2 Occupant participation 405.3 Frequency TABLE 405.2 Fire and Evacuation Drill Frequency and Participation 405.4 Leadership 405.5 Time 405.9 Accountability 406.1 General | HITF Interpretations, November 1998 HITF Interpretations, June 2006 HITF Interpretations, December 2006 HITF Interpretations, June 2014 | F28-19 AMCP1, F31-18 AS, F32-18 AS, F39-18 AM |  | Nanci/Mark
K741 | Fire | Smoking Regulations Smoking regulations shall be adopted and shall include not less than the following provisions: (1) Smoking shall be prohibited in any room, ward, or compartment where flammable liquids, combustible gases, or oxygen is used or stored and in any other hazardous location, and such area shall be posted with signs that read NO SMOKING or shall be posted with the international symbol for no smoking. (2) In health care occupancies where smoking is prohibited and signs are prominently placed at all major entrances, secondary signs with language that prohibits smoking shall not be required. (3) Smoking by patients classified as not responsible shall be prohibited. (4) The requirement of 18.7.4(3) shall not apply where the patient is under direct supervision. (5) Ashtrays of noncombustible material and safe design shall be provided in all areas where smoking is permitted. (6) Metal containers with self-closing cover devices into which ashtrays can be emptied shall be readily available to all areas where smoking is permitted. 18.7.4, 19.7.4 | LS.02.01.70- EP 1 LS.02.01.70- EP 2 | NFPA 101 19.7.4 | IFC 310.1; 310.2; 310.3; 310.4; 310.5; 310.7; 310.8 | IFC 310.1; 310.2; 310.3; 310.4; 310.5; 310.7; 310.8 | IFC 310.1 General 310.2 Prohibited area 310.3 "No Smoking" signs 310.4 Removal of signs prohibited 310.5 Compliance with "No Smoking" signs 310.7 Burning objects 310.8 Hazardous environmental conditions | HITF Interpretations, December 2006 | Commentary: Metal containers with self-closing cover devices are not required by IBC. |  | Nanci/Mark
K751 | Fire | Draperies, Curtains, and Loosely Hanging Fabrics Draperies, curtains including cubicle curtains and loosely hanging fabric or films shall be in accordance with 10.3.1. Excluding curtains and draperies: at showers and baths; on windows in patient sleeping room located in sprinklered compartments; and in non-patient sleeping rooms in sprinklered compartments where individual drapery or curtain panels do not exceed 48 square feet or total area does not exceed 20% of the wall. 18.7.5.1, 18.3.5.11., 19.7.5.1, 19.3.5.11, 10.3.1 | LS.02.01.70- EP 3 | NFPA 101 18/19.7.5, 18/19.7.5.1 18/19.3.5.11 Commentary: Requirements do not align with all NFPA 101 requirements. | IFC 807.2, 807.3, 807.4 Commentary: IBC requirements dictate that curtains, etc. do not exceed 10% of wall. | IFC 807.2, 807.3, 807.4 | IFC 807.2 Combustible decorative materials 807.3 Acceptance criteria and reports 807.4 Artificial decorative vegetation |  | Commentary: IBC requirements dictate that curtains, etc. do not exceed 10% of wall. |  | Maggie
K752 | Fire | Upholstered Furniture and Mattresses Newly introduced upholstered furniture meets Class I or char length, and heat release criteria in accordance with 10.3.2.1 and 10.3.3, unless the building is fully sprinklered. Newly introduced mattresses shall meet char length and heat release criteria in accordance with 10.3.2.2 and 10.3.4, unless the building is fully sprinklered. Upholstered furniture and mattresses belonging to nursing home residents do not have to meet these requirements as all nursing homes are required to be fully sprinklered. Newly introduced upholstered furniture and mattresses means purchased on or after the LSC final rule effective date. 18.7.5.2, 18.7.5.4, 19.7.5.2, 19.7.5.4 | LS.02.01.70- EP 4 | NFPA 101 18/19.7.5.2; 19.7.5.3; 18/19.7.5.4; 19.7.5.5 | IFC 805.2; 805.2.1; 805.2.1.1; 805.2.1.2; 805.2.1.3; 805.2.2; 805.2.2.1; 805.2.2.2; 805.2.2.3 | IFC 805.2; 805.2.1; 805.2.1.1; 805.2.1.2; 805.2.1.3; 805.2.2; 805.2.2.1; 805.2.2.2; 805.2.2.3 | IFC 805.2 Group I-2 and Group B ambulaotry care facilities 805.2.1 Upholstered furniture 805.2.1.1 Ignition by cigarettes 805.2.1.2 Heat release rate 805.2.1.3 Identification 805.2.2 Mattresses 805.2.2.1 Ignition by cigarettes 805.2.2.2 Heat release rate 805.2.2.3 Identification | HITF Interpretations May 2003 | F127-16 AM 10-19-2020: Amy Carpenter says okay; no propoal needed |  | Maggie
K753 | Fire | Combustible Decorations Combustible decorations shall be prohibited unless one of the following is met:  Flame retardant or treated with approved fire-retardant coating that is listed and labeled for product.  Decorations meet NFPA 701  Decorations exhibit heat release less than 100 kilowatts in accordance with NFPA 289.  Decorations, such as photographs, paintings and other art are attached to the walls, ceilings and non-fire-rated doors in accordance with 18.7.5.6 or 19.7.5.6.  The decorations in existing occupancies are in such limited quantities that a hazard of fire is not present. 18.7.5.6, 19.7.5.6 | LS.02.01.70- EP 5 | NFPA 101 18/19.7.5.6 | IFC 807.1; 807.2 | IFC 807.1; 807.2 | IFC 807.1 General 807.2 Combustible decorative materials 807.5.3 Groups I-1 and I-2 807.5.3.1 Group I-2 and I-2 Condition 1 within units. 807.5.3.2 In Group I-1 and I-2, Condition 1 for areas other than within units 807.5.3.3 In Group I-2, Condition 2 807.5.3.4 Other areas in Groups I-1 and I-2 |  |  |  | Maggie
K754 | Fire | Soiled Linen and Trash Containers Soiled linen or trash collection receptacles shall not exceed 32 gallons in capacity. The average density of container capacity in a room or space shall not exceed 0.5 gallons/ square feet. A total container capacity of 32 gallons shall not be exceeded within any 64 square feet area. Mobile soiled linen or trash collection receptacles with capacities greater than 32 gallons shall be located in a room protected as a hazardous area when not attended. Containers used solely for recycling are permitted to be excluded from the above requirements where each container is ≤ 96 gal. unless attended, and containers for combustibles are labeled and listed as meeting FM Approval Standard 6921 or equivalent. 18.7.5.7, 19.7.5.7 | LS.02.01.70- EP 6 | NFPA 101 18/19.7.5.7; 18/19.7.5.7.1; 18/19.7.5.7.2; 18/19.7.5.7.3 Commentary: This requirement is exempted by the LSC in Section 18.7.5.7.3. | IFC 808.1 | IFC 808.1 | IFC 808.1 Wastebaskets and linen containers in Group I-1, I-2 and I-3 occupancies and Group B ambulatory care facilities | HITF Interpretation, November 2009 | F137-16 AM, F138-16 AM Commentary: IBC requires compliance with ASTM E 1354 and requires metal wastebaskets exceeding 20 gallons to be listed in accordance with UL 1315 in health care (I-2) occupancies. 10-19-2020: look at increasing quantities; difference in standards; not a building code issue; ask Healthercare committee if an issue? |  | Nanci/Mark
K771 | MEP | Engineer Smoke Control Systems 2012 NEW When installed, engineered smoke control systems are tested in accordance with NFPA 92, Standard for Smoke Control Systems. Test documentation is maintained on the premises. 18.7.7 | LS.02.01.70- EP 7 | NFPA 101 18.7.7; 18.7.7.1; 18.7.7.2 | IFC 909 | IFC 909 | IFC 909 Smoke Control Systems |  | NFPA 92 reference in 909.7 and 909.8 |  | TP
K781 | MEP | Portable Space Heaters Portable space heating devices shall be prohibited in all health care occupancies. Except, unless used in nonsleeping staff and employee areas where the heating elements do not exceed 212 degrees Fahrenheit (100 degrees Celsius). 18.7.8, 19.7.8 [A] 106.2 Permits not required. Permits shall not be required for the following: 1. Portable heating appliances. 2. Portable ventilation appliances and equipment. 3. Portable cooling units. 4. Steam, hot water or chilled water piping within any heating or cooling equipment or appliances regulated by this code. 5. The replacement of any minor part that does not alter the approval of equipment or an appliance or make such equipment or appliance unsafe. 6. Portable evaporative coolers. 7. Self-contained refrigeration systems that contain 10 pounds (4.5 kg) or less of refrigerant, or that are actuated by motors of 1 horsepower (0.75 kW) or less. 8. Portable fuel cell appliances that are not connected to a fixed piping system and are not interconnected to a power grid. Exemption from the permit requirements of this code shall not be deemed to grant authorization for work to be done in violation of the provisions of this code or other laws or ordinances of this jurisdiction. 309.1 Space-heating systems. Interior spaces intended for human occupancy shall be provided with active or passive space-heating systems capable of maintaining an indoor temperature of not less than 68°F (20°C) at a point 3 feet (914 mm) above floor on the design heating day. The installation of portable space heaters shall not be used to achieve compliance with this section. Exceptions: 1. Interior spaces where the primary purpose is not associated with human comfort. 2. Group F, H, S and U occupancies. | LS.02.01.70- EP 8 | NFPA 101 18/19.7.8 | IFC | IFC 604.10; 604.10.1; 604.10.2; 604.10.3; 604.10.4 | IFC 603.9 Portable, electic space heaters 603.9.1 Listed and labeled 603.9.2 Power supply 603.9.3 Extension cords 603.9.4 Prohibited areas 604.9.5 Group I-2 occupancies and ambulatory care facilities | IMC 920 Unit heaters 920.1 General. Unit heaters shall be installed in accordance with the listing and the manufacturer’s instructions. Oil-fired unit heaters shall be tested in accordance with UL 731. 920.2 Support. Suspended-type unit heaters shall be supported by elements that are designed and constructed to accommodate the weight and dynamic loads. Hangers and brackets shall be of noncombustible material. Suspendedtype oil-fired unit heaters shall be installed in accordance with NFPA 31. 920.3 Ductwork. A unit heater shall not be attached to a warm-air duct system unless listed for such installation. 605.10 Portable, electric space heaters. Where not prohibited by other sections of this code, portable, electric space heaters shall be permitted to be used in all occupancies other than Group I-2 and in accordance with Sections 605.10.1 through 605.10.4. Exception: The use of portable, electric space heaters in which the heating element cannot exceed a temperature of 212°F (100°C) shall be permitted in nonsleeping staff and employee areas in Group I-2 occupancies. 605.10.1 Listed and labeled. Only listed and labeled portable, electric space heaters shall be used. 605.10.2 Power supply. Portable, electric space heaters shall be plugged directly into an approved receptacle. 605.10.3 Extension cords. Portable, electric space heaters shall not be plugged into extension cords. 605.10.4 Prohibited areas. Portable, electric space heaters shall not be operated within 3 feet (914 mm) of any combustible materials. Portable, electric space heaters shall be operated only in locations for which they are listed. | F73-16 AMPC1 IMC change may be more restrictive since it prohibits in I-2 throughout with no allowance for use in non-sleeping staff areas ..this works since then don't have to also stipulate 212 F max. | Complete | Pier
K791 | Fire | Construction, Repair, and Improvement Operations Construction, repair, and improvement operations shall comply with 4.6.10. Any means of egress in any area undergoing construction, repair, or improvements shall be inspected daily to ensure its ability to be used instantly in case of emergency and compliance with NFPA 241. 18.7.9, 19.7.9, 4.6.10, 7.1.10.1 | LS.01.02.01- EP 4 | NFPA 101 18/19.7.9.1; 18/19.7.9.2 | IBC CHAPTER 33 | IBC CHAPTER 33 | IBC CHAPTER 33 Safeguards During Construction |  | G200-12 D 10-19-2020: no report; seperation from operational area; what if sprinkler is turned off? |  | Jeff/Jim
K900 | General | Health Care Facilities Code - Other List in the REMARKS section, any NFPA 99 requirements (excluding Chapter 7, 8, 12, and 13) that are not addressed by the provided K-Tags, but are deficient. This information, along with the applicable Health Care Facilities Code or NFPA standard citation, should be included on Form CMS-2567. | EC.02.03.01- EP 13 EC.02.05.05- EP 8 EC.02.05.09- EP 14 |  |  |  |  | Navigating, Identifying, and Interpreting NFPA 99 (2016) Jonathan R. Hart NFPA 99: Health Care Facilities Code (2012) Classroom Training | SOM 482.41 (a)(1)The hospital must comply with the applicable provisions of the Life Safety Code, National Fire Protection Amendments (NFPA) 101, 2000 Edition and applicable references, such as, NFPA-99: Health Care Facilities, for emergency lighting and emergency power.
K901 | MEP | Fundamentals – Building System Categories Building systems are designed to meet Category 1 through 4 requirements as detailed in NFPA 99. Categories are determined by a formal and documented risk assessment procedure performed by qualified personnel. Chapter 4 (NFPA 99) | EC.02.05.01- EP 2 | NFPA 99 Chapter 4 | IFC 1105.10. 1105.10.1; 1105.10.2 | IFC 1105.11, 1105.11.1; 1105.11.2 IBC 407.11, 422.6, 2702.1.8; 2702.2; 2702.2.8 | IFC 1105.11 Essential electrical systems 1105.11.1 Where required 1105.11.2 Installation and duration 5306 Medical Gases IBC 407.11 Electrical systems 422.6 Electrical systems 2702.1.8 Group I-2 occupancies 2702.2 Where required 2702.2.8 Group I-2 occupancies IPC 1202 Medical Gases | NFPA 99 2012 Update: Risk Categories (2017) Michael A. Crowley | SOM 482.41 (a)(1)The hospital must comply with the applicable provisions of the Life Safety Code, National Fire Protection Amendments (NFPA) 101, 2000 Edition and applicable references, such as, NFPA-99: Health Care Facilities, for emergency lighting and emergency power. EB11-19 AM; EB49-19 AS; EB99-19 AS include TIA for NFPA 99 IBC 2702.2.1 Ambulatory care facilities Work needed in IFC chapter 6 for a number of systems. IFC 5603.5 for NFPA 99 reference to medical gases. Electrical Systems Gas & Vacuum Systems - See K903 for proposal. |  | TP
K902 | MEP | Gas and Vacuum Piped Systems – Other List in the REMARKS section, any NFPA 99 Chapter 5 Gas and Vacuum Systems requirements that are not addressed by the provided K-Tags, but are deficient. This information, along with the applicable Life Safety Code or NFPA standard citation, should be included on Form CMS-2567. Chapter 5 (NFPA 99) | EC.02.05.09- EP 14 | NFPA 99 Chapter 5 | IFC 5306.5 | IFC 5306.5 | IFC 5306.5 Medical gas systems and equipment | NFPA 99 2012 Update: Medical Gas and Vacuum Systems (2017) James K Lathrop | SOM 482.41 (a)(1)The hospital must comply with the applicable provisions of the Life Safety Code, National Fire Protection Amendments (NFPA) 101, 2000 Edition and applicable references, such as, NFPA-99: Health Care Facilities, for emergency lighting and emergency power. EB11-19 AM; EB49-19 AS IPC 1202 references NFPA 99 it appears there is no reference for IPC in the mechanical code for vacuum systems. Medical Gas systems are covered in the IPC scope not the IMC. |  | TP
K903 | MEP | Gas and Vacuum Piped Systems – Categories Medical gas, medical air, surgical vacuum, WAGD, and air supply systems in which failure is likely to cause major injury or death are designated Category 1. Systems in which failure is likely to cause minor injury to patients are designated Category 2. Systems in which failure is not likely to cause injury, but can cause discomfort is designated Category 3. Deep sedation and general anesthesia are not administered when using a Category 3 medical gas system. 5.1.1.1, 5.2.1, 5.3.1.1, 5.3.1.5 (NFPA 99) | EC.02.05.09- EP 1 | NFPA 99 5.1.1.1; 5.2.1; 5.3.1.1; 5.3.1.5 | IPC 101.2 1202; 1202.1 | IPC 101.2 1202; 1202.1 IEBC 1009.5 | IPC 101.2 Scope 202 Definitions MEDICAL GAS SYSTEM 1202 MEDICAL GASES 1202.1 Nonflammable medical gases IEBC 501.3 Healthcare facilities 1009.5 Group I-2 |  | SOM 482.41 (a)(1)The hospital must comply with the applicable provisions of the Life Safety Code, National Fire Protection Amendments (NFPA) 101, 2000 Edition and applicable references, such as, NFPA-99: Health Care Facilities, for emergency lighting and emergency power. EB49-19 AS; EB99-19 AS, EB100-19 Develop proposal to strengthen risk assessment language. Proposal developed |  | TP
K904 | MEP | Gas and Vacuum Piped Systems – Warning Systems All master, area, and local alarm systems used for medical gas and vacuum systems comply with appropriate Category warning system requirements, as applicable. 5.1.9, 5.2.9, 5.3.6.2.2 (NFPA 99) | EC.02.05.09- EP 2 | NFPA 99 5.1.9 5.2.9 5.3.6.2.2 | IFC 5306.5 | IFC 5306.5 | IFC 5306.5 Medical gas systems and equipment |  | EB11-19 AM; EB49-19 AS Modify IFC 5306.5 to include alarm systems. Proposal developed. |  | TP
K905 | MEP | Gas and Vacuum Piped Systems – Central Supply System Identification and Labeling Containers, cylinders and tanks are designed, fabricated, tested, and marked in accordance with 5.1.3.1.1 through 5.1.3.1.7. Locations containing only oxygen or medical air have doors labeled with "Medical Gases, NO Smoking or Open Flame". Locations containing other gases have doors labeled "Positive Pressure Gases, NO Smoking or Open Flame, Room May Have Insufficient Oxygen, Open Door and Allow Room to Ventilate before opening. 5.1.3.1, 5.2.3.1, 5.3.10 (NFPA 99) | EC.02.05.09- EP 3 EC.02.05.09- EP 4 | NFPA 99 5.1.3.1 5.2.3.1 5.3.10 | IFC 1103.10 5303.4.3 5306.5 | IFC 1103.10 5303.4.3 5306.5 | IFC 1103.10 Medical gases 5303.4.3 Piping systems 5306.5 Medical gas systems and equipment IPC 1202.1 Medical Gases |  | EB11-19 AM; EB49-19 AS Add language to IFC 5306.5 on signage? Proposal developed. |  | TP
K906 | MEP | Gas and Vacuum Piped Systems – Central Supply System Operations Adaptors or conversion fittings are prohibited. Cylinders are handled in accordance with 11.6.2. Only cylinders, reusable shipping containers, and their accessories are stored in rooms containing central supply systems or cylinders. No flammable materials are stored with cylinders. Cryogenic liquid storage units intended to supply the facility are not used to transfill. Cylinders are kept away from sources of heat. Valve protection caps are secured in place, if supplied, unless cylinder is in use. Cylinders are not stored in tightly closed spaces. Cylinders in use and storage are prevented from exceeding 130°F, and nitrous oxide and carbon dioxide cylinders are prevented from reaching temperatures lower than manufacture recommendations or 20°F. Full or empty cylinders, when not connected, are stored in locations complying with 5.1.3.3.2 through 5.1.3.3.3, and are not stored in enclosures containing motor-driven machinery, unless for instrument air reserve headers. 5.1.3.2, 5.1.3.3.17, 5.1.3.3.1.8, 5.1.3.3.4, 5.2.3.2, 5.2.3.3, 5.3.6.20.4, 5.6.20.5, 5.3.6.20.7, 5.3.6.20.8, 5.3.6.20.9 (NFPA 99) | EC.02.05.09- EP 12 | NFPA 99 5.1.3.2; 5.1.3.3.1.7; 5.1.3.3.1.8; 5.1.3.3.4 5.2.3.2; 5.2.3.3 5.3.6.20.4; 5.3.6.20.5; 5.3.6.20.7; 5.3.6.20.8; 5.3.6.20.9 11.6.2 | IFC 5303.1; 5303.2. | IFC 5303.1; 5303.2.; 5306 | IFC 5303.1 Containers, cylinders and tanks 5303.2 Design and construction 5306.4 Transfilling 5306.5 Medical Gas Systems 5303.7.4 Temperature Extremes |  | EB11-19 AM Needs alignment to NFPA 99 302.3.1 Additional codes in healthcare. In existing Group I-2 occupancies, ambulatory healthcare facilities, outpatient clinics and hyperbaric facilities, alterations, repairs, additions and changes of occupancy to, or relocation of, existing buildings and structures shall also comply with the provisions for alterations, repairs, additions and changes of occupancy in NFPA 99. | Complete | TP
K907 | MEP | Gas and Vacuum Piped Systems – Maintenance Program Medical gas, vacuum, WAGD, or support gas systems have documented maintenance programs. The program includes an inventory of all source systems, control valves, alarms, manufactured assemblies, and outlets. Inspection and maintenance schedules are established through risk assessment considering manufacturer recommendations. Inspection procedures and testing methods are established through risk assessment. Persons maintaining systems are qualified as demonstrated by training and certification or credentialing to the requirements of AASE 6030 or 6040. 5.1.14.2.1, 5.1.14.2.2, 5.1.15, 5.2.14, 5.3.13.4.2 (NFPA 99) | EC.02.05.09- EP 7 | NFPA 99 5.1.14.2.1; 5.1.14.2.2; 5.1.15 5.2.14 5.3.13.4.2 | IFC 5306.5 | IFC 5306.5 IPC 1201.1, 1202.1 | IFC 5306.5 Medical gas systems and equipment IPC CHAPTER 12 SPECIAL PIPING AND STORAGE SYSTEMS 1201.1 Scope 1202.1 Nonflammable medical gases |  | SOM 482.41(a)(1)( c )(2) IFC 5306.5 "maintenance, inpsection and testing per NFPA 99" |  | TP
K908 | MEP | Gas and Vacuum Piped Systems – Inspection and Testing Operations The gas and vacuum systems are inspected and tested as part of a maintenance program and include the required elements. Records of the inspections and testing are maintained as required. 5.1.14.2.3, B.5.2, 5.2.13, 5.3.13, 5.3.13.4 (NFPA 99) | EC.02.05.09- EP 7 | NFPA 99 5.1.14.2.3 5.2.13 5.3.13; 5.3.13.4 | IFC 5306.5 | IFC 5306.5 IPC 1201.1, 1202.1 | IFC 5306.5 Medial gas systems and equipment IPC CHAPTER 12 SPECIAL PIPING AND STORAGE SYSTEMS 1201.1 Scope 1202.1 Nonflammable medical gases |  | SOM 482.41(a)(1)( c )(2) IFC 5306.5 "maintenance, inpsection and testing per NFPA 99" |  | TP
K909 | MEP | Gas and Vacuum Piped Systems – Information and Warning Signs Piping is labeled by stencil or adhesive markers identifying the gas or vacuum system, including the name of system or chemical symbol, color code (Table 5.1.11), and operating pressure if other than standard. Labels are at intervals not more than 20 ft., are in every room, at both sides of wall penetrations, and on every story traversed by riser. Piping is not painted. Shutoff valves are identified with the name or chemical symbol of the gas or vacuum system, room or area served, and caution to not use the valve except in emergency. 5.1.14.3, 5.1.11.1, 5.1.11.2, 5.2.11, 5.3.13.3, 5.3.11 (NFPA 99) | EC.02.05.09- EP 11 | NFPA 99 5.1.14.3; 5.1.11.1; 5.1.11.2, 5.2.11 5.3.13.3; 5.3.11 | IFC 5303.4.3 5003.7.1. 6303.1.3 | IFC 5303.4.3 5003.7.1. 6303.1.3 5306 | IFC 5303.4.3 Piping systems 5003.7.1 Smoking 6303.1.3 Ignition source control |  | F297-18 Part 1 and 2 AS/AS; EB49-19 AS |  | TP
K910 | MEP | Gas and Vacuum Piped Systems – Modifications Whenever modifications are made that breach the pipeline, any necessary installer and verification test specified in 5.1.2 is conducted on the downstream portion of the medical gas piping system. Permanent records of all tests required by system verification tests are maintained. 5.1.14.4.1, 5.1.14.4.6, 5.2.13, 5.3.13.4.3 (NFPA 99) | EC.02.05.09- EP 10 | NFPA 99 5.1.14.4.1; 5.1.14.4.6 5.2.13 5.3.13.4.3 | IFGC SECTION 406 |  | IFGC SECTION 406 INSPECTION, TESTING AND PURGING |  | EB49-19 AS We submitted EB49-19 |  | TP
K911 | MEP | Electrical Systems – Other List in the REMARKS section, any NFPA 99 Chapter 6 Electrical Systems requirements that are not addressed by the provided K- Tags, but are deficient. This information, along with the applicable Life Safety Code or NFPA standard citation, should be included on Form CMS-2567. Chapter 6 (NFPA 99) | EC.02.04.03- EP 27 EC.02.05.05- EP 8 | NFPA 99 Chapter 6 | IFC 1105.10; 1105.10.1; 1105.10.2. 604.1.2; 604.1.7; 604.2.6 IBC 407.10 2702.1.7; 2702.2.6 IEBC 1008.1 | IFC 1105.10; 1105.11.1; 1105.11.2. 1203 IBC 407.11 2702.1.8; 2702.2.8 IEBC 1007.1 | IFC 1105.10 Group I-2 automatic fire alarm system 1105.11.1 Where required 1105.11.2 Installation and duration 1203 Emergency and Standby Power Systems IBC 407.11 Electrical systems 2702.1.8 Group I-2 occupancies 2702.2.8 Group I-2 occupancies IEBC 1007.1 Special occupancies | Electrical Systems Handbook for Health Care Facilities Electrical Systems for Health Care Facilities Program TIAs affecting adoption of the 2012 editions of NFPA 101 and NFPA 99 Focus on Compliance: | G80-12 AMPCE, EB11-19 AM (healthcare committee submission), EB99-19 AS (healthcare Committee Submission) F255-16 AS, F76-16 AM, G80-18 |  | TP
K912 | MEP | Electrical Systems – Receptacles Power receptacles have at least one, separate, highly dependable grounding pole capable of maintaining low-contact resistance with its mating plug. In pediatric locations, receptacles in patient rooms, bathrooms, play rooms, and activity rooms, other than nurseries, are listed tamper-resistant or employ a listed cover. If used in patient care room, ground-fault circuit interrupters (GFCI) are listed. 6.3.2.2.6.2 (F), 6.3.2.2.6 (NFPA 99) | EC.02.05.01- EP 22 | NFPA 99 6.3.2.2.6.2; 6.3.2.2.2 (2018) | IEBC 607.1.4 | IEBC 406.1.4 | IEBC 406.1.4 Healthcare facilities |  | EB11-19 AM; EB46-19 AS This is a requirement so we will need to determine code location consider new section in IFC 1105.12 for this item I-2 Condition 2 pediatric receptacles per NFPA 6.3.2.2.6.2 F Proposal developed. | Proposal Needed | JF
K913 | MEP | Electrical Systems – Wet Procedure Locations Operating rooms are considered wet procedure locations, unless otherwise determined by a risk assessment conducted by the facility governing body. Operating rooms defined as wet locations are protected by either isolated power or ground-fault circuit interrupters. A written record of the risk assessment is maintained and available for inspection. 6.3.2.2.8.4, 6.3.2.2.8.7, 6.4.4.2 (NFPA 99) | EC.02.05.01- EP 20 | NFPA 99 6.3.2.2.8; 6.3.2.2.8.4; 6.3.2.2.8.7 6.4.4.2 | IFC 604.4 | IFC 1203.4 | IFC 1203.4 Maintenance 1203.4.1 Group I-2 and ambulatory care facilities | Wet Location Tool | F69-18 AS; EB49-19 AS F76-16 AM, F192-18 AS Most deal with maintenance not risk assessment. | Minor Change Needed | JF
K914 | MEP | Electrical Systems – Maintenance and Testing Hospital-grade receptacles at patient bed locations and where deep sedation or general anesthesia is administered, are tested after initial installation, replacement or servicing. Additional testing is performed at intervals defined by documented performance data. Receptacles not listed as hospital-grade at these locations are tested at intervals not exceeding 12 months. Line isolation monitors (LIM), if installed, are tested at intervals of ≤ 1 month by actuating the LIM test switch per 6.3.2.6.3.6, which activates both visual and audible alarm. For, LIM circuits with automated self-testing, this manual test is performed at intervals ≤ 12 months. LIM circuits are tested per 6.3.3.3.2 after any repair or renovation to the electric distribution system. Records are maintained of required tests and associated repairs or modifications, containing date, room or area tested, and results. 6.3.4 (NFPA 99) | EC.02.05.01- EP 22 EC.02.05.01- EP 5 EC.02.05.05- EP 7 | NFPA 99 6.3.4 | IFC 604.4 604.1.8 604.5 | IFC 1203.4; 1203.5 | IFC 1203.4 Maintenance 1203.4.1 Group I-2 and ambulatory care facilities 1203.5 Operational inspection and testing 1203.5.1 Group I-2 and ambulatory care facilities |  | SOM 482.41(a)(1)( c )(2) F69-18 AS; EB11-19 AM F76-16 AM, F192-18 AS | Complete | JF
K915 | MEP | Electrical Systems – Essential Electric System Categories Critical care rooms (Category 1) in which electrical system failure is likely to cause major injury or death of patients, including all rooms where electric life support equipment is required, are served by a Type 1 EES. General care rooms (Category 2) in which electrical system failure is likely to cause minor injury to patients (Category 2) are served by a Type 1 or Type 2 EES. Basic care rooms (Category 3) in which electrical system failure is not likely to cause injury to patients and rooms other than patient care rooms are not required to be served by an EES. Type 3 EES life safety branch has an alternate source of power that will be effective for 1 1/2 hours. 3.3.138, 6.3.2.2.10, 6.6.2.2.2, 6.6.3.1.1 (NFPA 99), TIA 12-3 | EC.02.05.01 EP 21 | NFPA 99 3.3.138 6.3.2.2.10 6.6.2.2.2; 6.6.3.1.1 | IFC 604.4 | IFC 1203.4 | IFC 1105.11 Essential eletrical systems 1105.11.1 Where required 1105.11.2 Installation and duration 1203.4 Maintenance 1203.4.1 Group I-2 and ambulatory care facilities | IFC 1203,1,3 EPS & standby pwr sys shal be installed in accordance with the IBC, NFPA 70, NFPA 110 & NFPA 11. IFC 2018 1203.1.5 duration 2 hrs 1203.1.8 Group I-2 Occupancies In Group I-2 occupancies, located in flood hazard areas established in Section 1612.3 of the International Building Code where new essential electrical systems are installed and where new essential electrical system generators are installed, the systems and generators shall be located and installed in accordance with ASCE 24. Where connections for hook up of temporary generators are provided, the connections shall be located at or above the elevation required in ASCE 24. 1203.2.1 Ambulatory Care Facilities Essential electrical systems for ambulatory care facilities shall be in accordance with Section 422.6 of the International Building Code. 1203.2.7 Group I-2 Occupancies Essential electrical systems for Group I-2 occupancies shall be in accordance with Section 407.11 of the International Building Code. | EB11-19 AM; EB49-19 AS IEBC 302.3.1 states that for I-2 any change must comply with NFPA99. this does not apply to extg if no renov or change.. IFC 1203 requires ASCs to follow IBC for emerg power?? Any issues with this? PGZ: No, since 2018 IBC references NFPA 99 for emerg pwr incldg ASCs in 2702.2.1 F76-18 AS | Complete | Pier
K916 | MEP | Electrical Systems – Essential Electric System Alarm Annunciator A remote annunciator that is storage battery powered is provided to operate outside of the generating room in a location readily observed by operating personnel. The annunciator is hard-wired to indicate alarm conditions of the emergency power source. A centralized computer system (e.g., building information system) is not to be substituted for the alarm annunciator. 6.4.1.1.17, 6.4.1.1.17.5 (NFPA 99) | EC.02.05.03- EP 11 | NFPA 99 6.4.1.1.17; 6.4.1.1.17.5 | N/A | 807.1, 807.3 IFC 1206.2.10 IFC 1206.2.10.3 | IEBC 503.1 General 707.1 Healthcare facilities 806.4 Residential occupancies |  | EB49-19 AS; EB11-19 AM; EB49-19 AS; EB99-19 AS PGZ note: EB49-19 references NFPA 99 for any alteration of existing electrical or med gas system for I-2, Ambul care or outpatient. Was approved as submitted. EB99-19 deals with hyperbaric, references NFPA 99 and was approved with minor nonsubstantive committee change. EB11-19 also references NFPA 99 for similar and was approved as modified with same minor committee change. So what is the equivalent action for IBC as opposed to IEBC covered here? ANSWER: We are covered for changes in an existing building above code change approvals AND previos cycle A effective in 2018 IBC references compliance with NFPA 99 for new construction. See also PZ comment under K919. | Complete | Pier
K917 | MEP | Electrical Systems – Essential Electric System Receptacles Electrical receptacles or cover plates supplied from the life safety and critical branches have a distinctive color or marking. 6.4.2.2.6, 6.5.2.2.4.2, 6.6.2.2.3.2 (NFPA 99) | EC.02.05.01- EP 22 . | NFPA 99 6.4.2.2.6 6.5.2.2.4.2 6.6.2.2.3.2 | IEBC 607.1.4 | IEBC 406.4 | IEBC 406.4 Healthcare facilities |  | EB46-19 AS | Complete | Pier
K918 | MEP | Electrical Systems – Essential Electric System Maintenance and Testing The generator or other alternate power source and associated equipment is capable of supplying service within 10-seconds. If the 10-second criterion is not met during the monthly test, a process shall be provided to annually confirm this capability for the life safety and critical branches. Maintenance and testing of the generator and transfer switches are performed in accordance with NFPA 110. Generator sets are inspected weekly, exercised under load 30 minutes 12 times a year in 20-40 day intervals, and exercised once every 36 months for 4 continuous hours. Scheduled test under load conditions include a complete simulated cold start and automatic or manual transfer of all EES loads, and are conducted by competent personnel. Maintenance and testing of stored energy power sources (Type 3 EES) are in accordance with NFPA 111. Main and feeder circuit breakers are inspected annually, and a program for periodically exercising the components is established according to manufacturer requirements. Written records of maintenance and testing are maintained and readily available. EES electrical panels and circuits are marked and readily identifiable. Minimizing the possibility of damage of the emergency power source is a design consideration for new installations. 6.4.4, 6.5.4, 6.6.4 (NFPA 99), NFPA 110, NFPA 111, 700.10 (NFPA 70) | EC.02.05.01- EP 9 EC.02.05.03- EP 5 EC.02.05.03- EP 6 EC.02.05.03- EP 7 EC.02.05.03- EP 11 EC.02.05.07- EP 3 EC.02.05.07- EP 4 EC.02.05.07- EP 5 EC.02.05.07- EP 6 EC.02.05.07- EP 7 EC.02.05.07- EP 9 EC.02.05.07- EP 10 | NFPA 99 6.4.4 6.5.4 6.6.4 NFPA 110 NFPA 111 NFPA 70 700.10 | IFC 604.4 | IFC 1203.4 | IEBC 503.1 General 706.1 General 806.3 Healthcare facilities IFC 1203.4 Maintenance 1203.4.1 Group I-2 and ambulatory care facilities | Video: Changes to the Conditions of Participation impacting health care facilities (June 27, 2016) | SOM 482.41(a)(1)( c )(2) EB49-19 AS IEBC 806.3 lateral loads? IFC 1203.4 follow NFPA 110 & 111 for maint, 1203.4.1 follow NFPA 99 in I-2 for maint | Complete | Pier
K919 | MEP | Electrical Equipment – Other List in the REMARKS section, any NFPA 99 Chapter 10, Electrical Equipment, requirements that are not addressed by the provided K-Tags, but are deficient. This information, along with the applicable Life Safety Code or NFPA standard citation, should be included on Form CMS-2567. Chapter 10 (NFPA 99) | EC.02.04.03- EP 27 | NFPA 99 Chapter 10 | N/A | N/A | N/A | Evaluating Electrical Distribution Equipment to Determine Replacement Needs (2013) Krista McDonald Biason, PE | NFPA 99 Chp 10 covers oxygen enriched atmospheres. The monograph mentions NFPA 99 requirements for fault current and separate branch circuits. Older HC facilities may be required to bring their essential electrical system branch circuits up to code by being properly separated. This has already been addressed by EB 49-19. What is the code reference for NEW construction having separate life safety, critical & equipment branches when generator greater than 150 kVA? Tag K911 covers NFPA 99 chptr 6 which does cover EES. where does IBC, NEC require these conceepts for new construction. ANSWER: 2018 IBC sections 407.11 covers elec sys for I-2 to comply with NFPA 99. Sectons 422.6 similar for ambulatory care and 425.1 similar for hyperbaric facilities. | Complete | Pier
K920 | MEP | Electrical Equipment – Power Cords and Extension Cords Power strips in a patient care vicinity are only used for components of movable patient-care-related electrical equipment (PCREE) assembles that have been assembled by qualified personnel and meet the conditions of 10.2.3.6. Power strips in the patient care vicinity may not be used for non-PCREE (e.g., personal electronics), except in long-term care resident rooms that do not use PCREE. Power strips for PCREE meet UL 1363A or UL 60601-1. Power strips for non-PCREE in the patient care rooms (outside of vicinity) meet UL 1363. In non-patient care rooms, power strips meet other UL standards. All power strips are used with general precautions. Extension cords are not used as a substitute for fixed wiring of a structure. Extension cords used temporarily are removed immediately upon completion of the purpose for which it was installed and meets the conditions of 10.2.4. 10.2.3.6 (NFPA 99), 10.2.4 (NFPA 99), 400-8 (NFPA 70), 590.3(D) (NFPA 70), TIA 12-5 | EC.02.05.01- EP 23 EC.02.05.01- EP 24 . | NFPA 99 10.2.3.6 10.2.4 NFPA 70 400-8 590.3(D) | IFC 605.5 | IFC 604.5 | IFC 603.6 Extension cords | Quantifying Hospital Cord Connected Plug Loads in Inpatient Areas(2014) Jason V. D’Antona, PE, LEED® AP, and John Messervy, AIA TIAs affecting adoption of the 2012 editions of NFPA 101 and NFPA 99 EC.02.05.01 Inappropriate Electrical Issues [EP1] HITF Interpretations, June 2014 | F73-18 AS, F82-16 AS F73-18 added IBC 604.1.1 604.4.1.1 Listing in Group I-2 occupancies and ambulatory care f acilities. . In Group I-2 occupancies and ambulatory care facilities, relocatable power taps shall be listed in accordance with UL 1363 except under the following conditions. 1. In Group I-2, Condition 2 occupancies, relocatable power taps providing power to patient carerelated electrical equipment in the patient care vicinity as defined by NFPA 99 shall be listed in accordance with UL 1363A or UL 60601-1. 2. In Group I-2, Condition 1 facilities, in care recipient rooms using line-operated patientcare-related electrical equipment, relocatable power taps in the patient care vicinity as defined by NFPA 99 shall be listed in accordance with UL 1363A or UL 60601-1. 3. In ambulatory care facilities, relocatable power taps providing power to patient care-related electrical equipment in the patient care vicinity as defined by NFPA 99 shall be listed in accordance with UL 1363A or UL 60601-1. | Complete | Pier
K921 | MEP | Electrical Equipment – Testing and Maintenance Requirements The physical integrity, resistance, leakage current, and touch current tests for fixed and portable patient-care related electrical equipment (PCREE) are performed as required in 10.3. Testing intervals are established with policies and protocols. All PCREE used in patient care rooms is tested in accordance with 10.3.5.4 or 10.3.6 before being put into service and after any repair or modification. Any system consisting of several electrical appliances demonstrates compliance with NFPA 99 as a complete system. Service manuals, instructions, and procedures provided by the manufacture include information as required by 10.5.3.1.1 and are considered in the development of a program for electrical equipment maintenance. Electrical equipment instructions and maintenance manuals are readily available, and safety labels and condensed operating instructions on the appliance are legible. A record of electrical equipment tests, repairs, and modifications is maintained for a period of time to demonstrate compliance in accordance with the facility's policy. Personnel responsible for the testing, maintenance and use of electrical appliances receive continuing trained. 10.3, 10.5.2.1, 10.5.2.1.2, 10.5.2.5, 10.5.3, 10.5.6, 10.5.8 | EC.02.04.03 EP 27 | NFPA 99 10.3 10.5.2.1; 10.5.2.1.2; 10.5.2.5 10.5.3 10.5.6 10.5.8 | IFC | IFC 604.5 | IEBC 503.1 General 706.1 General 806.3 Healthcare facilities IFC SECTION 603 ELECTRICAL EQUIPMENT, WIRING AND HAZARDSSYSTEMS 603.1.1.1 Healthcare facilities | Managing Hospital Emergency Power Systems: Testing, Operation, Maintenance, Vulnerability Mitigation, and Power Failure Planning (2014) David L. Stymiest, PE, CHFM, CHSP, FASHE | EB 49-19 F69-18 AS F69-18 added 604.1.1 Healthcare f acilities. In Group I-2 facilities, ambulatory care facilities and outpatient clinics, the electrical systems and equipment shall be maintained and tested in accordance with NFPA 99. | Complete | Pier
K922 | MEP | Gas Equipment – Other List in the REMARKS section, any NFPA 99 Chapter 11 Gas Equipment requirements that are not addressed by the provided K-Tags, but are deficient. This information, along with the applicable Life Safety Code or NFPA standard citation, should be included on Form CMS-2567. Chapter 11 (NFPA 99) | EC.02.05.09- EP 14 | NFPA 99 Chapter 11 | IMC 502.9; 502.9.1 Storage Rooms | IMC 502.9; 502.9.1 IFC 5306.5 | IMC 502.9 Hazardous materials—requirements for specific materials 502.9.1 Compressed gases—medical gas systems | Focus on Compliance: Utility systems (EC.02.05.01) (August/September 2015) | Need reference in IMC for NPFA 99 for medical gas systems. IMC reference here is for storage areas. IPC 1202.1 refences installation. Referenced in IFC 5306.5 Remap NFPA 99 requirements into ICC Codes | Complete | TP
K923 | MEP | Gas Equipment – Cylinder and Container Storage ≥ 3,000 cubic feet Storage locations are designed, constructed, and ventilated in accordance with 5.1.3.3.2 and 5.1.3.3.3. > 300 but <3,000 cubic feet Storage locations are outdoors in an enclosure or within an enclosed interior space of non- or limited- combustible construction, with door (or gates outdoors) that can be secured. Oxidizing gases are not stored with flammables, and are separated from combustibles by 20 feet (5 feet if sprinklered) or enclosed in a cabinet of noncombustible construction having a minimum 1/2 hr. fire protection rating. ≤ 300 cubic feet In a single smoke compartment, individual cylinders available for immediate use in patient care areas with an aggregate volume of ≤ 300 cubic feet are not required to be stored in an enclosure. Cylinders must be handled with precautions as specified in 11.6.2. A precautionary sign readable from 5 feet is on each door or gate of a cylinder storage room, where the sign includes the wording as a minimum "CAUTION: OXIDIZING GAS (ES) STORED WITHIN NO SMOKING". Storage is planned so cylinders are used in order of which they are received from the supplier. Empty cylinders are segregated from full cylinders. When facility employs cylinders with integral pressure gauge, a threshold pressure considered empty is established. Empty cylinders are marked to avoid confusion. Cylinders stored in the open are protected from weather. 11.3.1, 11.3.2, 11.3.3, 11.3.4, 11.6.5 (NFPA 99) | EC.02.05.09- EP 5 EC.02.05.09- EP 6 EC.02.05.01- EP 18 | NPFA 99 11.3.1; 11.3.2; 11.3.3; 11.3.4 11.6.2; 11.6.5 | IFC 1103.10 5303.16; 5303.16.2 5306; 5306.1; 5306.2; 5306.2.1; 5306.2.2; 5306.2.3; 5306.3 | IFC 1103.10 5303.16; 5303.16.2 5306; 5306.1; 5306.2; 5306.2.1; 5306.2.2; 5306.2.3; 5306.3 | IFC 1103.10 Medical gases 5303.16 Vaults 5303.16.2 Design and construction 5306 Medical gases 5306.1 General 5306.2 Interior supply location 5306.2.1 One-hour exterior rooms 5306.2.2 One-hour interior room 5306.2.3 Gas cabinets 5306.3 Exterior supply locations IBC SECTION 427 MEDICAL GAS SYSTEMS 427.1 General. 427.2 Interior supply location. 427.2.1 One-hour exterior room. 427.2.2 One-hour interior room. 427.2.3 Gas cabinets. | Medical Gas Cylinder and Bulk Tank Storage (2012) Susan B. McLaughlin, MBA, FASHE, CHFM, CHSP; David A. Dagenais, CHSP, CHFM, SASHE Focus on Compliance: EC.02.06.01 Medical Gas Cylinder Storage [EP1] | F282-18 D not K-tag, but could be local alignment issue EB49-19 AS, F367-16 AS, F368-16 AS, G127-15 AMPC, F296-18 AS | Minor Change Needed | GH
K924 | MEP | Gas Equipment – Testing and Maintenance Requirements Anesthesia apparatus are tested at the final path to patient after any adjustment, modification or repair. Before the apparatus is returned to service, each connection is checked to verify proper gas and an oxygen analyzer is used to verify oxygen concentration. Defective equipment is immediately removed from service. Areas designated for servicing of oxygen equipment are clean and free of oil, grease, or other flammables. Manufacturer service manuals are used to maintain equipment and a scheduled maintenance program is followed. 11.4.1.3, 11.5.1.3, 11.6.2.5, 11.6.2.6 (NFPA 99) | EC.02.04.01- EPs 2-6 EC.02.04.03- EP 2 | NFPA 99 11.4.1.3, 11.5.1.3, 11.6.2.5, 11.6.2.6 | IFC 5306.5 | IFC 5306.5 | IFC 5306.5 Medical gas systems and equipment |  | SOM 482.41(a)(1)( c )(2) F297-18 Part 1 and 2 AS/AS | Complete | GH
K925 | MEP | Gas Equipment – Respiratory Therapy Sources of Ignition Smoking materials are removed from patients receiving respiratory therapy. When a nasal cannula is delivering oxygen outside of a patient’s room, no sources of ignition are within in the site of intentional expulsion (1-foot). When other oxygen deliver equipment is used or oxygen is delivered inside a patient’s room, no sources of ignition are within the area are of administration (15-feet). Solid fuel-burning appliances is not in the area of administration. Nonmedical appliances with hot surfaces or sparking mechanisms are not within oxygen-delivery equipment or site of intentional expulsion. 11.5.1.1, TIA 12-6 (NFPA 99) | EC.02.03.01- EP 1 Commentary: No specific TJC requirement for protection from sources of ignition in respiratory therapy areas. | NFPA 99 11.5.1.1 | IFGC 303.3 IFC 5003.7.1 | IFGC 303.3 IFC 5003.7.1 | IFGC 303.3 Fireplaces and decorative appliances in Group I-2 occupancies IFC 5003.7.1 Smoking |  | F286-18 AS; EB49-19 AS; F122-18 Part II | Complete | GH
K926 | MEP | Gas Equipment – Qualifications and Training of Personnel Personnel concerned with the application, maintenance and handling of medical gases and cylinders are trained on the risk. Facilities provide continuing education, including safety guidelines and usage requirements. Equipment is serviced only by personnel trained in the maintenance and operation of equipment. 11.5.2.1 (NFPA 99) | EC.02.05.09- EP 7 | NFPA 99 11.5.2.1 | N/A | N/A | N/A |  | F295-18 AS Commentary: No related I-Code requirement. | Complete | GH
K927 | MEP | Gas Equipment – Transfilling Cylinders Transfilling of oxygen from one cylinder to another is in accordance with CGA P-2.5, Transfilling of High Pressure Gaseous Oxygen Used for Respiration. Transfilling of any gas from one cylinder to another is prohibited in patient care rooms. Transfilling to liquid oxygen containers or to portable containers over 50 psi comply with conditions under 11.5.2.3.1 (NFPA 99). Transfilling to liquid oxygen containers or to portable containers under 50 psi comply with conditions under 11.5.2.3.2 (NFPA 99). 11.5.2.2 (NFPA 99) | EC.02.05.09- EP 6 EC.02.05.09- EP 7 EC.02.05.09- EP 13 | NFPA 99 11.5.2.2 11.5.2.3; 11.5.2.3.1; 11.5.2.3.2 | IFC 5306.4; 5306.5 | IFC 5306.4; 5306.5 | IFC 5306.4 Transfilling 5306.5 Medical gas systems and equipment |  | EB49-19 AS | Complete | GH
K928 | MEP | Gas Equipment – Labeling Equipment and Cylinders Equipment listed for use in oxygen-enriched atmospheres are so labeled. Oxygen metering equipment and pressure reducing regulators are labeled "OXYGEN-USE NO OIL". Flowmeters, pressure reducing regulators, and oxygen-dispensing apparatus are clearly and permanently labeled designating the gases for which they are intended. Oxygen-metering equipment, pressure reducing regulators, humidifiers, and nebulizers are labeled with name of manufacturer or supplier. Cylinders and containers are labeled in accordance with CGA C-7. Color coding is not utilized as the primary method of determining cylinder or container contents. All labeling is durable and withstands cleaning or disinfecting. 11.5.3.1 (NFPA 99) | EC.02.05.09- EP 12 EC.02.05.09- EP 14 Commentary: No specific TJC requirement to address labeling of gas equipment and cylinders. Reference is to general Chapter 11 citation. | NFPA 99 11.5.3.1 | IFC 5303.1 5303.4; 5303.4.1; 5303.4.2 | IFC 5303.1 5303.4; 5303.4.1; 5303.4.2 | IFC 5303.1 Containers, cylinder and tanks 5303.4 Marking 5303.4.1 Stationary compressed gas containers, cylinder and tanks 5303.4.2 Portable containers, cylinders and tanks |  | F297-18 Part 1 and 2 AS/AS | Complete | GH
K929 | MEP | Gas Equipment – Precautions for Handling Oxygen Cylinders and Manifolds Handling of oxygen cylinders and manifolds is based on CGA G-4, Oxygen. Oxygen cylinders, containers, and associated equipment are protected from contact with oil and grease, from contamination, protected from damage, and handled with care in accordance with precautions provided under 11.6.2.1 through 11.6.2.4 (NFPA 99) 11.6.2 (NFPA 99) | EC.02.05.09- EP 12 | NFPA 99 11.6.2; 11.6.2.1; 11.6.2.2; 11.6.2.3; 11.6.2.4 | IFC 5303.5; 5303.5.1; 5303.5.2; 5303.5.3 | IFC 5303.5; 5303.5.1; 5303.5.2; 5303.5.3 | IFC 5303.5 Security 5303.5.1 Security of areas 5303.5.2 Physical protection 5303.5.3 Securing compressed gas containers, cylinders and tanks |  | 2018 did not address this. None of the IFC sections in 2021 either. We will need to look at doing something to address the issues not addressed such as protection from contact with oil or grease, protection from contamination, and proper handling | Proposal Needed | BL/JF
K930 | MEP | Gas Equipment – Liquid Oxygen Equipment The storage and use of liquid oxygen in base reservoir containers and portable containers comply with sections 11.7.2 through 11.7.4 (NFPA 99). 11.7 (NFPA 99) | EC.02.05.09- EP 12 Commentary: No specific TJC requirement to address liquid oxygen storage. Reference is to general Chapter 11 citation. | NFPA 99 11.7; 11.7.2; 11.7.3; 11.7.4 | IFC 6301; 6301.1 | IFC 6301; 6301.1 | IFC CHAPTER 63 OXIDIZERS, OXIDIZING GASES AND OXIDIZING CRYOGENIC FLUIDS 6301 General 6301.1 Scope |  | These references in the IFC do not cover the context of the K-tag. We will need to look at doing something to address this | Proposal Needed | BL/JF
K931 | MEP | Hyperbaric Facilities All occupancies containing hyperbaric facilities comply with construction, equipment, administration, and maintenance requirements of NFPA 99. Chapter 14 (NFPA 99) | N/A Commentary: No TJC requirements related to hyperbaric facilities. | NFPA 99 Chapter 14 | IFC 611; 611.1; 611.2 | IFC 609; 609.1; 609.2 IBC 425; 425.1 | IBC 425 HYPERBARIC FACILITIES 425.1 Hyperbaric facilities IFC SECTION 609 HYPERBARIC FACILITIES 609.1 General. 609.2 Records. |  | G78-18 AS |  | TP
K932 | Fire | Features of Fire Protection – Other List in the REMARKS section, any NFPA 99 Chapter 15 Features of Fire Protection requirements that are not addressed by the provided K-Tags, but are deficient. This information, along with the applicable Life Safety Code or NFPA standard citation, should be included on Form CMS-2567. Chapter 15 (NFPA 99) | N/A | NFPA 99 Chapter 15 | N/A | N/A | IFC 404.2.3 Lockdown plans. 404.2.3.1 Lockdown plan contents. 404.2.3.2 Drills. 404.3 Maintenance 404.4 Availability 404.4.1 Distribution 405.1 General 406.3.4 Emergency lockdown trainings. |  | So generic, difficult to deal with F33-16 AS, F39-18 AM |  | Nanci/Mark
K933 | Fire | Features of Fire Protection – Fire Loss Prevention in Operating Rooms Periodic evaluations are made of hazards that could be encountered during surgical procedures, and fire prevention procedures are established. When flammable germicides or antiseptics are employed during surgeries utilizing electrosurgery, cautery or lasers:  packaging is non-flammable  applicators are in unit doses  Preoperative "time-out" is conducted prior the initiation of any surgical procedure to verify: o application site is dry prior to draping and use of surgical equipment o pooling of solution has not occurred or has been corrected o solution-soaked materials have been removed from the OR prior to draping and use of surgical devices o policies and procedures are established outlining safety precautions related to the use of flammable germicide or antiseptic use. Procedures are established for operating room emergencies including alarm activation, evacuation, equipment shutdown, and control operations. Emergency procedures include the control of chemical spills, and extinguishment of drapery, clothing and equipment fires. Training is provided to new OR personnel (including surgeons), continuing education is provided, incidents are reviewed monthly, and procedures are reviewed annually. 15.13 (NFPA 99) | N/A Commentary: No TJC requirements related to fire prevention in operating rooms. | NFPA 99 15.13 |  |  | IFC 403.7.2.5 Fire loss prevention in operating systems |  | F33-18 AS |  | Nanci/Mark
Future List Items
CMS Tag | Group | Description of issue | TJC EP Reference1 | NFPA 101 Reference 2012 Edition2 |  | ICC Reference 2018 Edition | ICC Reference 2021 Edition | Resource / source of idea | Comments | Complete?
| MEP | Clarify Mechanical Ventilation in Group I-1 and I-2 | [5 empty] | see failed M50 and M51 in 2021 cycle | We need to try them again as is. It came up early and there was no one from Healthcare to testify. M50 was disapproved because someone argued that all kitchens in Group I-1 and I-2 should vent to the outside – but they were not separating commercial kitchens from domestic kitchens. M51 was disapprove to be consistent with M50, not realizing that the were doing 2 different things. | Complete | GH/Jeff O'Niel
| MEP | MEP - range hood in apartment in assisted living? Allow recirculating hood. | [8 empty] | JF
| MEP | Figure out if Suspended Electric Heaters are allowed in the means of Egress See M81.2021 and public comment to add heaters |  | NFPA 101 18.5.2.3 | [6 empty] | JF
| MEP | Pharmacy air quality USP 797 and 800 Review for conflict with IMC | [6 empty] | Covered for USP 797 in ASHRAE 170. ASHRAE 170 has group working on USP language. Adding language to ASHE/ASHRAE 170 in footnote. | Proposal Needed | Pier/Benjamin
| MEP | Centralized monitoring, Telemetry, medical/digital routing storage Do these need to be more robust | [6 empty] | More clarity on scope |  | JF
| MEP | monitoring and data storage, Chapter 16 for hazard list | [6 empty] | Reach to John Williams |  | TP
| MEP | medical gas storge and adminstration to meet NFPA 99 LSC 18.3.2.4 |  | NFPA 101 18.3.2.4 | [6 empty] | GH
| MEP | anesthetizing locations to meet NFPA 99 LSC 18.3.2.3 |  | NFPA 101 18.3.2.3 | [6 empty] | GH
K921 | MEP | Move chapter 11 of the IFC into the IEBC Electrical testing and Maintenance requirements (Think this might be addressed by referencing NFPA 99) | [6 empty] | IEBC does not deal with Maintenance - scope change? | DOA | TP/Beth Tubbs
| MEP | Move chapter 11 of the IFC into the IEBC Liquid Oxygen equipment and storage | [6 empty] | Not expected to change. | DOA | TP
| MEP | see Henry for further information; IFC 5306/Compressed Gases 5307 | [8 empty] | GH
K916 | MEP | K916 EES alarm annunciator | [6 empty] | Add to K916 | Complete | Pier
| MEP | Cold water hand washing | [7 empty] | Proposal Needed | JF/Benjamin
| MEP | Vestibules required for energy |  |  |  |  | IECC 402.5.7 |  |  | Complete
| MEP | LCS/IBC Alignment question - IBC s. 425.1 requires hyperbaric facilities to meet NFPA 99. LSC s. 18.3.2.4 requires medical gas storage and administration to meet NFPA 99. LSC s. 18.3.2.3 requires anesthetizing locations to meet NFPA 99. | [8 empty] | TP
| MEP | K921 Elec equipment testing and maintenance requirements (Think this might be addressed by referencing NFPA 99) | [6 empty] | Add This to K921 comments. Pier is checking but this should be covered by NFPA 99 reference. | ? | Pier
K930 | MEP | K930 Liquid O2 equipment and storage | [7 empty] | Proposal Needed | BL/JF
| MEP | As written in both 420.8 and 904.13, Group I occupancies would have to install a UL 300A style hood everywhere a cooktop, range, or any other domestic cooking appliance is installed. While I think the intent should be in-line with Section 407.2.6 for I-2, cooking equipment open to the corridor. The current language would require compliance with all the provisions in 420.8 in every ALF resident unit where there is any kind of cooking equipment installed.
?? | General | Regular wood roofs on I-2 buildings - we need to correct disconnect between Class A roof requirement and Chapter 15 table | [6 empty] | Check former proposal against K-Tag and confirm alignment - Joe Holland suggests adding Class A requirement to Table in Chapter 15
| General | Lock-ups: How do we deal with this in a mixed occupancy? Separated Occupancy? non healthcare suites? | [5 empty] | Coordinate with Dave Frable/Bob Davidson | Check former proposals - Secluded room/padded room in hospitals, behavioral treatment, substance abuse center. From John - very challenging issue, probably needs a very broad group of people to find common ground - more about staffing, human side of the challenge, not the physical lock side of the challenge - restraint for person's safety vs. society's safety - I-3 definition "detained for penal or correctional purposes"
| General | Lock-ups: what is an acceptable size/protection for a incidental/accessory use? | [5 empty] | Coordinate with Dave Frable/Bob Davidson
| General | Lock-ups: how do we better define this so that secure memory support settings are not considered I-3? | [6 empty] | May have been addressed in 2018/2021 cycle - This really is more of an education of AHJ issue than a code change need
| General | Mechanical Ventilation in Group I-1 and I-2 - need to modify so that re-circulating hoods are permitted | [6 empty] | Refer to failed M50 & M51 in 2021 cycle - work with John Tacker / VBOA/CALBO
| General | Electric heaters in Stair towers/means of egress | [6 empty] | See M81 in 2021 cycle and public comment
| General | Control vestibules (Man trap) | [5 empty] | John W. - include Wayne Jewell & Steve Thomas | E49 -18 - PC1 but lost in on-line vote - need to bring it back with the revised language - look at it to make sure language is good
| MOE | "stuff in the corridors" - storage in corridors - what's allowed, how defined, etc | [6 empty] | Alcoves, and items that aren't blocking required width but could be combustible
| General | Retail Healthcare - are the existing occupancy classifications enough to cover what's out there? Do they need to be expanded? | [6 empty] | Nervous covering it under ambulatory healthcare, oral surgery, plastic surgery, dialysis
| General | Off-site medical facilities - file storage, centralized monitoring, etc - how are these defined? Are these considered part of critical infrastructure and need to be protected in a natural disaster? | [6 empty] | Probably can't cover - too broad. Dependent on each facility's risk assessment plan and how they choose to protect them, if they need to be protected
| General | IBC does not expressly define hazardous in definition of suites |  | 3.3.272 Hazardous suite definition; 18.2.5.7.1.3 hazardous suite provisions |  |  |  | David Soens - Henry will tackle | This is a suggestion by David Soens. Need Henry to shed more light. In my view, "hazardous" is defined adequately and doesn't need to be specifically addressed in the definition of suites. | ?
| General | Contiguous occupancies |  | 18.1.3.1 - " Sections of health care facilities shall be permitted to be classified as other occupancies, provided that they meet both of the following conditions:" 1) not more than 4 and 2) separated by 2 hour fire wall |  |  |  | David Soens - Henry will tackle |  | ?
| General | Sprinkler Requirement - NFPA allows portions of buildings not to be sprinkled when approved by AHJ |  | 18.3.5.5 |  |  |  | David Soens | I don't think we should make ICC less restrictive - no changes recommended
| General | Corridor width in patient care suites - not clearly defined but defaults to corridor width. Should be able to reduce width of aisle inside of care suites. Commentary is confusing and contradictory. |  |  |  | IBC: 407.4.4.5; 407.4.4.6; 1018.5; 1020.2 |  | Ajay Prasad
| General | Related to Above: Clarify that 96" corridor width is not a minimum for all corridors throughout an I-2 use, but only in certain areas. Nursing homes find this is interpreted to mean that the entire path of egress, up to the main entrance, must maintain minimum 8' clearance. Even exit discharge corridors, leading from a stair tower with access only from above, must be 8 foot wide. Common sense is not used. |  |  |  | Table 1020.2 |  | Ajay Prasad & Amy Carpenter
| General /MOE | DOJ and Acess board interpret all I-occupancies as long-term medical care and require higher % of accessible rooms. In their view, if Assisted Living is a licensed level of care it must be the same as long-term care. There is a big disconnect between what IBC required for I-1 occupancies, versus I-2 Occupancies | [5 empty] | Dave Yanchulis - Access Board | No change required/recommended on our side, but discussion/education needs to be had with DOJ and Access board.
| General/MEP | As written in both 420.8 and 904.13, Group I occupancies would have to install a UL 300A style hood everywhere a cooktop, range, or any other domestic cooking appliance is installed. While I think the intent should be in-line with Section 407.2.6 for I-2, cooking equipment open to the corridor. The current language would require compliance with all the provisions in 420.8 in every ALF resident unit where there is any kind of cooking equipment installed. |  |  |  | 420.8 |  | Allen Spaulding & Dan Purgiel | Additional language to clarify where UL 300 A hoods are needed and also re-circulation permitted
| General | How would a homeless shelter be classified? I-1 or R-1? Group homes were residents are supervised but do not need help? Literal text requires custodial care. Could be an issue with Group I-1 Condition 1 because they do not receive custodial care. |  |  |  | 308.1; 308.2;
| General | Separation walls scoping language is confusing and could be better described. If using intervening rooms and no corridor than 420.2 still kicks in 45 min unit entry door with closer. It is not clear if the corridor wall also is required to meet this provision besides the corridor 20 minute requirement. Some interpret that the 20 minute and 45 minutes are required. |  |  |  | 420.2 |  | Dan Purgeil | What happened with proposal from last cycle shared with dorm folks? Similar to definition on what constituted a sleeping unit
| General / MOE | Open spaces to corridors has been misinterpreted to be just limited to those spaces listed, since “and similar spaces” is not listed, meaning it should be inferred that this exception should also allow dining areas be open to a corridor under this provision. DCP has a had a case in CO where the corridor open was not allowed because specific room not listed. |  |  |  | 420.7 |  | Dan Purgeil | Needs discussion with larger group
| General | Is there an alternate to providing closers on corridor doors (maybe when no cooking present in unit?) at I-1 occupancies? Closers are heavy and pose great challenges to residents with mobility aides to go in and out through door. Consider using some of the concepts not requiring door closers from the correlating NFPA 101 Chapter 32 and 33 Residential Board and Care (RB&C) occupancy |  |  |  | IBC Section 716 |  | Dan Purgiel & Amy Carpenter | Talk to John W. Collect data for injuries caused by door closers as proof as issue.
| General | Table 510.2.4 Special Provisions. Should at least some I-1 C1 or I-1C2 or even R4 be considered to be added to this provision or other 510 provisions? | [5 empty] | Dan Purgiel | Needs clarification - are you looking at incidental use table? Or text of section 510.2?
| MOE | Section 1020.6 Corridor Continuity : In R, I-1 and R-4 using intervening rooms in large household or dorms often run into the wrong interpretation of the word “an” meaning one end the corridor is required to terminate at an exit and the other end has options. It might be time to codify better the 2 pages in the Commentary trying to describe the word “an” in the Corridor Continuity section. |  |  |  | IBC: 1020.6
| General | IBC I-1 Chapter 3 and IEBC: Better describe the difference between Condition 1 and Condition 2 especially for existing buildings that may have some C2 residents now. Also consider some modification of existing buildings that are NFPA 13R that cannot get to NFPA13 but may have some C2 residents. At least allow on the first floor? And or second with horizontal exit? And add smoke barriers on each floor in combustible construction. Create a prescription path to get there? | [5 empty] | Dan Purgiel
| General | IFC Emergency Preparedness and Evacuation: Review recent changes and confirm that concepts of staged evacuation whether implied or by a possible new definition is coordinated between I-1 abd defend in place I-2 | [5 empty] | Dan Purgiel
| General | Therapy/activity cooking - no hood protection needed
1 | Fire | Regular wood roofs on I-2 buildings - we need to correct disconnect between Class A roof requirement and Chapter 15 table
3B | Fire | Mixed and separated occupies, accessory uses and non healthcare suites. What is a hospital? When I Group I-2 more stringent that other occupancies? What is an acceptable level of incidental(accessory) | [6 empty] | Nanci will send CA revisions to Sectin 508 for possible options - allows for seperation for areas past accessory Do we need to address sleep labs? Is this group B? Do we need to address sleep labs? Is this group B? 10-19-2020: for doctor's sleeping room not require sleeping unit seperation, but ask for smoke alarm in room; Nanci has suggested language for 508.2.4 Item 3 and 4 in CA, but maybe better in Chapter 4 |  | Nanci
8 | Fire | Sprinklers in existing Group I-1 | [6 empty] | Did we address fire areas with sprinklers added getting to remove smoke protection features like door closer.
12 | Fire | Labs in healthcare | [6 empty] | Jeff working with BCAC
16 | Fire | LCS/IBC Alignment question - LSC 18.3.5.1 Buildings containing health care facilities shall be protected throughout by an approved, supervised automatic sprinkler system in accordance with Section 9.7 IBC 407.6 Smoke compartments containing sleeping rooms shall be equipped throughout with an automatic fire sprinkler system in accordance with Section 903 |  |  |  |  | IFC 5306
46 | Fire | Sprinkler Requirement - NFPA allows portions of buildings not to be sprinkled when approved by AHJ |  |  |  |  | IFC 904.2 |  | Should the be allownces for other suppression systems in areas of the hospital and still be considered sprinklered throughout - -example: MRI or comupter rooms?
21A | Fire | Are you proposing to move Chapter 11 to the IEBC or to copy it into the IEBC? Remember that the IEBC is not intended to establish a minimum level in existing buildings; but rather, what level of protection is required when work (upgrades) are taking place in an existing building. | [6 empty] | Double check IEBC Chapter 3 - do we want to add IFC Chapter 11 in IEBC and/or look at moving hospital requrirments into one place.
21B | Fire/General | With respect to K131, NFPA 101 requires a fire barrier meeting horizontal exit construction requirements to not provide smoke barriers in another occupancy on the same floor as health care. The IBC requires a two-hour fire barrier. There are some subtle differences.
21C | Fire | Corridor wall construction (again) - continuity
24 | Fire | K347 Cooking facilities open to corridor | [6 empty] | Cooking for nutritional counseling/rehab?
36 | Fire | I-1 unit entry doors in rated corridors require door closers. This is challenging for senior population to use. Consider using some of the concepts not requiring door closers from the correlating NFPA 101 Chapter 32 and 33 Residential Board and Care (RB&C) occupancy. |  |  |  |  | IBC Section 708 Fire partitions 716 Opening protectives |  | Need exception for door closers in Group I-1 for resident areas/units
38B | Fire/General | Clarifying the interpretation of the basis of I-2 Condition 2 allowing limited assistance with evacuation. Should this be more defined. The G31 2015 has extensive writing on the limits. the 2015 and 2018 IBC Commentary lays down three conceptual differences between I-1 and I-2. Is that sufficient? |  |  |  |  | IBC Section 308.3: IFC Chapter 4 |  | Do we need to beef this up in the fire and safety evacuation plans? Defintion? Group I-1 Condition 2 only The plan has to consider the level of assistance needed by the residents serrved and staff training..
38C | Fire/General | IFC Emergency Preparedness and Evacuation: Review recent changes and confirm that concepts of staged evacuation whether implied or by a possible new definition is coordinated between I-1 and defend in place I-2 | [6 empty] | Kim to send 2021 IFC Chapte 4 for Jeff |  | Jeff
39 | Fire/General | Separation of Group I-2 and I-1 in the same building |  |  |  |  | Table 508.4 footnoat a reference to 420 |  | Carification in 420 and 508.3.3 Exception 2: Should this be a 2 hour fire barrier or just a smooke barrier - not clear. See also 508.3.1.2 Do we have the same level of concern of assisted living vs. nuring home? Being treated the same as seperation from hosptial?