## Directions
Construction and Plans for Operation Compliance Documentation – Directions
Compliance Forms
Compliance forms are provided in the User’s Manual to assist in understanding and documenting compliance with each section's requirements.
To demonstrate compliance with the Standard’s requirements for this section, projects must demonstrate compliance with the mandatory measures.
The Mandatory Provisions form must be completed with ALL methods of compliance.
Header Information
Project Name: Enter the name of the project. This should agree with the name that is used on the plans and specifications or the common name used to refer to the project.
Project Address: Enter the street address of the project, for instance “949 Main Street, Irvine, CA 92618.”
Date: Enter the date when the compliance documentation was completed.
Designer of Record/Telephone: Enter the name and the telephone number of the designer of record.
Contact Person/Telephone: Enter the name and telephone number of the person who should be contacted if there are questions about the compliance documentation.
City: The city where the project is located.
Instructions
For each item in the compliance forms, there is the option to indicate that 1) the project complies with the requirement or 2) the requirement is not applicable to the project. Select the appropriate check box.
If a requirement's exception(s) apply to the project, check the appropriate box.
For every item checked "complies," the documentation author should fill in the Document Reference field by citing the plans (drawing number), specifications (specifications section number), or attached calculations that document the requirement.

## Mandatory
Construction and Plans for Operation Compliance Documentation – Mandatory
Project Name
Project Address: |  |  | Date:
Designer of Record: |  |  | Telephone:
Contact Person: |  |  | Telephone:
City:
Mandatory Provisions
Complies | Not applicable | Requirement | Document Reference
§10.3.1: Construction
q | q | §10.3.1: Functional and performance testing (FPT) has been performed on all buildings using generally accepted engineering standards and handbooks acceptable to the AHJ.
q | q | §10.3.1.1: An FPT process has been incorporated into the design and construction of the building project that verifies systems perform in accordance with construction documents.
q | q | §10.3.1.1.1a: Mechanical systems (heating, ventilating, air conditioning, IAQ, and refrigeration systems, mechanical and/or passive) meeting the size thresholds in this section have undergone an FPT process, along with their associated controls.
q | q | §10.3.1.1.1b: Lighting systems over 5kW in total capacity (including automatic daylighting controls, manual daylighting controls, occupancy sensing devices, and automatic shut-off controls) have undergone an FPT process.
q | q | §10.3.1.1.1c: Domestic water-heating systems rated at over 50,000 Btu/h (15,000 W) have undergone an FPT process.
q | q | §10.3.1.1.1d: Water pumping and mixing systems over 5 hp (4 kW) have undergone an FPT process.
q | q | §10.3.1.1.1e: Irrigation systems that use more than 1000 gal (4000 L) per day have undergone an FPT process.
q | q | §10.3.1.2a: Prior to building permit, the project has designated an independent and qualified FPT representative to lead, review, and oversee completion of system testing activities.
q | q | §10.3.1.2b: Prior to building permit, the FPT representative reviewed construction documents to verify that relevant sensor locations, devices, and control sequences are properly accounted for.
q | q | §10.3.1.3a: Prior to building occupancy, the FPT representative has verified that systems are properly installed and started up.
q | q | §10.3.1.3b: Prior to building occupancy, FPT has been performed. For each system test, there is a complete test form and the signature and license number, as appropriate, of the party who performed the test. Where necessary, seasonally dependent testing has been commissioned at the earliest operation time, postoccupancy.
q | q | §10.3.1.3c: Prior to building occupancy, a systems manual has been prepared that includes O&M documentation and full warranty information, and provides operating staff the information needed to understand and optimally operate building systems. This documentation has been delivered to the building owner and facility manager.
q | q | §10.3.1.4: The owner has retained completed FPT activity forms and documentation.
q | q | §10.3.2: For buildings that exceed 10,000 ft2 (1,000 m2) of gross floor area, commissioning has been performed following ANSI/ASHRAE/IES Standard 202 and/or using generally accepted engineering standards and handbooks acceptable to the AHJ.
q | q | §10.3.2: A Cx process has been incorporated into the pre-design, design, construction, and first year occupancy of the building project that verifies that the delivered building and its components, assemblies, and systems comply with the documented BOD and OPR.
q | q | §10.3.2.1 A commissioning process has be included in the design and construction of the building project for systems and associated controls in the building per section 10.3.2.1.
q | q | §10.3.2.2: Prior to building permit, the project has designated a qualified and independent commissioning provider to lead, review, and oversee completion of the Cx process. The Cx team shall include a FPT provider who may also be the Cx provider.
q | q | §10.3.2.3a: Prior to building occupancy, the Cx provider has verified the installation and performance of the systems to be commissioned, and completed the construction reporting including of test results.
q | q | q Exception §10.3.2.3a: Systems whose operation is seasonally dependent and therefore cannot be fully commissioned at the time of occupancy. These systems shall be commissioned at the earliest time after occupancy when their operation may be fully demonstrated, as determined by the Cx provider.
q | q | §10.3.2.3b: Prior to building occupancy, the preliminary commissioning report has been completed and submitted to the owner.
q | q | §10.3.2.3c: Prior to building occupancy, a system manual has been prepared and provided to the owner that includes O&M documentation and full warranty information, and that provides operating staff the information needed to understand and operate the commissioned systems as designed.
q | q | §10.3.2.4: The Cx plan contains postoccupancy Cx requirments and was developed by the Cx provider in accordance with ANSI/ASHRAE/IES Standard 202 for all systems commissioned and/or tested.
q | q | §10.3.2.5.1: The Cx provider has prepared a Cx plan in accordance with ASHRAE Standard 202.
q | q | §10.3.2.5.2: The Cx provider provided the owner and design teams a Cx design review report that complied with Standard 202 and detailed compliance with the OPR.
q | q | §10.3.2.5.3a: A Preliminary Cx Report was provided that included performance of commissioned equipment, systems, and assemblies.
q | q | §10.3.2.5.3b: A Preliminary Cx Report was provided that included issue and resolution logs, including deficiencies found during testing and commissioning that have not been corrected at the time of report preparation.
q | q | §10.3.2.5.3c: A Preliminary Cx Report was provided that included deferred tests that could not be performed at the time of report preparation.
q | q | §10.3.2.5.3d: A Preliminary Cx Report was provided that documented the training of operating personnel and building occupants on commissioned systems and a plan for the completion of any deferred trainings that were unable to be fully commissioned at the time of report preparation.
q | q | §10.3.2.5.3e: A Preliminary Cx Report was provided that included a plan for the completion of commissioning and any deferred tests.
q | q | §10.3.2.5.4: The Cx provider has given the owner a complete systems manual, all record documents, and a complete final Cx report in accordance with ASHRAE Standard 202.
q | q | §10.3.2.5.5: Owner has retained the System Manual and Final Cx Report.
q | q | §10.4.1: An ESC plan for all construction activities has been developed and implemented.
q | q | §10.4.1: The ESC plan conforms to the erosion and sedimentation control requirements of the most current version of the USEPA NPDES General Permit for Stormwater Discharges from Construction Activities or local erosion and sedimentation control standards and codes, whichever is more stringent and regardless of size of project.
q | q | §10.4.2: An IAQ construction management plan has been developed and implemented.
q | q | §10.4.2a: Air conveyance materials have been stored and covered so that they remain clean.
q | q | §10.4.2a: All filters and controls were in place and functioning when HVAC systems were operated during building flush-out or baseline IAQ monitoring.
q | q | §10.4.2a: Except for system startup, testing, balancing, and commissioning, permanent HVAC systems have not been used during construction.
q | q | §10.4.2b: Materials stored on the site or materials installed that are absorbent were protected from moisture damage.
q | q | §10.4.2c: Building construction materials that showed visual evidence of biological growth due to the presence of moisture have not been installed on the building project.
q | q | §10.4.3: Construction-related vehicles do not idle on the construction site for more than 5 minutes in any 60-minute period, except where necessary to perform their construction-related function.
q | q | §10.4.3: Signage is posted at vehicle entrances to the building project providing notice of the requirement in Section 10.3.1.6.
q | q | §10.4.4: [JO] The construction documents identify operable windows, doors, and air intake opening that serve occupied spaces, including those not associated with the building project, that are in the area of construction activity or within 35 ft (11 m) of the limits of construction activity (management of affected building(s) not under the building project manager has been notified in writing of planned construction activity and possible entry of contaminates into their building(s)).
q | q | §10.4.4: [JO] During construction, building penetrations and openings that serve occupied spaces that are in the area of construction activity or within 35ft (11m) of the limits of construction activity were closed or otherwise made to limit contaminant entry.
q | q | §10.4.5.1: Specific area(s) on the construction site are designated for collection of recyclable and reusable materials or off-site storage and sorting of materials has been permitted.
q | q | §10.4.5.2: Prior to issuance of the final certificate of occupancy, a final construction waste management report documenting compliance with Section 9.3.1 have been submitted to the owner and AHJ.
q | q | §10.5.1 Interior background sound levels have been tested. Not less than 10% of the rooms of each type have been tested and performance of spaces does not exceed the values specified in Table 8.3.3.2 by greater than 5 dBA or 5 dBC.
q | q | §10.5.2 Interior sound transmission levels have been tested per ASTM E336 and ASTM E1007. Not less than 10% of partitions between rooms have been tested and the performance meets section 8.3.3.
q | q | §10.5.3 Property line sound levels have been tested per ANSI/ASA SI.13. Testing results shall comply with the property line noise levels in section 8.3.3. and Table 8.3.3.5.2.
q | q | §10.6 Building envelope air-tightness has been performed in accordance with section 10.6. Testing has followed section 10.6a and/or verification has followed section 10.6b.
q | q | §10.7: [JO] After construction ends, prior to occupancy and with all interior finishes installed, one of the following has been performed: a building flush-out as described under Section 10.7.1, or baseline IAQ monitoring as described under Section 10.7.2.
q | q | §10.8: The building has been tested for soil-gas postconstruction in accordance with ANSI/AARST MALB. As necessary, mitigation has been conducted in accordance with ANSI/AARST RMS-LB and retested so that radon concentration is below 2.7 pCi/L (100Bq/m3).
§10.9: Plans for High-Performance Building Operation
q | q | §10.9: A Master Building Plan for Operation has been developed that meets the requirements specified in Sections 10.9.1 through 10.9.8.
q | q | §10.9.1: Site Sustainability. A site sustainability plan for operation is included that has maintenance procedures needed to maintain healthy vegetation growth, procedures for replacing any vegetation, roof system maintenance procedures, and roof plantings maintenance and replacement.
q | q | §10.9.2: Water Use Efficiency. The plan for operation specifies verification activities for building projects to track and assess building water consumption, including how to collect and store M&V data, and specify the procedures for tracking and assessing water use.
q | q | §10.9.2.1: The plan includes instructions on how to collect building project water use data for water sources and subsystems measured in section 6.3.5. The documentation of M&V for the building's water use are intended to be retained by the owner for a minimum of three years.
q | q | §10.9.2.2: The plan includes instructions on how to enter building operating characteristics and water use data into the ENERGY STAR Portfolio Manager program. The plan describes how to assess water use performance and efficiency.
q | q | §10.9.3: Energy Efficiency. The plan for operation specifies verification activities for building projects to track and assess building energy performance, including how to collect and store M&V data (per section 7.3.3) and specifies the procedures for tracking and assessing energy use and performance
q | q | §10.9.3.1: The plan includes instructions on how to measure and collect energy use data for devices and equipment specified in section 7.3.3.
q | q | §10.9.3.2: The plan includes instructions on how to track and assess energy consumption, produce energy use reports, benchmark with ENERGY STAR Portfolio Manager program, and track and assess energy performance per section 10.9.3.2.
q | q | §10.9.4.1a: Outdoor air delivery monitors required by Section 8.3.1.2 that include notification of fault conditions or indicate when a damper is out of position have a procedure for responding to notifications.
q | q | §10.9.4.1b: Outdoor air delivery monitors required by Section 8.3.1.2 are visually inspected at least once each quarter and cleaned or repaired as necessary and calibrated at the manufacture's recommended interval or not less than once per year, whichever is more frequent.
q | q | §10.9.4.1c: Systems with a damper indicator and with less than 2000 cfm (1000 L/s) of supply air, the system components controlling the minimum outdoor airflow are visually inspected every two years and the record of inspection is maintained on-site (electronically or in written form).
q | q | §10.9.4.2: Ventilation systems have schedules that ensure operation during times when spaces are expected to be operated.
q | q | §10.9.4.3: Outdoor airflow is documented such that each air system requiring direct airflow measurement is listed, monitoring procedures and frequencies for sending devices are provided, and calibration check procedures are included with project record documents.
q | q | §10.9.4.4: The plan for operations includes procedures for maintaining and monitoring IAQ after occupancy, including filtration system operation, air cleaning equipment, biennial monitoring of IAQ via testing or monitoring, and radon inspection and mitigation where applicable.
q | q | §10.9.4.5: Ozone air cleaning devices are planned to operate whenever outdoor ozone concentrations are forecast to exceed applicable regulatory limits.
q | q | §10.9.5: A green cleaning plan has been developed that follows Green Seal Standard GS-42.
q | q | §10.9.6: A plan for regular humidity sensor monitoring has been included. The plan includes annual procedures for monitoring and cleaning/repairing and recalibrating sensors as appropriate.
q | q | §10.9.7: The plan for operation includes instructions for implementing an indoor environmental quality survey of building occupants within a period of 6 to 18 months after occupancy. The survey design follows ASHRAE Standard 55 (relevant sections) and includes instructions on satisfaction results and corrections, benchmarking, and reporting.
q | q | §10.9.8: The plan for operation includes include procedures for tracking the quantity and vintage of RECs that are required to be retained and retired in compliance with Sections 701.3.2 (7.3.2) and 701.4.1.1 (7.4.1.1).
q | q | §10.9.9: Where renewable energy is allocated to multiple buildings in compliance with Section 7.4.1.3(g), the plan indicates how renewable energy produced from on-site or off-site systems that is not allocated before issuance of the certificate of occupancy will be allocated to new or existing buildings included in the building project. The plan indicates who will be responsible for retaining the documentation and where it will be stored.
q | q | §10.9.10: A Maintenance Plan has been be developed for mechanical, electrical, plumbing, and fire protection systems.
q | q | §10.9.10a: The Maintenance Plan is in accordance with ANSI/ASHRAE/ACCA Standard 180 for HVAC systems, in buildings that meet the standard's definition of commercial buildings in ANSI/ASHRAE/ACCA Standard 180.
q | q | §10.9.10b: The Maintenance Plan addresses all elements of Section 4 of ANSI/ASHRAE/ACCA Standard 180 and develops required inspection and maintenance tasks for electrical and plumbing systems similar to Section 5, in buildings that meet the standard's definition of commercial buildings.
q | q | §10.9.10c: Outdoor air delivery monitors required by Section 8.3.1.2 are visually inspected at least once each quarter and cleaned or repaired as necessary and calibrated at the manufacture's recommended interval or not less than once per year, whichever is more frequent.
q | q | §10.9.10d: Systems with a damper indicator and with less than 2000 cfm (1000 L/s) of supply air, the system components controlling the minimum outdoor airflow are visually inspected every two years and the record of inspection is maintained on-site (electronically or in written form).
q | q | §10.9.10e.: Documentation of the Maintenance Plan has been maintained on the building site at all times in: 1. Electronic format for storage on the building Energy Management System (EMS), Building Management System (BMS), computerized maintenance management system (CMMS), or other computer storage means, or 2. Manuals specifically developed and maintained to document completed maintenance activities.
q | q | §10.10: [JO] A Service Life Plan consistent with the OPR has been developed to estimate to what extent structural, building envelope (not mechanical and electrical), and hardscape materials will need to be repaired or replaced during the service life of the building.
q | q | §10.10: [JO] Documentation in the Service Life Plan includes the building project's designed service life and the basis on which that service life was determined, along with the following for each assembly or component: a. Building assembly description b. Materials or products c. Design or estimated service life, in years d. Maintenance frequency e. Maintenance access for components with an estimated service life less than the service life of the building
q | q | §10.10: [JO] The Service Life Plan was provided at the completion of design development to the owner.
q | q | §10.11: A transportation management plan has been developed which includes: a. Preferred parking for carpools and vanpools with parking facilities b. A plan for bicycle transportation
q | q | §10.11: The owner has retained a copy of the transportation management plan.
q | q | §10.11.2: [JO] For all the employees in owner-occupied buildings, or for the employees in the owner-occupied portions of a building, the building has offered at least one of the following primary benefits: a. Incentives to commute using mass transit, vanpool, carpool, or non-motorized forms of transportation b. A telework or flexible work schedule program that reduces by at least 5% the number of commuting trips by the owner’s employees c. A ride sharing or carpool matching program, either in-house or through an outside organization
q | q | q Exception §10.11.2: [JO] Multi-family residential building projects.
q | q | §10.11.2: [JO] The owner has provided all of the following to the owner’s employees: a. Access to an emergency ride home, either provided in-house or by an outside organization b. A central point of contact in charge of commuter benefits c. Maintenance of commuter benefits in a centralized location d. Active promotion of commuter benefits
q | q | §10.11.3: [JO] The building owner has provided a copy of the Transportation Management Plan to tenants within the building.
q | q | §10.11.3: [JO] The building owner did not include parking fees in lease rates or identify the value of parking in the lease.
The proposed and baseline buildings comply with the mandatory requirements of ANSI/ASHRAE/USGBC/IES Standard 189.1-2017 / 2018-IgCC. Individual certifying authenticity of the data provided in this analysis:
Signature: Date:
Printed Name: License/Registration #:
Company Name: