## Sheet1
Proposal number | Code Change # | Time | Postion - Approval (A), No position (NP), Disapproval(D) | Testifyer | Section | Topic | Notes
HC5 | EB073-22 | 3/28 PM | A | Wayne, Bill | IEBC: 503.16 (New), 902.3 (New) | CHC Ambulatory care Level 3
HC1 | EB032-22 | 3/28 AM | A | Wayne, Bill | 308.1 | IEBC BCAC 30 Carbon monoxide detectors | Joint with FCAC and BCAC
HC2 | EB116-22 | 3/28 PM-3/29 AM | A | Wayne, Bill | New IEBC appendix | BCAC IEBC 28 Appendix for emergency operations | Joint with FCAC and BCAC
HC8 | EB072-22 | 3/28 PM | A | Wayne, Bill | IEBC: 503.16 (New), 503.16.1 (New), 902.2 (New), 902.2.1 (New) | CHC upgrade/declare a condition for existing I-1 occupancies
HC6 | EB056-22 | 3/28 PM | A | Wayne, Bill | IEBC: 502.5 (New), 1101.4 (New) | CHC Addition for Group I-1
HC7 | EB095-22 | 3/28 PM-3/29 AM | A | Wayne, Bill | IEBC: 1002.3 | CHC COO for Group I-1
HC4 | EB098-22 | 3/28 PM-3/29 AM | A | Wayne, Bill | 1011.5.1 | CHC occupied roof (guards) | concern for fire service access - fire department will be aware because of regular visits for licensure; fire and life safety planning is a large part of this facility; MOE will require stair access to the roof with stairways; COO for alteration would also require extensive review
HC3 | EB071-22 | 3/28 PM | A | Wayne, Bill | IEBC: SECTION 202 (New), 503.15, 804.11 | CHC Ambulatory care definitions
| G002-22 | 4/3 PM | D | Jonathan | Definition of life safety components |  | does not add any clarity
| S062-22 | 4/4 PM | NP |  | Definition of wind borne debris, 1609 | wind load changes - see definition for Healthcare | no change in defintion
| S074-22 | 4/4 PM | D | Jonathan | Table 1604.5 | risk category - Group I-2 | increase in risk category - change in first sentence puts this on occupants other than facility being operational; language is too subjective; some nursing homes jumping from Category 2 to 4; these facilites have emegency plans - not always continuous occupancy; is loss of water or power for a couple of hours a substantial hazard?
| S075-22 | 4/4 PM | D | Jonathan | Table 1604.5 | descriptor for Group I-2 in category 4 | change in first sentence puts this on occupants other than facility being operational; language is too subjective
| S076-22 | 4/4 PM | D | Jonathan | Table 1604.5 | descriptor for Group I-2 in category 4 | change in first sentence puts this on occupants other than facility being operational; language is too subjective
| S077-22 | 4/4 PM | D | Jonathan | Table 1604.5 | risk category - Group I-1 | increase in risk category - same as S74-22; why 1/2 of the occupants? Is that mixed use?
| S116-22 | 4/5 PM-4/6 AM | NP
| EB023-22 | 3/28 AM | NP |  | 306.6 | clarification of Type B units – altered or added | improvement to clarify if an area is changed to sleeping units vs. addition
| S009-22 | 4/3 PM | NP |  | IBC: SECTION 202, [BS] 1404.16, [BS] 1404.18, 1504.6, 1504.9; IBC: TABLE 1504.9; IBC: 1507.1.1, TABLE 1507.1.1(1), TABLE 1507.1.1(2), TABLE 1507.1.1(3), 1507.16.8, 1602.1, 1603.1, 1603.1.4, TABLE 1604.3, 1609.1.1, TABLE 1609.2, 1609.2.2, 1609.3, 1609.3.1, TABLE 1609.3.1, 1705.12, 2304.6.1, TABLE 2304.10.2, TABLE 2308.7.5, 2404.1, 2404.2, 2404.3.1, 2404.3.3, 2404.3.5, 2405.5.2 |  | wind-borne debris regions; prefer S62
| S062-22 | 4/4 PM | NP |  | IBC: CHAPTER 2, SECTION 202, SECTION 202 (New), CHAPTER 15, SECTION 1504, TABLE 1504.2, 1504.6, CHAPTER 16, SECTION 1602, 1602.1, SECTION 1609, 1609.1.1, 1609.3, FIGURE 1609.3(1), FIGURE 1609.3(2), FIGURE 1609.3(3), FIGURE 1609.3(4), FIGURE 1609.3(5), FIGURE 1609.3(6), FIGURE 1609.3(7), FIGURE 1609.3(8), FIGURE 1609.3(9), FIGURE 1609.3(10), FIGURE 1609.3(11), FIGURE 1609.3(12), 1609.3.1, TABLE 1609.3.1 |  | wind-borne debris regions
| EB043-22 | 3/28 PM | D | Bill Koffel, Wayne | IEBC: SECTION 406, 406.1, 406.1.1 (New), 406.1.1, 406.1.2, 406.1.3, 406.1.4, 406.1.5 | Modification to 406.1.2 - Portions of elecrical systems and equipement being repair or reconditioned in Group I-2… John will work on modification, but back in front of BCAC. | Reconditioned Electrical Equipment – although this might be considered out of our scope since they are not modifying the Health Care Facilities section – it could still impact us though since some AHJ’s could decide the NEC would take precedence. Will need to look at this one carefully. Would NFPA 70 prohibit reconditioned equipment? NFPA 99 allows this for medical equipment. This is also an issue with Group I-1. Would this be fixed by the 2023 edition of NFPA 70.
| EB087-22 | 3/28 PM | NP |  | IEBC: 804.11 (New), 804.12 (New), 804.10, 804.10.1, 804.10.2, 804.12, 804.12.1, 804.12.2, 804.11 |  | may not be an issue since the Group I-1, I-2 and I-3 occupancies section is not being modified just renumbered. Still need to take a close look at the added language for stairways and handrails.
| EB010-22 | 4/2 PM | D | Jonathan, Wayne | IEBC: 302.6 (New), 302.6.1 (New), 302.6.2 (New) |  | More of Mr. Bonowitz’s Risk Category changes – concern is with the Current Risk Category proposal. How do you change part of an existing building?
| EB101-22 | 3/28 PM-3/29 AM | D | Bill Koffel, Wayne | IEBC: 1011.8.2 | testify if needed | Change of supply source allowance for limited area sprinkler systems; issue for doctor's offices
| EB065-22 | 4/3 AM | D | Jonathan, Wayne | IEBC: [BS] 503.5, [BS] 906.3 |  | requiring supports and attachments for non-structural components serving any portion of the building in Risk Category IV to comply with Section 1613 which requires “Every structure, and portion thereof, including nonstructural components that are permanently attached to structures and their supports and attachments…”; this is asking for more than IBC requirements; could be read to apply to the entire system 'serving' the space
| EB066-22 | 4/3 AM | D | Jonathan, Wayne | IEBC: [BS] 503.11, [BS] 906.2 |  | similar to above but for Seismic Design Cat D or E
| EB075-22 | 4/3 AM | D | Jonathan, Wayne | IEBC: 506.5.3, [BS] 1006.3 |  | similar to EB65 & EB66
| ADM003-22 Part 1 and 2 | PART I: 3/27 PM PART II: 3/29 AM | NP/D | Jeff, Bill, Wayne | IEBC: [A] 101.2; IRC: R101.2 | monitor | clarification of IRC scope which could effect small group homes and day care
| ADM004-22 Part 1 and 2 | PART I: 3/27 PM PART II: 3/29 AM | NP/D | Jeff, Bill, Wayne | IEBC: [A] 101.2; IRC: R101.2 | monitor | clarification of IRC scope which could effect small group homes and day care
| RB004-22 | 3/29 AM | NP |  | IRC: R101.2 | monitor | clarification of IRC scope which could effect small group homes and day care
| RB005-22 | 3/29 AM | D | Bill, Wayne | IRC: R101.2 | BCAC will be speaking against; monitor | clarification of IRC scope which could effect small group homes and day care
| EB67-22 | 4/3 AM | NP |  | IEBC 503.12, 706.3.2, C201.1 |  | Effects Group I-1 and R-4
| ADM47-22 | 3/28 PM | NP |  |  | monitor | Not applicable to Group I - why Group I-1 and I-4
| EB64-22 | 4/3 AM | D | Jonathan, Wayne |  |  | what is the date - permit, COO, alteration date?