ICC CODE TECHNOLOGY COMMITTEE

BALANCED FIRE PROTECTION – ROOF VENTS

ROOF VENT STUDY GROUP

2009/2010 DRAFT PROPOSALS

(4/1/09)

The following are proposed changes to the IBC and IFC based on the CTC November/2008 meeting where the direction was given by the CTC to remove all smoke and heat vent requirements from the code for buildings that are sprinklered and to reference NFPA 204 for smoke and heat vent operational requirements for unsprinklered buildings. The SG further reviewed the provisions in Section 910.4 for smoke exhaust in sprinklered buildings and proposes the revisions noted and the provisions in the IFC for high piled storage as they relate to protection requirements.

IBC/IFC SECTION 910

SMOKE AND HEAT VENTS VENTING

[F] 910.1 General. Where required by this code or otherwise installed, smoke and heat vents, or mechanical smoke exhaust systems, and draft curtains shall conform to the requirements of this section. The provisions of Section 910.2 and 910.3 do not apply to buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. The provisions of Section 910.4 apply to buildings equipped throughout with an automatic sprinkler system.

Exceptions:

1. Frozen food warehouses used solely for storage of Class I and II commodities where protected by an approved automatic sprinkler system.

2. Where areas of buildings are equipped with early suppression fast-response (ESFR) sprinklers, automatic smoke and heat vents shall not be required within these areas.

[F] 910.2 Where required. Smoke and heat vents shall be installed in the roofs of one-story buildings or portions thereof which are not protected by an automatic sprinkler system occupied for the uses set forth in Sections 910.2.1 through 910.2.3.  containing high-piled combustible stock or rack storage in any occupancy group in accordance with Section 413 and the International Fire Code.

[F] 910.2.1 Group F-1 or S-1. Buildings and portions thereof used as a Group F-1 or S-1 occupancy having more than 50,000 square feet (4645 m2) in undivided area.

Exception: Group S-1 aircraft repair hangars.

[F] 910.2.2 High-piled combustible storage. Buildings and portions thereof containing high-piled combustible stock or rack storage in any occupancy group in accordance with Section 413 and the International Fire Code.

[F] 910.2.3 Exit access travel distance increase. [Deleted in 09: E114-07/08]

[F] 910.3 Design and installation. The design and installation of smoke and heat vents and draft curtains in buildings which are not protected by an automatic sprinkler system shall be as specified in Sections 910.3.1 through 910.3.5.2 and Table 910.3. in accordance with NFPA 204

Sections noted for deletion in 910.3 are based on the provisions being included in NFPA 204.

Delete Table 910.3 in its entirety w/o substitution

| [F] TABLE 910.3 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| REQUIREMENTS FOR DRAFT CURTAINS AND SMOKE AND HEAT VENTSa |  |  |  |  |  |  |
|  |  |  |  |  |  | MAXIMUM |
|  |  |  |  |  |  | DISTANCE FROM |
|  |  |  | MAXIMUM AREA |  | MAXIMUM | VENTS TO WALL |
| OCCUPANCY GROUP AND | DESIGNATED | MINIMUM DRAFT | FORMED BY DRAFT | VENT-AREA- | SPACING OF | OR DRAFT |
| COMMODITY | STORAGE HEIGHT | CURTAIN DEPTH | CURTAINS | TO-FLOOR-AREA | VENT CENTERS | CURTAINb |
| CLASSIFICATION | (feet) | (feet) | (square feet) | RATIOc | (feet) | (feet) |
| Group F-1 and S-1 | — | 0.2 × Hd but ≥ 4 | 50,000 | 1:100 | 120 | 60 |
| High-piled Storage | ≤ 20 | 6 | 10,000 | 1:100 | 100 | 60 |
| (see Section 910.2.2) |  |  |  |  |  |  |
| I-IV (Option 1) | > 20 ≤ 40 | 6 | 8,000 | 1:75 | 100 | 55 |
| High-piled Storage | ≤ 20 | 4 | 3,000 | 1:75 | 100 | 55 |
| (see Section 910.2.2) |  |  |  |  |  |  |
| I-IV (Option 2) | > 20 ≤ 40 | 4 | 3,000 | 1:50 | 100 | 50 |
| High-piled Storage | ≤ 20 | 6 | 6,000 | 1:50 | 100 | 50 |
| (see Section 910.2.2) High hazard (Option 1) | > 20 ≤ 30 | 6 | 6,000 | 1:40 | 90 | 45 |
| High-piled Storage | ≤ 20 | 4 | 4,000 | 1:50 | 100 | 50 |
| (see Section 910.2.2) High hazard (Option 2) | > 20 ≤ 30 | 4 | 2,000 | 1:30 | 75 | 40 |
| For SI: 1 foot = 304.8 mm, 1 square foot = 0.0929 m2 . |  |  |  |  |  |  |
| a. Additional requirements for rack storage heights in excess of those indicated shall be in accordance with Chapter 23. For solid-piled storage heights in excess of those indicated, an approved engineered design shall be used. |  |  |  |  |  |  |
| b. Vents adjacent to walls or draft curtains shall be located within a horizontal distance not greater than the maximum distance specified in this column as measured perpendicular to the wall or draft curtain that forms the perimeter of the draft curtained area. |  |  |  |  |  |  |
| c. Where draft curtains are not required, the vent area to floor area ratio shall be calculated based on a minimum draft curtain depth of 6 feet (Option 1). |  |  |  |  |  |  |
| d. “H” is the height of the vent, in feet, above the floor. |  |  |  |  |  |  |

[F] 910.3.1 Design. Smoke and heat vents shall be listed and labeled to indicate compliance with UL 793 or  FM 4430..

[F] 910.3.2 Vent operation. Smoke and heat vents shall be capable of being operated by approved automatic and manual means. Automatic operation of smoke and heat vents shall conform to the provisions of Sections 910.3.2.1 through 910.3.2.3.

[F] 910.3.2.1 Gravity-operated drop-out vents. Automatic smoke and heat vents containing heat-sensitive glazing designed to shrink and drop out of the vent opening when exposed to fire shall fully open within 5 minutes after the vent cavity is exposed to a simulated fire, represented by a time-temperature gradient that reaches an air temperature of 500°F (260°C) within 5 minutes.

[F] 910.3.2.2 Sprinklered buildings. Where installed in buildings provided with an approved automatic sprinkler system, smoke and heat vents shall be designed to operate automatically.

[F] 910.3.2.3 Nonsprinklered buildings. Where installed in buildings not provided with an approved

automatic sprinkler system, smoke and heat vents shall operate automatically by actuation of a heat-responsive device rated at between 100°F (38°C) and 220°F (104°C) above ambient.

Exception: Gravity-operated drop-out vents complying with Section 910.3.2.1

[F] 910.3.3 Vent dimensions. The effective venting area shall not be less than 16 square feet (1.5 m2) with no dimension less than 4 feet (1219 mm), excluding ribs or gutters having a total width not exceeding 6 inches (152 mm).

[F] 910.3.4 Vent locations. Smoke and heat vents shall be located 20 feet (6096 mm) or more from adjacent lot lines and fire walls and 10 feet (3048 mm) or more from fire barriers. Vents shall be uniformly located within the roof in the areas of the building where the vents are required to be installed by Section 910.2 with consideration given to roof pitch, draft curtain location, sprinkler location and structural members.

[F] 910.3.5 Draft curtains. Where required by Table 910.3 by NFPA 204, draft curtains shall be installed on the underside of the roof in accordance with this section.

Exception: Where areas of buildings are equipped with ESFR sprinklers, draft curtains shall not be provided within these areas. Draft curtains shall only be provided at the separation between the ESFR sprinklers and the non ESFR sprinklers.

[F] 910.3.5.1 Construction. Draft curtains shall be constructed of sheet metal, lath and plaster, gypsum board or other approved materials which provide equivalent performance to resist the passage of smoke. Joints and connections shall be smoke tight.

[F] 910.3.5.2 Location and depth. The location and minimum depth of draft curtains shall be in accordance with Table 910.3.

SECTION 910.4 NOTE – REVISE AS NOTED. CHANGES ORGANIZED BASED ON CURRENT 2009 TEXT IN ORDER TO COMPARE PROPOSAL TO CURRENT, PROPOSAL SECTION HEIRARCHY TO BE DETERMINED

[F] 910.4 Mechanical smoke exhaust. Where approved by the fire code official, engineered mechanical smoke exhaust shall be an acceptable alternate to smoke and heat vents.

[F] 910.4. Mechanical Smoke Removal System. A mechanical smoke removal system

shall be provided in buildings or portions thereof which are protected by a sprinkler system.

Exception: Buildings or portions thereof which are protected by ESFR sprinklers.

[F] 910.4.1 Location. Exhaust fans shall be uniformly spaced within each draft-curtained area and the maximum distance between fans shall not be greater than 100 feet (30 480 mm).

[F] 910.4.x.x Exhaust Fan Spacing. The spacing between exhaust fans shall not exceed 100 feet.

[F] 910.4.2 Size. Fans shall have a maximum individual capacity of 30,000 cfm (14.2 m3/s). The aggregate capacity of smoke exhaust fans shall be determined by the equation:

C=A× 300 (Equation 9-10)

where:

C = Capacity of mechanical ventilation required, in cubic feet per minute (m3/s).

A = Area of roof vents provided in square feet (m2) in accordance with Table 910.3.

[F] 910.x.x System Design Criteria. The mechanical smoke removal system shall be sized to exhaust the building at a minimum rate of 2 air changes per hour based upon the volume of the building or portion thereof without contents. The capacity of each exhaust fan shall not exceed 30,000 cubic feet per minute.

[F] 910.x.x Exhaust Fan Construction. Exhaust fans which are part of the smoke

removal system shall be permitted to be rated for operation at ambient temperatures only.

[F] 910.4.3 Operation. Mechanical smoke exhaust fans shall be automatically activated by the automatic sprinkler system or by heat detectors having operating characteristics equivalent to those described in Section 910.3.2. Individual manual controls of each fan unit shall also be provided.

[F] 910.x.x  Activation. The mechanical smoke removal system shall be activated by manual controls. The mechanical smoke removal system shall not be automatically activated.

[F] 910.4.x.x Manual Control Location. Manual controls shall be located so as to be accessible to the fire service from the exterior of the building and be protected against interior fire exposure by not less than 1-hour fire barriers constructed in accordance with Section 706 or horizontal assemblies constructed in accordance with Section 711, or both.

[F] 910.4.4 Wiring and control. Wiring for operation and control of smoke exhaust fans shall be connected ahead of the main disconnect and protected against exposure to temperatures in excess of 1,000̊F (538̊C) for a period of not less than 15 minutes. Controls shall be located so as to be immediately accessible to the fire service from the exterior of the building and protected against interior fire exposure by not less than 1-hour fire barriers constructed in accordance with Section 706 or horizontal assemblies constructed in accordance with Section 711, or both.

[F] 910.4.x,x Wiring and control. Wiring for operation and control of smoke removal system fans shall be connected ahead of the main disconnect and be protected by materials with a finish rating of 30 minutes.

[F] 910.4.5 Supply air. Supply air for exhaust fans shall be provided at or near the floor level and shall be sized to provide a minimum of 50 percent of required exhaust. Openings for supply air shall be uniformly distributed around the periphery of the area served.

[F] 910.4.6 Interlocks. In combination comfort air-handling/ smoke removal systems or independent comfort air-handling systems, fans shall be controlled to shut down in accordance with the approved smoke control sequence.

[F] 910.X.X Interlocks. Where building air-handling and smoke removal systems are combined or where independent building air-handling systems are provided, fans shall automatically shut down in accordance with the International Mechanical Code. The manual controls provided for the smoke removal system shall override the automatic shutdown of fans which are part of the smoke removal system.

IFC SECTION 2306

GENERAL FIRE PROTECTION AND

LIFE SAFETY FEATURES

2306.1 General. Fire protection and life safety features for high-piled storage areas shall be in accordance with Sections 2306.2 through 2306.10.

2306.2 Extent and type of protection. Where required by Table 2306.2, fire detection systems, smoke and heat removal, draft curtains and automatic sprinkler design densities shall extend the lesser of 15 feet (4572 mm) beyond the high-piled storage area or to a permanent partition. Where portions of high-piled storage areas have different fire protection requirements because of commodity, method of storage or storage height, the fire protection features required by Table 2306.2 within this area shall be based on the most restrictive design requirements.

Changes to T 2306.2 in the boxed cells: deletion of reference to footnote g, and add reference footnote d; footnote j revision on next page

| TABLE 2306.2 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| GENERAL FIRE PROTECTION AND LIFE SAFETY REQUIREMENTS |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | SOLID-PILED STORAGE, SHELF |  |  |  |
|  |  | ALL STORAGE AREAS |  |  |  |  | STORAGE AND PALLETIZED STORAGE |  |  |  |
|  | SIZE OF HIGH-PILED | (See Sec tions 2306, 2307 and 2308)b |  |  |  |  | (see Section 2307.3) |  |  |  |
|  |  | Automatic fire- | Fire |  |  |  |  | Maximum |  |  |
|  | STORAGE AREAa | extinguishing | detection | Building | Smoke and | Draft |  | permissible |  |  |
| COMMODITY | (square feet) (see Sections 2306.2 | system (see Section | system (see Section | access (see Section | heat removal (see Section | curtains (see Section | Maximum pile dimensionc | storage heightd | Maximum pile volume |  |
| CLASS | and 2306.4) | 2306.4) | 2306.5) | 2306.6) | 2306.7) | 2306.7) | (feet) | (feet) | (cubic feet) |  |
| I-IV | 0-500 | Not Requireda | Not Required | Not Requirede | Not Required | Not Required | Not Required | Not Required | Not Required |  |
|  | 501-2,500 | Not Requireda | Yesi | Not Requirede | Not Required | Not Required | 100 | 40 | 100,000 |  |
|  | 2,501-12,000 Public accessible | Yes | Not Required | Not Requirede | Not Required | Not Required | 100 | 40 | 400,000 |  |
|  | 2,501-12,000 Nonpublic accessible (Option 1) | Yes | Not Required | Not Requirede | Not Required | Not Required | 100 | 40 | 400,000 |  |
|  | 2,501-12,000 Nonpublic accessible (Option 2) | Not Requireda | Yes | Yes | Yesj | Yesj | 100 | 30f | 200,000 |  |
|  | 12,001-20,000 | Yes | Not Required | Yes | Yesj | Not Required | 100 | 40 | 400,000 |  |
|  | 20,001-500,000 | Yes | Not Required | Yes | Yesj | Not Required | 100 | 40 | 400,000 |  |
|  | Greater than 500,000g d | Yes | Not Required | Yes | Yesj | Not Required | 100 | 40 | 400,000 |  |
| High | 0-500 | Not Requireda | Not Required | Not Requirede | Not Required | Not Required | 50 | Not Required | Not Required |  |
|  | 501-2,500 Public accessible | Yes | Not Required | Not Requirede | Not Required | Not Required | 50 | 30 | 75,000 |  |
|  | 501-2,500 Nonpublic accessible (Option 1) | Yes | Not Required | Not Requirede | Not Required | Not Required | 50 | 30 | 75,000 |  |
| hazard | 501-2,500 Nonpublic accessible (Option 2) | Not Requireda | Yes | Yes | Yesj | Yesj | 50 | 20 | 50,000 |  |
|  | 2,501-300,000 | Yes | Not Required | Yes | Yesj | Not Required | 50 | 30 | 75,000 |  |
|  | 300,001-500,000g,d,h | Yes | Not Required | Yes | Yesj | Not Required | 50 | 30 | 75,000 |  |

For SI: 1 foot = 304.8 mm, 1 cubic foot = 0.02832 m3 , 1 square foot = 0.0929 m2 .

a. When automatic sprinklers are required for reasons other than those in Chapter 23, the portion of the sprinkler system protecting the high-piled storage area shall be designed and installed in accordance with Sections 2307 and 2308.

b. For aisles, see Section 2306.9.

c. Piles shall be separated by aisles complying with Section 2306.9.

d. For storage in excess of the height indicated, Class I-IV storage areas greater than 500, 000 square feet and high hazard storage areas greater than 300, 000 square feet, special fire protection an approved engineering design such as fire protection of structural elements and enhanced fire suppression shall be provided in accordance with Note g when required by the fire code official. See also Chapters 28 and 34 for special limitations for aerosols and flammable and combustible liquids, respectively.

e. Section 503 shall apply for fire apparatus access.

f. For storage exceeding 30 feet in height, Option 1 shall be used.

g. Special fire protection provisions including, but not limited to, fire protection of exposed steel columns; increased sprinkler density; additional in-rack sprinklers, without associated reductions in ceiling sprinkler density; or additional fire department hose connections shall be provided when required by the fire code official.

h. High-piled storage areas shall not exceed 500,000 square feet. A 2-hour constructed in accordance with the International Building Code shall be used to divide high-piled storage exceeding 500,000 square feet in area.

i. Not required when an automatic fire-extinguishing system is designed and installed to protect the high-piled storage area in accordance with Sections 2307 and 2308.

j. Smoke and heat removal shall not be Not required when storage areas are protected by early suppression fast response (ESFR) sprinkler systems installed in accordance with NFPA 13. Where a standard sprinkler system is installed in these locations, a mechanical smoke exhaust shall be provided in accordance with Section 910.4. See Section 2306.7.

2306.3 Separation of high-piled storage areas. High-piled storage areas shall be separated from other portions of the building where required by Sections 2306.3.1 through 2306.3.2.2.

2306.3.1 Separation from other uses. Mixed occupancies shall be separated in accordance with the International Building Code.

2306.3.2 Multiple high-piled storage areas. Multiple high-piled storage areas shall be in accordance with Section 2306.3.2.1 or 2306.3.2.2.

2306.3.2.1 Aggregate area. The aggregate of all high-piled storage areas within a building shall be used

for the application of Table 2306.2 unless such areas are separated from each other by 1-hour fire barrier walls constructed in accordance with the International Building Code. Openings in such walls shall be protected by opening protective assemblies having a 1-hour fire protection rating.

2306.3.2.2 Multiclass high-piled storage areas. High-piled storage areas classified as Class I through IV

not separated from high-piled storage areas classified as high hazard shall utilize the aggregate of all high-piled storage areas as high hazard for the purposes of the application of Table 2306.2. To be considered as separated, 1-hour fire barrier walls shall be constructed in accordance with the International Building Code. Openings in such walls shall be protected by opening protective assemblies having a 1-hour fire protection rating.

Exception: As provided for in Section 2304.2.

2306.4 Automatic sprinklers. Automatic sprinkler systems shall be provided in accordance with Sections 2307, 2308 and 2309.

Staff note: Sections 2307.2, 2308.2 and 2309.2 all defer to Table 2306.2 to determine where required.

2306.5 Fire detection. Where fire detection is required by Table 2306.2, an approved automatic fire detection system shall be installed throughout the high-piled storage area. The system shall be monitored and be in accordance with Section 907.

2306.6 Building access. Where building access is required by Table 2306.2, fire apparatus access roads in accordance with Section 503 shall be provided within 150 feet (45 720 mm) of all portions of the exterior walls of buildings used for high-piled storage.

Exception: Where fire apparatus access roads cannot be installed because of topography, railways, waterways, non-negotiable grades or other similar conditions, the fire code official is authorized to require additional fire protection.

2306.6.1 Access doors. Where building access is required by Table 2306.2, fire department access doors shall be provided in accordance with this section. Access doors shall be accessible without the use of a ladder.

2306.6.1.1 Number of doors required. A minimum of one access door shall be provided in each 100 lineal feet (30 480 mm), or fraction thereof, of the exterior walls that face required fire apparatus access roads. The required access doors shall be distributed such that the lineal distance between adjacent access doors does not exceed 100 feet (30 480 mm).

2306.6.1.2 Door size and type. Access doors shall not be less than 3 feet (914 mm) in width and 6 feet 8 inches (2032 mm) in height. Roll-up doors shall not be used unless approved.

2306.6.1.3 Locking devices. Only approved locking devices shall be used.

2306.7 Smoke and heat removal. Where smoke and heat removal in buildings not protected by an automatic sprinkler system  are required by Table 2306.2, smoke and heat vents shall be provided in accordance with Section 910. Smoke and heat removal shall not be required where storage areas are protected by early suppression fast response (ESFR) sprinkler systems installed in accordance with NFPA 13.  Where Table 2306.2 requires smoke and heat removal in a building with a standard sprinkler system, a mechanical smoke  exhaust shall be provided in accordance with Section 910.4.Where draft curtains are required by Table 2306.2, they shall be provided in accordance with Section 910.3.4.

2306.8 Fire department hose connections. Where exit passageways are required by the International Building Code for egress, a Class I standpipe system shall be provided in accordance with Section 905.

2306.9 Aisles. Aisles providing access to exits and fire department access doors shall be provided in high-piled storage areas exceeding 500 square feet (46m2), in accordance with Sections 2306.9.1 through 2306.9.3. Aisles separating storage piles or racks shall comply with NFPA 13. Aisles shall also comply

with Chapter 10.

Exception: Where aisles are precluded by rack storage systems, alternate methods of access and protection are allowed when approved.

2306.9.1 Width. Aisle width shall be in accordance with Sections 2306.9.1.1 and 2306.9.1.2.

Exceptions:

1. Aisles crossing rack structures or storage piles, which are used only for employee access, shall be a

minimum of 24 inches (610 mm) wide.

2. Aisles separating shelves classified as shelf storage shall be a minimum of 30 inches (762 mm)

wide.

2306.9.1.1 Sprinklered buildings. Aisles in sprinklered buildings shall be a minimum of 44 inches (1118 mm) wide. Aisles shall be a minimum of 96 inches (2438 mm) wide in high-piled storage areas exceeding 2,500 square feet (232 m2) in area, that are accessible to the public and designated to contain high-hazard commodities.

Exception: Aisles in high-piled storage areas exceeding 2,500 square feet (232 m2) in area, that are accessible to the public and designated to contain high-hazard commodities, are protected by a sprinkler

system designed for multiple-row racks of high-hazard commodities shall be a minimum of 44

inches (1118 mm) wide.

Aisles shall be a minimum of 96 inches (2438 mm) wide in areas accessible to the public where mechanical stocking methods are used.

2306.9.1.2 Nonsprinklered buildings. Aisles in nonsprinklered buildings shall be a minimum of 96

inches (2438 mm) wide.

2306.9.2 Clear height. The required aisle width shall extend from floor to ceiling. Rack structural supports and catwalks are allowed to cross aisles at a minimum height of 6 feet 8 inches (2032 mm) above the finished floor level, provided that such supports do not interfere with fire department hose stream trajectory.

2306.9.3 Dead ends. Dead-end aisles shall be in accordance with Chapter 10.

2306.10 Portable fire extinguishers. Portable fire extinguishers shall be provided in accordance with Section 906.