ICC CODE TECHNOLOGY COMMITTEE

BALANCED FIRE PROTECTION

VERTICAL OPENINGS STUDY GROUP

Discussion Draft (as of June 11, 2007)

(Red indicates items that require discussion or resolution)

Chapter 7 organization

Section 701 GENERAL

Section 702 DEFINITIONS

Section 703 FIRE-RESISTANCE RATINGS AND FIRE TESTS

Section 704 PRESCRIPTIVE FIRE RESISTANCE

Section 705 CALCULATED FIRE RESISTANCE

Section 706 EXTERIOR WALLS

Section 707 FIRE WALLS

Section 708 FIRE BARRIERS

Section 709 FIRE PARTITIONS

Section 710 HORIZONTAL ASSEMBLIES

Section 711 HORIZONTAL BARRIERS

Section 712 FIRE-RESISTANCE RATING OF STRUCTURAL MEMBERS

Section 713 PROTECTION OF OPENINGS

Section 714 CONCEALED SPACES

Section 715 FIRE-RESISTANCE REQUIREMENTS FOR PLASTER

Section 716 THERMAL-AND SOUND-INSULATING MATERIALS

702.1 Definitions.

OPENING. A breach in a building assembly that is necessary for utility, egress or architectural purposes.

BUILDING ASSEMBLY.  An element of building construction as indicated in Table 601.  Building assemblies are comprised of one or more construction components.

ENCLOSURE.

FIRE-RESISTANCE RATING. The period of time that a building assembly maintains the ability to confine a fire, continues to perform a given structural function, or both, as determined by the tests, or the methods based on tests, prescribed in Section 703.

HORIZONTAL ASSEMBLY.  A fire-resistance-rated floor or roof building assembly based on building type of construction requirements and which is designed to perform a given structural function.

HORIZONTAL BARRIER.  A fire-resistance-rated floor building assembly wherein openings are protected and which is designed to maintain the ability to confine a fire.

SHAFT ENCLOSURE. An enclosure for an opening that serves utility purposes such as, accommodating electrical, mechanical. plumbing equipment and elevator hoistways.

EXIT ENCLOSURE. An enclosure for an opening that serves means of egress or human movement purposes such as stairways and ramps.

ATRIUM ENCLOSURE. An enclosure for an opening that serves functional or aesthetic purposes such as atria, escalators and air transfer openings.

AIR TRANSFER OPENING. An unducted opening designed to allow the movement of environmental air between two contiguous spaces

FIRESTOP.  A material, device or construction installed to maintain the fire-resistance rating required for a building assembly.

FLAMESTOP. A material, device or construction installed to resist the free passage of flame and products of combustion in nonfire-resistance rated building elements.

JOINT.  The linear opening in or between adjacent fire-resistance rated building assemblies that is designed to allow for independent movement of the building in any plane.

DRAFTSTOP.  A material, device or construction installed to restrict the movement of air within open spaces of concealed areas of a building such as crawl spaces, floor/ceiling assemblies, roof/ceiling assemblies and attics

FIRE AREA.  The aggregate floor area enclosed and bounded by fire walls, fire barriers, exterior walls or fire-resistance-rated horizontal assemblies of a building.

FIRE COMPARTMENT.  A fire-resistance rated or nonfire-resistance rated interior envelope of building construction beyond which no atmospheric communication of fire will occur.  (In a fire event?)

OPENING PROTECTIVE ASSEMBLY.  A listed device installed in a building assembly that is designed to confine a fire or to resist the spread of fire for a prescribed period of time. Opening protective assemblies include fire door assemblies, fire window assemblies, fire dampers, ceiling dampers, smoke dampers, through-penetration fire stops and fire-resistant joint systems.

SECTION 713

PROTECTION OF OPENINGS

713.1 General.  Openings in building assemblies shall be protected in accordance with the provisions of this section.

713.1.1 Unconcealed openings.  Where required to be protected, openings that are not concealed within building construction shall be enclosed by fire-resistance rated construction or protected by an opening protective assembly.  (Through opening)

Exceptions:

1.  Openings totally within an individual dwelling unit and connecting four stories or less.

2.  Openings in Group S-2 open and enclosed parking garages that serve only the parking structure.

3.  Openings in Group A-5 occupancies which are essentially open to the outdoors.

713.1.2 Concealed openings. Openings that are concealed within building construction shall be protected in accordance with the provisions of Section 714. (Membrane or cavity opening)

Exception: Openings within enclosures constructed in accordance with the provisions of Section 713.8.

713.2 Fire compartments. Fire compartments shall include those contiguous building areas not separated by fire walls, fire barriers or horizontal barriers.  Areas so separated shall be considered separate fire compartments.  Enclosures in accordance with the provisions of Section 713.8 and exit passageways in accordance with the provisions of Section 1021 shall not be considered separate compartments; however, the protection of openings shall be required between such areas and the compartments in which they are located.  Areas isolated by fire partitions shall not be considered separate compartments; however, the protection of openings shall be required between such areas and the compartments in which they are located.

Fire compartments shall be permitted to extend vertically and include intercommunicating stories in accordance with Table 713.2.  Openings that are not concealed within building construction and serve the indicated number of adjacent stories are not required to be enclosed or protected provided such interconnected stories do not atmospherically communicate with additional stories, other fire compartments or tenant spaces. The total height of communicating stories within a given fire compartment shall not exceed 50 feet.  Stories, as used in this section, shall include basements, but not include balconies in Group A occupancies or mezzanines that comply with Section 505.

TABLE 713.2

ALLOWED NUMBER OF INTERCOMMUNICATING

STORIES WITHIN FIRE COMPARTMENTS

| Occupancy | Number of Stories | Sprinkler System | Mechanical Smoke Controla |
| --- | --- | --- | --- |
| Group A, B, E, F, M, S or U | 2 | 3b | 4c |
| Group H, I or R | 1 | 1 | 1 |

a. In other than Group H occupancies, unlimited intercommunicating stories are permitted where buildings comply with the provisions of  Section 713.8.3.6.

b. Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.

c. Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 and a mechanical smoke control system in accordance with Section 909 within the applicable fire compartment.

713.3 Floor, floor/ceiling construction.  Openings in floors or floor/ceiling construction shall be protected in accordance with the provisions of this section.  Structural members supporting floor, floor/ceiling construction that is a portion of a fire compartment shall be protected consistent with the supported construction.  Flexible ducts and air connectors shall not pass through any fire-resistance-rated assembly. Flexible air connectors shall not pass through any floor.

713.3.1 Building assemblies. Openings in nonfire-resistance rated floor/ceiling construction that is not a portion of a fire compartment envelope shall not require protection unless required by other provisions of this code.  Openings in nonfire-resistance rated floor/ceiling construction that is a portion of a fire compartment envelope shall be protected in accordance with Section 713.7 or enclosed in accordance with Sections 713.8.1 through 713.8.3.

713.3.2 Horizontal assemblies. Openings in horizontal assemblies that are not a portion of a fire compartment envelope shall not require protection other than as necessary to maintain the integrity of the assembly itself unless required by other provisions of this code.  Openings in horizontal assemblies that are a portion of a fire compartment envelope shall be protected with opening protective assemblies in accordance with Sections 713.6.1 through 713.6.6 or enclosed in accordance with Sections 713.8.1 through 713.8.3.

713.3.3 Horizontal barriers.  Openings in horizontal barriers shall be protected with opening protective assemblies in accordance with Sections 713.6.1 through 713.6.6 or enclosed in accordance with Sections 713.8.1 through 713.8.3.

713.4 Roof, roof/ceiling construction. Openings in roofs or roof/ceiling construction shall be protected in accordance with the provisions of this section.  Flexible ducts and air connectors shall not pass through any fire-resistance-rated assembly. Flexible air connectors shall not pass through any ceiling.

Skylights and other penetrations through a fire-resistance-rated roof deck or slab are permitted to be unprotected, provided that the structural integrity of the fire-resistance-rated roof construction is maintained. Unprotected skylights shall not be permitted in roof construction required to be fire-resistance rated in accordance with Section 704.10.

(Infill with requirements.)

713.5 Wall construction.  Openings in fire-resistance rated wall construction shall comply with the provisions of this section. Flexible ducts and air connectors shall not pass through any fire-resistance-rated assembly. Flexible air connectors shall not pass through any wall.

713.5.1 Exterior walls.  Openings in bearing and nonbearing exterior walls shall be protected in accordance with the provisions of Section 706.X.

713.5.2 Interior walls.  Openings in bearing and nonbearing interior walls shall be protected in accordance with the provisions of this section.

713.5.2.1 Building assemblies.  Openings in interior bearing walls required to have a fire-resistance rating by Table 601 shall not require protection other than as necessary to maintain the integrity of the assembly itself unless required by other provisions of this code.

713.5.2.2 Fire walls, fire barriers and fire partitions.  Openings in fire walls, fire barriers and fire partitions shall be protected in accordance with the provisions this section.

713.5.2.2.1 Doors.  Door openings shall be protected in accordance with the provisions of Section 713.6.1.

713.5.2.2.2 Windows. Window openings shall be protected in accordance with the provisions of Section 713.6.2.  Window openings in fire walls shall not be permitted.

Exceptions:

- Glazing tested as part of a fire-resistance-rated wall assembly in accordance with ASTM E 119 shall not be required to comply with this section.

- Glazing protected by fire door assemblies.

713.5.2.2.3 Ducts.  Duct openings shall be protected in accordance with the provisions of Sections 713.6.3, 713.6.4 and 9XXX.X.

Exceptions:

1. In other than Group H occupancies, fire dampers are not required in fire barriers where any of the following apply:

1. Where ducts are used as part of an approved smoke control system in accordance with Section 909 and where the use of a fire damper would interfere with the operation of a smoke control system.

- In ducted HVAC systems in other than Group H occupancies, where fire barriers have a required fire-resistance rating of 1 hour or less and are in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. For the purposes of this exception, a ducted HVAC system shall be a duct system for conveying supply, return or exhaust air as part of the structure’s HVAC system. Such a duct system shall be constructed of sheet steel not less than 26 gage thickness and shall be continuous from the air-handling appliance or equipment to the air outlet and inlet terminals.

2. In other than Group H occupancies, fire dampers are not required in fire partitions where any of the following apply:

1. The fire partitions are tenant separation or corridor walls in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2 and the duct is protected as a through penetration in accordance with Section 712.

2. Tenant partitions in covered mall buildings where the fire partitions are not required to extend to the underside of the floor or roof deck above by provisions elsewhere in this code.

3. The duct system is constructed of approved materials in accordance with the International Mechanical Code and the duct penetrating the fire partition complies with all of the following requirements:

3.1. The duct shall not exceed 100 square inches (0.06 m2).

3.2. The duct shall be constructed of steel a minimum of 0.0217 inch (0.55 mm) in thickness.

3.3. The duct shall not have openings that communicate the corridor with adjacent spaces or rooms.

3.4. The duct shall be installed above a ceiling.

3.5. The duct shall not terminate at a wall register in the fire-resistance-rated wall.

3.6. A minimum 12-inch-long (305 mm) by 0.060-inch-thick (1.52 mm) steel sleeve shall be centered in each duct opening. The sleeve shall be secured to both sides of the wall and all four sides of the sleeve with minimum 1½-inch by 1½-inch by 0.060-inch (38 mm by 38 mm by 1.52 mm) steel retaining angles. The retaining angles shall be secured to the sleeve and the wall with No. 10 (M5) screws. The annular space between the steel sleeve and the wall opening shall be filled with mineral wool batting on all sides.

713.5.2.2.4 Penetrations.  Through-penetrations and membrane-penetrations shall be protected in accordance with the provisions of Section 713.6.5.

713.5.2.2.5 Joints.  Joints in shall be protected in accordance with the provisions of Section 713.6.6.

713.6 Opening protective assemblies.  Opening protective assemblies required by other provisions of this code shall comply with the provisions of this section.

The required fire resistance of an opening protective assembly shall be established by any of the following methods or procedures:

1. Designs documented in approved sources.

2. Calculations performed in an approved manner.

3. Engineering analysis based on a comparison of opening protective designs having fire-protection ratings as determined by the test procedures set forth in referenced test standards.

4. Alternative protection methods as allowed by Section 104.11.

The application of any of the alternative methods listed in this section shall be based on the fire exposure and acceptance criteria specified in referenced test standards.

713.6.1 Fire door assemblies. Fire door assemblies shall comply with the provisions of this section.  Fire door assemblies shall be constructed of any material or assembly of materials that conforms to the test requirements of Section 713.6.1.1, 1-3.  Fire shutters shall comply with the provisions for fire doors.

Exceptions:

1. Labeled fire door assemblies that conform to the requirements of this section or UL10A, UL14B and UL 14C for tin-clad fire door assemblies.

2. Floor fire door assemblies in accordance with this section.

713.6.1.1 Fire protection rating. Fire door assemblies shall have the fire protection rating indicated in Table 713.6.1.

Exceptions:

1.  Corridor door assemblies in occupancies of Group I-2 shall be in accordance with Section 407.3.1.

- Unprotected openings shall be permitted for corridors in multitheater complexes where each motion picture auditorium has at least one-half of its required exit or exit access doorways opening directly to the exterior or into an exit passageway.

- Floor fire door assemblies used to protect openings in horizontal assemblies and horizontal barriers shall have a fire-resistance rating not less than the assembly being penetrated.

TABLE 713.6.1

FIRE DOOR FIRE PROTECTION RATINGS

(Contents of table to remain unchanged)

713.6.1.2 Testing.  Fire door assemblies shall be tested in accordance with NFPA 252, UL 10B or UL 10C, as specified below.

Side-hinged and pivoted swinging fire door assemblies shall be tested in accordance with NFPA 252 or UL 10C.  After 5 minutes into the NFPA 252 test, the neutral pressure level in the furnace shall be established at 40 inches (1016 mm) or less above the sill.

Other types of fire door assemblies, including swinging elevator doors, shall be tested in accordance with NFPA 252 or UL 10B.  The pressure in the furnace shall be maintained as nearly equal to the atmospheric pressure as possible. Once established, the pressure shall be maintained during the entire test period.

Fire door assemblies in exit enclosures and exit passageways shall have a maximum transmitted temperature end point of not more than 450°F (250° C) above ambient at the end of 30 minutes of standard fire test exposure.

Exception: The maximum transmitted temperature rise is not limited in buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2.

Fire door assemblies located in corridor walls or smoke-barrier walls and required to have a minimum fire protection rating of 20 minutes in accordance with Table 713.6.1 shall be tested in accordance with NFPA 252 or UL 10C without the hose stream test. Such smoke and draft control assemblies shall also be tested in accordance with UL 1784.  Louvers are prohibited.

Exceptions:

1.  View ports that require a hole not larger than 1 inch (25 mm) in diameter through the door, have at least a 0.25-inch-thick (6.4 mm) glass disc and the holder is of metal that will not melt out where subject to temperatures of 1,700°F (927°C) shall be permitted.

Floor fire door assemblies used to protect openings in fire-resistance-rated floors shall be tested in accordance with NFPA 288.

713.6.1.3 Labeling. The labels shall comply with NFPA 80 and shall be permanently affixed to the door or frame. The label shall be applied at the factory or location where fabrication and assembly are performed.  Fire door labels shall include the name of the manufacturer, the name of the third-party inspection agency, the fire protection rating and, where required for fire doors used in exit enclosures and exit passageways, the maximum transmitted temperature end point.  Fire door frames shall be labeled showing the name of the manufacturer and the name of the third-party inspection agency.

Smoke and draft control assemblies complying with UL 1784 shall be labeled and shall show the letter “S” on the fire protection rating label of the door. This marking shall indicate that the door and frame assembly are in compliance when listed or labeled gasketing is also installed.

Oversized fire door assemblies shall bear an oversized fire door label by an approved agency or shall be provided with a certificate of inspection furnished by an approved testing agency.  When a certificate of inspection is furnished by an approved testing agency, the certificate shall state that the door conforms to the requirements of design, materials and construction, but has not been subjected to the fire test.

Floor fire door assemblies shall be labeled by an approved agency. The label shall be permanently affixed and shall specify the manufacturer, the test standard and the fire-resistance rating.

713.6.1.4 Installation.  Fire door assemblies shall be installed in accordance in accordance with NFPA 80.  Smoke and draft control assemblies shall be installed in accordance with NFPA 105.

713.6.1.5 Closing. Fire door assemblies shall be self- or automatic closing in accordance with this section.

Exceptions:

1. Fire door assemblies located in common walls separating sleeping units in Group R-1 occupancies shall be permitted without self- or automatic-closing devices.

2. The elevator car doors and the associated hoistway enclosure doors at the floor level designated for recall in accordance with Section 3003.2 shall be permitted to remain open during Phase I emergency recall operation.

Unless otherwise permitted, single fire door assemblies and both leaves of pairs of side-hinged swinging fire door assemblies shall be provided with an active latch bolt that will secure the door when it is closed.

713.6.1.5.1 Smoke-activated doors.  Automatic-closing doors installed in the following locations shall be automatic closing by the actuation of smoke detectors installed in accordance with Section 907.10 or by loss of power to the smoke detector or hold-open device.  Doors that are automatic closing by smoke detection shall not have more than a 10-second delay before the door starts to close after the smoke detector is actuated:

1. Doors installed across a corridor.

2. Doors that protect openings in exits or corridors required to be of fire-resistance-rated construction.

3. Doors that protect openings in walls that are capable of resisting the passage of smoke in accordance with Section 508.2.2.1.

4. Doors installed in smoke barriers in accordance with Section 9XXX.X.

5. Doors installed in fire partitions in accordance with Section 709.6.

6. Doors installed in a fire wall in accordance with Section 707.8.

7. Doors installed in shaft enclosures in accordance with Section 713.8.1.

8. Doors installed in refuse and laundry chutes and access and termination rooms in accordance with Section 713.8.1.2.3.

9. Doors installed in the walls for compartmentation of underground buildings in accordance with Section 405.4.2.

10. Doors installed in the elevator lobby walls of underground buildings in accordance with Section 405.4.3.

11. Doors installed in smoke partitions in accordance with Section 9XXX.X.

713.6.1.5.2 Fire shutters and steel fire doors.  Vertical sliding or vertical rolling steel fire door assemblies in openings through which pedestrians travel shall be heat activated or activated by smoke detectors with alarm verification.

Where fire shutters of the rolling type are installed, such shutters shall include approved automatic-closing devices.

Where fire shutters of the swinging type are installed in exterior openings, not less than one row in every three vertical rows shall be arranged to be readily opened from the outside, and shall be identified by distinguishing marks or letters not less than 6 inches (152 mm) high. (?)

713.6.1.6 Glazing.  Fire-protection-rated glazing shall be permitted in fire door assemblies in accordance with the provisions of this section.

Fire-protection-rated glazing in fire door assemblies located in fire walls shall be prohibited except that where serving as a horizontal exit, a self-closing swinging fire door assembly shall be permitted to have a vision panel of not more than 100 square inches (0.065 m2) without a dimension exceeding 10 inches (254 mm).

Fire-protection-rated glazing shall not be installed in fire door assemblies having a 1½-hour fire protection rating intended for installation in fire barriers, unless the glazing is not more than 100 square inches (0.065 m2) in area.

Fire-protection-rated glazing in excess of 100 square inches (0.065 m2) shall be permitted in fire door assemblies in exit enclosures and exit passageways when tested in accordance with NFPA 252 as components of the door assemblies and not as glass lights, and shall have a maximum transmitted temperature rise of 450°F (250°C) in accordance with Section 713.4.4.

Exception: The maximum transmitted temperature end point is not required in buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2.

Fire-protection-rated glazing in smoke and draft control assemblies shall have a minimum fire-protection rating of 20 minutes and shall be exempt from the hose stream test. Glazing material in any other part of the door assembly, including transom lites and sidelites, shall be tested in accordance with NFPA 257 and UL 9, including the hose stream test, in accordance with Section 713.5.

713.6.1.6.1 Labeling.  Fire-protection-rated glazing in fire door assemblies shall be labeled by an approved agency.  The labels shall comply with NFPA 80 and shall be permanently affixed to the glazing.  The label shall be applied at the factory or location where fabrication and assembly are performed.  For fire-protection-rated glazing, the label shall include the name of the manufacturer, the test standard and shall bear the following four-part identification: “D – H or NH – T or NT – XXX.” “D” indicates that the glazing shall be used in fire door assemblies and that the glazing meets the fire containment requirements of the NFPA 257 and UL 9.  “H” shall indicate that the glazing meets the hose stream requirements of the test standard. “NH” shall indicate that the glazing does not meet the hose stream requirements of the test.  “T” shall indicate that the glazing meets the temperature requirements of Section 713.4.4.1.  “NT” shall indicate that the glazing does not meet the temperature requirements of Section 713.4.4.1.  The placeholder “XXX” shall specify the fire-protection-rating period, in minutes, as tested.

713.6.1.6.1 Installation.  Wired glass used in fire door assemblies shall comply with Table 713.6.2.1.  Other fire-protection-rated glazing shall comply with the size limitations of NFPA 80.

Approved fire-protection-rated glazing used in fire door assemblies in elevator and exit enclosures shall be so located as to furnish clear vision of the passageway or approach to the elevator, ramp or stairway.

Fire-protection-rated glazing installed in fire door assemblies or fire window assemblies in areas subject to human impact in hazardous locations shall comply with Chapter 24.

713.6.2 Fire window assemblies.  Fire window assemblies shall comply with the provisions of this section.

Exception: Glazing tested as part of a fire-resistance-rated wall assembly in accordance with ASTM E 119 shall not be required to comply with this section.

Fire window assemblies shall be limited to fire partitions in accordance with Section 708 and fire barriers utilized in the applications set forth in Sections 706.3.6 and 706.3.8 (?) where the fire-resistance rating does not exceed 1 hour.

The total area of windows shall not exceed 25 percent of the area of a common wall with any room. (Versus requirements at Sections 706 and 708)

Glazing installed in fire door assemblies shall comply with Section 713.6.1.6.

713.6.2.1 Fire protection rating. Fire window assemblies shall have the fire protection rating indicated in Table 713.6.2.  Metal mullions that exceed a nominal height of 12 feet (3658 mm) shall be protected with materials to afford the same fire-resistance rating as required for the wall construction in which the fire window assembly is located.

Exceptions:

1. Steel window frame assemblies of 0.125-inch (3.2 mm) minimum solid section or of not less than nominal 0.048-inch-thick (1.2 mm) formed sheet steel members fabricated by pressing, mitering, riveting, interlocking or welding and having provision for glazing with ¼-inch (6.4 mm) wired glass where securely installed in the building construction and glazed with ¼-inch (6.4 mm) labeled wired glass shall be deemed to meet the requirements for a ¾-hour fire window assembly. Wired glass panels shall conform to the size limitations set forth in Table 713.6.2.1.

2. Fire window assemblies in 0.5-hour fire-resistance-rated partitions is permitted to have a 20 minute fire protection rating.

TABLE 713.6.2

FIRE WINDOW ASSEMBLY FIRE PROTECTION RATINGS

(Contents of table to remain unchanged, except add new footnote)

Exterior wallsb

b. Openings in nonfire-resistance-rated exterior wall assemblies that require protection in accordance with Section 704.3, 704.8, 704.9 or 704.10 shall have a fire-protection rating of not less than ¾ hour.

TABLE 713.6.2.1

LIMITING SIZES OF WIRED GLASS PANELS

(Contents of table to remain unchanged)

713.6.2.2 Testing.  Fire window assemblies shall be tested in accordance with NFPA 257 and UL 9.

NFPA 257 AND UL 9 shall evaluate fire window assemblies under positive pressure. Within the first 10 minutes of a test, the pressure in the furnace shall be adjusted so at least two-thirds of the test specimen is above the neutral pressure plane, and the neutral pressure plane shall be maintained at that height for the balance of the test.

Nonsymmetrical glazing systems in fire partitions, fire barriers or in exterior walls with a fire separation distance of 5 feet (1524 mm) or less in accordance with Section 704 shall be tested with both faces exposed to the furnace, and the assigned fire protection rating shall be the shortest duration obtained from the two tests conducted in compliance with NFPA 257 AND UL 9.

713.6.2.3 Labeling.  Fire windows shall be labeled by an approved agency. The labels shall comply with NFPA 80 and shall be permanently affixed to the glazing.  The label shall be applied at the factory or location where fabrication and assembly are performed.  Fire window labels shall include the name of the manufacturer, the test standard and shall bear the following two-part identification: “OH – XXX.” “OH” indicates that the glazing meets both the fire containment and the hose-stream requirements of NFPA 257 and UL 9.  “XXX” represents the fire-protection rating period, in minutes, as tested.

713.6.2.4 Installation. Fire window assemblies shall be installed in approved frames in a fixed position or be automatic-closing.

713.6.3 Fire dampers. Fire dampers shall comply with the provisions of this section.

Exception: Openings tested as part of a fire-resistance-rated wall assembly in accordance with ASTM E 119 shall not be required to comply with this section.

Where a building assembly is required to have both fire dampers and smoke dampers, combination fire/smoke dampers or a fire damper and a smoke damper shall be required.

Exception:(?)  Where the installation of a fire damper will interfere with the operation of a required smoke control system in accordance with Section 909, approved alternative protection shall be utilized.  Fire dampers are not required in shafts where ducts are used as part of an approved mechanical smoke control system designed in accordance with Section 909 and where the fire damper will interfere with the operation of the smoke control system.

Fire dampers for hazardous exhaust duct systems shall comply with the International Mechanical Code.

713.6.3.1 Fire protection rating.  Fire dampers shall have the fire protection rating indicated in Table 713.6.3.

TABLE 713.6.2

FIRE DAMPER FIRE PROTECTION RATINGS

(Contents of table to remain unchanged, except add new footnote)

713.6.3.2 Testing. Fire dampers shall be tested in accordance with UL 555.  Combination fire/smoke dampers shall be tested in accordance with both UL 555 and UL 555S.

713.6.3.3 Labeling. Fire dampers shall be labeled by an approved agency.

Only fire dampers labeled for use in dynamic systems shall be installed in heating, ventilation and air-conditioning systems designed to operate with fans on during a fire.

713.6.3.4 Installation. The fire damper actuating device shall meet one of the following requirements:

1. The operating temperature shall be approximately 50°F (10°C) above the normal temperature within the duct system, but not less than 160°F (71°C).

2. The operating temperature shall be not more than 286°F (141°C) where located in a smoke control system complying with Section 909.

3. Where a combination fire/smoke damper is located in a smoke control system complying with Section 909, the operating temperature rating shall be approximately 50°F (10°C) above the maximum smoke control system designed operating temperature, or a maximum temperature of 350°F (177°C). The temperature shall not exceed the UL 555S degradation test temperature rating for a combination fire/smoke damper.

Fire dampers shall be provided with an approved means of access, which is large enough to permit inspection and maintenance of the damper and its operating parts.  The access openings shall not reduce the fire-resistance rating of the building assembly.  The access shall not affect the integrity of fire-resistance-rated building assemblies.  Access points shall be permanently identified on the exterior by a label having letters not less than 0.5 inch (12.7 mm) in height reading: FIRE DAMPER or FIRE/SMOKE DAMPER.  Access doors in ducts shall be tight fitting and suitable for the required duct construction.

Fire dampers and combination fire/smoke dampers located within air distribution and smoke control systems shall be installed in accordance with the requirements of this section, the manufacturer’s installation instructions and the dampers’ listing.

713.6.4 Ceiling dampers.  Ceiling dampers shall comply with the provisions of this section and the applicable provisions of Section 713.6.3.

Exception: Ceiling radiation dampers are not required where either of the following applies:

1.	Where tests in accordance with ASTM E 119 have shown that ceiling radiation dampers are not necessary in order to maintain the fire-resistance rating of the assembly.

2.	Where exhaust duct penetrations are protected in accordance with Section 712.4.1.2, are located within the cavity of a wall and do not pass through another dwelling unit or tenant space.

713.6.4.1 Fire protection rating. Ceiling dampers shall have the fire protection rating indicated in Table 713.6.3.

713.6.4.2 Testing. Ceiling radiation dampers shall be tested in accordance with UL 555C.  Ceiling radiation dampers shall be tested in accordance with UL 555C and installed in accordance with the manufacturer’s installation instructions and listing.

713.6.4.3 Labeling. Ceiling dampers shall be labeled by an approved agency.

713.6.4.4 Installation.  Ceiling radiation dampers located within air distribution and smoke control systems shall be installed in accordance with the requirements of this section, the manufacturer’s installation instructions and the dampers’ listing.

713.6.5 Through-penetration fire stops. Through-penetration or membrane- penetration fire stops shall comply with the provisions of this section. Through-penetrations or membrane-penetrations in fire-resistance rated building assemblies that are not smoke barriers shall be shall tested in accordance with ASTM E 814 or UL 1479, with a minimum positive pressure differential of 0.01 inch (2.49 Pa) of water, or shall comply with any of the alternative methods listed in Sections 713.6.5.1 through 713.6.5.9. The tested system shall have a minimum one hour F-rating and T-rating, or a rating equal to the required rating of the building assembly penetrated if such assembly has a fire resistance rating greater than one hour. Penetration protection of smoke barriers shall comply with Section 9XXX.X.  Penetrations of Non- fire resistance rated horizontal fire compartment envelope assemblies are permitted to comply with the provisions of this section or section 714.6.7.

Exceptions:

1. Floor penetrations contained and located within the cavity of a wall do not require a T- rating.

2. Penetrations tested as part of a fire-resistance-rated wall assembly in accordance with ASTM E 119 shall not be required to comply with this section.

713.6.5.1 Membrane-penetrations.  Membrane-penetrations or partial penetrations shall comply with the requirements for though-penetrations.

713.6.5.1 Single concrete floor penetrations (metal pipe or tube).  Penetrations in a single concrete floor by steel, ferrous or copper conduits, pipes, tubes or vents with a maximum 6-inch (152 mm) nominal diameter, provided the concrete, grout or mortar is installed the full thickness of the floor or the thickness required to maintain the fire-resistance rating. The penetrating items shall not be limited to the penetration of a single concrete floor, provided the area of the opening through each floor does not exceed 144 square inches (92 900 mm2).

713.6.5.2 Single fire-resistance rated floor penetrations (metal pipe or tube).  Penetrations by steel, ferrous or copper conduits, pipes, tubes or vents or concrete or masonry items through a single fire-resistance-rated floor assembly where the annular space is protected with materials that prevent the passage of flame and hot gases sufficient to ignite cotton waste when subjected to ASTM E 119 time-temperature fire conditions under a minimum positive pressure differential of 0.01 inch (2.49 Pa) of water at the location of the penetration for the time period equivalent to the fire-resistance rating of the construction penetrated. Penetrating items with a maximum 6-inch (152 mm) nominal diameter shall not be limited to the penetration of a single fire-resistance-rated floor assembly, provided the aggregate area of the openings through the assembly does not exceed 144 square inches (92 900 mm2) in any 100 square feet (9.3 m2) of floor area.

713.6.5.3 Fire-resistance rated wall penetrations (metal pipe or tube).  Penetrations by steel, ferrous or copper pipes, tubes or conduits, are permitted provided the annular space between the penetrating item and the fire-resistance-rated wall is protected as follows:

1.	In concrete or masonry walls where the penetrating item is a maximum 6-inch (152 mm) nominal diameter and the area of the opening through the wall does not exceed 144 square inches (0.0929 m2), concrete, grout or mortar is permitted where it is installed the full thickness of the wall or the thickness required to maintain the fire-resistance rating; or

2. The material used to fill the annular space shall prevent the passage of flame and hot gases sufficient to ignite cotton waste when subjected to ASTM E 119 time-temperature fire conditions under a minimum positive pressure differential of 0.01 inch (2.49 Pa) of water at the location of the penetration for the time period equivalent to the fire-resistance rating of the construction penetrated.

713.6.5.4 Floor assembly membrane penetrations (metal pipe or tube).   Membrane-penetrations of a maximum 2-hour fire-resistance-rated horizontal assembly by steel, ferrous or copper conduits, pipes, tubes or vents, or concrete or masonry items where the annular space is protected to prevent the free passage of flame and the products of combustion. The aggregate area of the openings through the membrane shall not exceed 100 square inches (64 500 mm2) in any 100 square feet (9.3 m2) of ceiling area in assemblies tested without penetrations.

713.6.5.5 Listed electrical box penetrations.  Penetrations by listed electrical boxes of any material, provided such boxes have been tested for use in fire-resistance-rated assemblies and are installed in accordance with the instructions included in the listing. The annular space between the ceiling membrane and the box shall not exceed 1/8 inch (3.1 mm) unless listed otherwise.

713.6.5.6 Listed electrical box membrane penetrations.  Membrane-penetrations of a fire rated assembly membrane by listed electrical boxes of any material, are permitted provided such boxes have been tested for use in fire-resistance-rated assemblies and are installed in accordance with the instructions included in the listing. The annular space between the wall membrane and the box shall not exceed 1/8 inch (3.1 mm) unless listed otherwise. Such boxes on opposite sides of the wall or partition shall be separated as follows:

1. By a horizontal distance of not less than 24 inches (610 mm);

2. By solid fireblocking in accordance with Section 717.2.1;

3. By protecting both boxes with listed putty pads; or

4. By other listed materials and methods.

5. The annular space created by the penetration of a fire sprinkler, provided it is covered by a metal escutcheon plate.

713.6.5.7 Steel electrical box membrane floor penetrations.  Ceiling membrane penetrations of maximum 2-hour fire-resistance-rated horizontal assemblies by steel electrical boxes that do not exceed 16 square inches (10 323 mm2) in area, provided the aggregate area of such penetrations does not exceed 100 square inches (44 500 mm2) in any 100 square feet (9.29 m2) of ceiling area, and the annular space between the ceiling membrane and the box does not exceed 1/8 inch (3.12 mm).

713.6.5.8  Steel electrical box membrane wall penetrations.  Partial assembly penetrations of an assembly membrane of maximum two-hour fire-resistance-rated walls and partitions are permitted by steel electrical boxes that do not exceed 16 square inches (0.0103 m2) in area, provided the aggregate area of the openings through the membrane does not exceed 100 square inches (0.0645 m2) in any 100 square feet (9.29 m2) of wall area. The annular space between the wall membrane and the box shall not exceed 1/8 inch (3.1 mm). Such boxes on opposite sides of the wall or partition shall be separated by one of the following:

1. By a horizontal distance of not less than 24 inches (610 mm);

2. By a horizontal distance of not less than the depth of the wall cavity where the wall cavity is filled with cellulose loose-fill, rockwool or slag mineral wool insulation;

3. By solid fireblocking in accordance with Section 717.2.1;

4. By protecting both outlet boxes with listed putty pads; or

5. By other listed materials and methods.

713.6.5.9  Sprinkler head penetrations.  The annular space created by the penetration of a fire sprinkler head is permitted to be protected by a metal escutcheon plate that completely covers the annular space.

713.6.5.10  Installation. Noncombustible penetrating items shall not connect to combustible items beyond the point of firestopping unless it can be demonstrated that the fire-resistance integrity of the building assembly wall is maintained.

Where sleeves are used, they shall be securely fastened to the building assembly penetrated. The space between the item contained in the sleeve and the sleeve itself and any space between the sleeve and the assembly penetrated shall be protected in accordance with the applicable provisions of Section 713.6.5.1 or 713.6.5.2. Insulation and coverings on or in the penetrating item shall not penetrate the building assembly unless the specific material used has been tested as part of the assembly in accordance with this section.

713.6.6 Fire-resistant joint systems.  Fire-resistant joint systems shall comply with the provisions of this section. Joints in or between fire-resistance-rated building assemblies shall be protected by a fire-resistant joint system.

Exception: Fire-resistant joint systems shall not be required for joints in the following locations:

1. Floors within a single dwelling unit.

2. Floors within malls.

3. Mezzanine floors.

4. Walls that are permitted to have unprotected openings.

5. Roofs where openings are permitted.

6. Control joints not exceeding a maximum width of 0.625 inch (15.9 mm) and tested in accordance with ASTM E 119.

713.6.6.1 Fire protection rating.  Fire-resistant joint systems shall be designed to resist the passage of fire for a time period not less than the required fire-resistance rating of the building assembly in or between which it is installed.

713.6.6.2 Testing. Fire-resistant joint systems shall be tested in accordance with the requirements of either ASTM E 1966 or UL 2079. Nonsymmetrical wall joint systems shall be tested with both faces exposed to the furnace, and the assigned fire-resistance rating shall be the shortest duration obtained from the two tests. When evidence is furnished to show that the wall was tested with the least fire-resistant side exposed to the furnace, subject to acceptance of the building official, the wall need not be subjected to tests from the opposite side.

Exception: For exterior walls with a horizontal fire separation distance greater than 5 feet (1524 mm), the joint system shall be required to be tested for interior fire exposure only.

714.6.6.3 Installation. Fire-resistant joint systems shall be securely installed in or on the joint for its entire length so as not to dislodge, loosen or otherwise impair its ability to accommodate expected building movements and to resist the passage of fire and hot gases.

714.6.6.4 Exterior curtain wall/floor intersection.  Where fire resistance-rated floor or floor/ceiling assemblies are required, voids created at the intersection of the exterior curtain wall assemblies and such floor assemblies shall be sealed with an approved material or system to prevent the interior spread of fire. Such material or systems shall be securely installed and capable of preventing the passage of flame and hot gases sufficient to ignite cotton waste where subjected either to ASTM E 119 time-temperature fire conditions under a minimum positive pressure differential of 0.01 inch (0.254 mm) of water column (2.5 Pa) or installed as tested in accordance with ASTM E 2307 for the time period at least equal to the fire-resistance rating of the floor assembly. Height and fire-resistance requirements for curtain wall spandrels shall comply with Section 704.9.  Where Section 704.9 does not require a fire-resistance-rated spandrel wall, the requirements of this section shall still apply to the intersection between the spandrel wall and the floor.

713.7 Nonfire-resistance-rated fire compartment opening protection.  Openings in nonfire-resistance rated floor/ceiling construction that is a portion of a fire compartment envelope shall be protected in accordance with this section or enclosed in accordance with Sections 713.8.1 through 713.8.3.

713.7.1 Penetrating items.  Through-membrane or membrane-penetrations in or between floor or floor/ceiling building assemblies shall be protected by an approved flamestop or a listed through-penetration firestop system.

713.7.2 Construction joints.  Joints installed in or between floor or floor/ceiling building assemblies shall be protected by an approved flamestop or a listed fire-resistant joint system.

713.7.3 Ducts. Ducts shall be constructed of sheet steel not less than 0.019 inch (0.48 mm) (26 gage) in thickness.  The annular space around the duct shall not exceed 1/8 inch (3.1 mm) and shall be filled with cellulose loose-fill, rockwool or slag mineral wool insulation or other approved material.  Or, ducts shall be protected with a listed fire damper.

713.8 Enclosures. Shaft enclosures, exit enclosures and atrium enclosures required by other provisions of this code shall comply with the provisions of this section.

713.8.1 Utility openings.  Except as permitted in Section 715.2, openings in floor/ceiling construction for elevators, dumbwaiters, or other hoistways; refuse and laundry chutes and plumbing, electrical, HVAC or other equipment shall be enclosed by a shaft enclosure constructed in accordance with this section.  Elevator, dumbwaiter and other hoistway enclosures shall be also be constructed in accordance with Chapter 30.

Exception:  A shaft enclosure is not required for approved masonry chimneys, where annular space protection is provided at each floor level in accordance with Section 717.2.5.

A shaft enclosure containing a refuse chute or laundry chute shall not be used for any other purpose and shall originate and terminate in rooms in accordance with Section 713.7.1.2.3.

Exception: Chutes serving, and contained within, a single dwelling unit.

Refuse chutes shall not terminate in an incinerator room.

713.8.1.1 Materials.  Shaft enclosures shall be constructed of materials consistent with those permitted for the type of construction of the building in accordance with Section 602.2-5.

713.8.1.2 Construction.  Shaft enclosures shall be constructed as fire barriers in accordance with Section 708 or horizontal barriers in accordance with Section 711, or both.

713.8.1.2.1 Bottom enclosure. Shaft enclosures that do not extend to the bottom of the building or structure shall be enclosed at the lowest level with a horizontal barrier having the same fire-resistance rating as the lowest floor through which the shaft enclosure passes, but not less than the rating required for the shaft enclosure or shall terminate in a room complying with the provisions of Section 713.7.1.2.3.

Exception: A termination room or a horizontal barrier at the bottom of the shaft enclosure are not required provided there are no combustible materials in the shaft enclosure and there are no openings through the shaft enclosure to the interior of the building.

Openings in a horizontal barrier at the bottom of a shaft enclosure shall be protected with opening protective assemblies in accordance with Sections 713.6.3 through 713.6.6

713.8.1.2.2 Top enclosure.  Shaft enclosures that do not extend to the underside of the roof sheathing, slab or deck of the building shall be enclosed at the top with a horizontal barrier having the same fire-resistance rating as the topmost floor through which the shaft enclosure passes, but not less than the fire-resistance rating required for the shaft enclosure.

Openings in a horizontal barrier at the top of a shaft enclosure shall be protected with opening protective assemblies in accordance with Sections 713.6.3 through 713.6.6

713.8.1.2.3 Access and termination rooms.  Access and termination rooms shall comply with the provisions of this section.  Where applicable, termination rooms shall also comply with the provisions of Section 508.2.  Access and termination rooms shall be constructed as fire barriers in accordance with Section 708 or horizontal assemblies in accordance with Section 710, or both and shall have a fire-resistance ratings of not less 1 hour.  Access and termination rooms shall be equipped with an automatic sprinkler system installed in accordance with Section 903.2.10.2.

713.8.1.2.4 Elevator lobbies. A lobby shall be provided at each floor where a shaft enclosure contains an elevator and connects more than three stories.  Lobbies constructed as fire partitions in accordance with Section 709 (smoke partitions in accordance with Section 9XX?) shall separate shaft enclosure doors from means of egress corridors at each floor.  Such fire partitions shall have a fire-resistance rating equal to that of the corridor and have required opening protection. Elevator lobbies shall have at least one means of egress complying with Chapter 10 and other provisions within this code.

Exceptions:

1. Elevator lobbies are not required at the street floor provided the entire street floor is equipped with an automatic sprinkler system in accordance with Section 903.3.1.1.

2. Where additional doors are provided at the shaft enclosure opening in accordance with Section 3002.6.  Such doors shall be tested in accordance with UL 1784 without an artificial bottom seal.

3. In other than Group I-3 occupancies and buildings having occupied floors located more than 75 feet (22 860 mm) above the lowest level of fire department vehicle access, elevator lobbies are not required where the building is equipped with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2.

4. Smoke partitions shall be permitted in lieu of fire partitions to separate the elevator lobby at each floor where the building is equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2. (?)

5. Elevator lobbies are not required where the shaft enclosure is pressurized in accordance with Section 713.7.1.3.4.1.

713.8.1.2.4.1 Pressurization alternative.  Shaft enclosure pressurization is permitted to be provided in lieu of required elevator lobbies.  The pressurization system shall comply with this section.

Shaft enclosures shall be pressurized to maintain a minimum positive pressure of 0.04 inches of water column and a maximum positive pressure of 0.06 inches of water column with respect to adjacent occupied space on all floors.  This pressure shall be measured at the midpoint of each shaft enclosure door, with all ground floor level shaft enclosure doors open and all other shaft enclosure doors closed.

Fan systems located within the building and duct systems that are part of the pressurization system shall be protected with the same fire-resistance rating as required for the elevator shaft enclosure. The fan system shall be equipped with a smoke detector that will automatically shut down the fan system when smoke is detected within the system. A separate fan system shall be used for each bank of elevators.  The supply air intake shall be from an outside, uncontaminated source located a minimum distance of 20 feet (6096 mm) from any air exhaust system or outlet.  The supply fan shall either be adjustable with a capacity of at least 1,000 cfm (.4719 m3/s) per door, or that specified by a registered design professional to meet the requirements of a designed pressurization system.  The pressurization system shall be provided with standby power from the same source as other required emergency systems for the building.  The shaft enclosure pressurization system shall be activated upon activation of the building fire alarm system or upon activation of the elevator lobby smoke detectors.

713.8.1.3 Fire-resistance rating.  Shaft enclosures shall have a fire-resistance rating of not less than 1 hour where connecting less than four stories and not less than 2 hours where connecting four stories or more. Shaft enclosures shall have a fire-resistance rating not less than the floor/ceiling assembly penetrated, but need not exceed 2 hours.

Exception:  Where exterior walls serve as a part of a shaft enclosure, such walls shall comply with the requirements of Section 706 for exterior walls and the fire-resistance-rated shaft enclosure requirements shall not apply.

713.8.1.4 Openings.  Openings in shaft enclosures shall be protected with opening protective assemblies in accordance with Section 713.5.2.2 for fire barriers.

Exceptions:

1. Fire dampers are not required in shafts where:

1.1. Steel exhaust subducts are extended at least 22 inches (559 mm) vertically in exhaust shafts, provided there is a continuous airflow upward to the outside; or

1.2. The penetrations are in parking garage exhaust or supply shafts that are separated from other building shafts by not less than 2-hour fire-resistance-rated construction.

2. In Group B and R occupancies equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, smoke dampers are not required in shafts where:

2.1. Kitchen, clothes dryer, bathroom and toilet room exhaust openings are installed with steel exhaust subducts, having a wall thickness of at least 0.019 inch (0.48 mm); and

2.2. Subducts extend at least 22 inches (559 mm) vertically; and

2.3. An exhaust fan is installed at the upper terminus of the shaft that is, powered continuously in accordance with the provisions of Section 909.11, so as to maintain a continuous upward airflow to the outside.

3. Smoke dampers are not required in exhaust or supply shafts in parking garages that are separated from other building shafts by not less than 2-hour fire-resistance-rated construction.

4. Smoke dampers are not required in shafts where ducts are used as part of an approved mechanical smoke control system designed in accordance with Section 909 and where the smoke damper will interfere with the operation of the smoke control system.

Openings other than those necessary for the utility purpose of the shaft shall not be permitted in shaft enclosures.

Openings into refuse or laundry chutes shall not be located in means of egress corridors.  Heat-activated closing devices shall be permitted between refuse or laundry chutes and their termination rooms.

713.8.2 Egress openings.  Except as permitted in Section 713.2, openings in floor/ceiling construction for interior means of egress stairways and ramps shall be enclosed by an exit enclosure constructed in accordance with this section.

Exceptions:

1. Means of egress stairways as required by Section 410.5.4 are not required to be enclosed.

2. Stairways in Group I-3 occupancies, as provided for in Section 408.3.6, are not required to be enclosed.

713.8.2.1 Materials.  Exit enclosures shall be constructed of materials consistent with those permitted for the type of construction of the building in accordance with Section 602.2-5.

713.8.2.2 Construction.  Exit enclosures shall be constructed as fire barriers in accordance with Section 708 or horizontal barriers in accordance with Section 711, or both.

Exterior walls of an exit enclosure shall comply with the requirements of Section 706 for exterior walls. Where nonrated walls or unprotected openings enclose the exterior of the stairway and the walls or openings are exposed by other parts of the building at an angle of less than 180 degrees (3.14 rad), the building exterior walls within 10 feet (3048 mm) horizontally of a nonrated wall or unprotected opening shall have a fire-resistance rating of not less than 1 hour. Openings within such exterior walls shall be protected by opening protectives having a fire protection rating of not less than 3/4 hour. This construction shall extend vertically from the ground to a point 10 feet (3048 mm) above the topmost landing of the stairway or to the roof line, whichever is lower.

713.8.2.3 Fire-resistance rating.  Exit enclosures shall have a fire-resistance rating of not less than 1 hour where connecting less than four stories and not less than 2 hours where connecting four stories or more. Exit enclosures shall have a fire-resistance rating not less than the floor/ceiling assembly penetrated, but need not exceed 2 hours.

713.8.2.4 Openings. Openings in exit enclosures shall be protected with opening protective assemblies in accordance with Section 713.5.2.2 for fire barriers.

Openings in exit enclosures shall be limited to those necessary for exit access to the enclosure from normally occupied spaces and for egress from the exit enclosure.

Exceptions:

1. Unprotected exterior openings as permitted in Section 706.8.

2. Service areas as permitted in Section 402.4.6.

Openings into or through an exit enclosure are prohibited except for required exit doors, equipment and ductwork necessary for independent pressurization, sprinkler piping, standpipes, electrical raceways for fire department communication systems and electrical raceways serving the exit enclosure and terminating at a steel box not exceeding 16 square inches (0.010 m2). Such openings shall be protected in accordance with Section 713.6.5. There shall be no penetrations or communication openings, whether protected or not, between adjacent exit enclosures.

Equipment and ductwork for exit enclosure ventilation shall comply with one of the following items:

1. Such equipment and ductwork shall be located exterior to the building and shall be directly connected to the exit enclosure by ductwork enclosed in construction as required for shafts.

2. Where such equipment and ductwork is located within the exit enclosure, the intake air shall be taken directly from the outdoors and the exhaust air shall be discharged directly to the outdoors, or such air shall be conveyed through ducts enclosed in construction as required for shafts.

3. Where located within the building, such equipment and ductwork shall be separated from the remainder of the building, including other mechanical equipment, with construction as required for shafts.

In each case, openings into the fire-resistance-rated construction shall be limited to those necessary for maintenance and operation and shall be protected by opening protective assemblies in accordance with Section 715 for shaft enclosures.

Exit enclosure ventilation systems shall be independent of other building ventilation systems.

Elevators shall not open into an exit enclosure.

Fire door assemblies in exit enclosures shall comply with Section 713.6.1.2.

713.8.3 Architectural openings.  Except as permitted in Section 715.3.2, openings in floor/ceiling construction for aesthetic or functional purposes, to include escalators, shall be enclosed by an atrium enclosure constructed in accordance with this section.

The floor of the atrium shall not be used for other than low fire hazard uses and only approved materials and decorations in accordance with the International Fire Code shall be used in the atrium space.

Exception: The atrium floor area is permitted to be used for any approved use where the individual space is provided with an automatic sprinkler system in accordance with Section 903.3.1.1.

713.8.3.1 Materials.  Atrium enclosures shall be constructed of materials consistent with those permitted for the type of construction of the building in accordance with Section 602.2-5.

713.8.3.2 Construction.  Atrium enclosures shall be constructed as fire barriers in accordance with Section 708 or horizontal barriers in accordance with Section 711, or both.

713.8.3.3 Fire-resistance rating. Atrium enclosures shall have a fire-resistance rating of not less than 1 hour.

Exceptions:

1. A glass wall forming a smoke partition where automatic sprinklers are spaced 6 feet (1829 mm) or less along both sides of the separation wall, or on the room side only if there is not a walkway on the atrium side, and between 4 inches and 12 inches (102 mm and 305 mm) away from the glass and designed so that the entire surface of the glass is wet upon activation of the sprinkler system without obstruction. The glass shall be installed in a gasketed frame so that the framing system deflects without breaking (loading) the glass before the sprinkler system operates.

2. A glass-block wall assembly in accordance with Section 2110 and having a ¾-hour fire protection rating.

3. The adjacent spaces of any three floors of the atrium shall not be required to be separated from the atrium where such spaces are included in the design of the smoke control system.

713.8.3.4 Openings. Openings in atrium enclosures shall be protected with opening protective assemblies in accordance with Section 713.5.2.2 for fire barriers.

Exception: Fire window assemblies permitted in atrium enclosure walls shall not be limited to a maximum aggregate width of 25 percent of length of the wall.

713.8.3.5 Escalators.  An enclosure is not required in a building equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 for an escalator opening or stairway that is not a portion of the means of egress protected according to Item 2.1 or 2.2:

2.1.	Where the area of the floor opening between stories does not exceed twice the horizontal projected area of the escalator or stairway and the opening is protected by a draft curtain and closely spaced sprinklers in accordance with NFPA 13. In other than Groups B and M, this application is limited to openings that do not connect more than four stories.

2.2.	Where the opening is protected by approved power-operated automatic shutters at every penetrated floor. The shutters shall be of noncombustible construction and have a fire-resistance rating of not less than 1.5 hours. The shutter shall be so constructed as to close immediately upon the actuation of a smoke detector installed in accordance with Section 907.11 and shall completely shut off the well opening. Escalators shall cease operation when the shutter begins to close. The shutter shall operate at a speed of not more than 30 feet per minute (152.4 mm/s) and shall be equipped with a sensitive leading edge to arrest its progress where in contact with any obstacle, and to continue its progress on release therefrom.

713.8.3.6 Unlimited height in stories.  An atrium is permitted to be of unlimited height in stories based on the building type of construction when complying with the provisions of this section.

713.8.3.6.1 Automatic sprinkler system.  An approved automatic sprinkler system shall be installed throughout the entire building.

Exceptions:

1. That area of a building adjacent to or above the atrium need not be sprinklered, provided that portion of the building is separated from the atrium portion by not less than a 2-hour fire-resistance-rated fire barrier or horizontal assembly, or both.

2. Where the ceiling of the atrium is more than 55 feet (16 764 mm) above the floor, sprinkler protection at the ceiling of the atrium is not required.

713.8.3.6.2 Smoke control system. A smoke control system shall be installed in accordance with Section 909.

713.8.3.6.3 Standby power. Equipment required to provide smoke control shall be connected to a standby power system in accordance with Section 909.11.

713.8.3.6.4 Interior finish. The interior finish of walls and ceilings of the atrium shall not be less than Class B with no reduction in class for sprinkler protection.

713.8.3.6.5 Travel distance. In other than the lowest level of the atrium, where the required means of egress is through the atrium space, the portion of means of egress travel distance within the atrium space shall not exceed 200 feet (60 960 mm).

(RELATED CHANGES)

TABLE 601

FIRE-RESISTANCE RATING REQUIREMENTS FOR BUILDING ASSEMBLIES BASED ON TYPE OF CONSTRUCTION

BUILDING ASSEMBLY

(Remainder of table to remain unchanged)

SECTION 708

FIRE BARRIERS

708.1 General.

708.7 Openings. Openings in fire barriers shall be protected in accordance with the provisions of Section 713.5.2.2.

Fire door assembly and fire window assembly openings shall be limited to a maximum aggregate width of 25 percent of the length of the wall, and the maximum area of any single opening shall not exceed 156 square feet (15 m2).

Exceptions:

1. Such openings shall not be limited to 156 square feet (15 m2) where adjoining fire areas are equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.

2. Fire door assemblies serving an exit enclosure.

3. Such openings shall not be limited to 156 square feet (15 m2) or an aggregate width of 25 percent of the length of the wall where the opening protective assembly has been tested in accordance with ASTM E 119 and has a minimum fire-resistance rating not less than the fire-resistance rating of the wall.

SECTION 710

HORIZONTAL ASSEMBLIES

710.1 General.  Floor and roof assemblies required to have a fire-resistance rating by Table 601 shall comply with this section.

710.2 Materials.  Horizontal assemblies shall be constructed of materials consistent with those permitted for the type of construction of the building in accordance with Section 602.2-5.

710.3 Fire-resistance rating.  Horizontal assemblies shall have a fire-resistance rating not less than that required by Table 601 based on the building type of construction.  Construction supporting a horizontal assembly shall be protected so as to provide the required fire-resistance rating of such horizontal assembly.

Floor assemblies separating dwelling units in the same building or sleeping units in occupancies in Group R-1, hotel occupancies, R-2 and I-1 shall be a minimum of 1-hour fire-resistance-rated construction.  (Does this belong as a footnote to Table 601?)

Exception: Dwelling unit and sleeping unit separations in buildings of Type IIB, IIIB, and VB construction shall have fire-resistance ratings of not less than ½ hour in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.  (Does this belong as a footnote to Table 601?)

710.4 Openings.  Openings in horizontal assemblies shall be protected in accordance with the provisions of Section 713.3.2.

SECTION 711

HORIZONTAL BARRIERS

711.1 General.  Where required by other provisions of this code, horizontal barriers shall comply with this section.

711.2 Materials.  Horizontal barriers shall be constructed of materials consistent with those permitted for the type of construction of the building in accordance with Section 602.2-5.

711.3 Fire-resistance rating.  Horizontal barriers shall have a fire-resistance rating not less than that required by Table 601 based on the building type of construction and as required elsewhere in this code.  Construction supporting a horizontal barrier shall be protected so as to provide the required fire-resistance rating of such horizontal barrier.

Where the floor assembly separates mixed occupancies, the assembly shall have a fire-resistance rating of not less than that required by Section 508.3.2 based on the occupancies being separated. Where the floor assembly separates a single occupancy into different fire areas, the assembly shall have a fire-resistance rating of not less than that required by Section 706.3.9 (901.7). Floor assemblies separating dwelling units in the same building or sleeping units in occupancies in Group R-1, hotel occupancies, R-2 and I-1 shall be a minimum of 1-hour fire-resistance-rated construction.  (Does this belong as a footnote to Table 601?)

Exception: Dwelling unit and sleeping unit separations in buildings of Type IIB, IIIB, and VB construction shall have fire-resistance ratings of not less than ½ hour in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.  (Does this belong as a footnote to Table 601?)

711.4 Openings.  Openings in horizontal barriers shall be protected in accordance with the provisions of Section 713.3.3.

Voids created at the intersection of a horizontal barrier and an exterior curtain wall assembly shall be protected in accordance with Section 713.4.  (This is a cross-reference and may not be necessary.)

CHAPTER 9 (Maybe help from Doug Evans?)

Section 902.1 Definitions.

SMOKE COMPARTMENT. A fire-resistance rated or nonfire-resistance rated envelope of building construction beyond which no atmospheric communication of smoke will occur.  (Locate definition and envelope provisions in Chapter 9 because the title of Chapter 7 is FIRE-RESISTANCE-RATED CONSTRUCTION?)

SMOKE BARRIER

SMOKE PARTITION

Section 909

9XX.X Smoke compartments. Smoke compartments shall comply with the applicable provisions of Section 909 and the International Fire Code.  (Move to Chapter 9)

9XX.X Smoke compartments. Smoke compartments shall include those building areas that are separated by smoke barriers or smoke partions or are protected by a mechanical smoke control system.

9XXX.X Smoke barriers.

9XXX.X.1 Openings. A listed smoke damper designed to resist the passage of smoke shall be provided at each point a duct or air transfer opening penetrates a smoke barrier. Smoke dampers and smoke damper actuation methods shall comply with Section 716.3.2.1.

Exception: Smoke dampers are not required where the openings in ducts are limited to a single smoke compartment and the ducts are constructed of steel.

Fire-resistant joint systems in smoke barriers shall be tested in accordance with the requirements of UL 2079 for air leakage. The air leakage rate of the joint shall not exceed 5 cfm per lineal foot (0.00775 m3/slm ) of joint at 0.30 inch (7.47 Pa ) of water for both the ambient temperature and elevated temperature tests.

Penetrations in smoke barriers shall be tested in accordance with the requirements of UL 1479 for air leakage. The air leakage rate of the penetration assembly shall not exceed 5.0 cfm per square foot (0.025 m3 / s × m2 ) of penetration opening at 0.30 inch ( 7.47 Pa) of water for both the ambient temperature and elevated temperature tests.

9XX.X Smoke dampers.  Smoke dampers shall comply with the provisions of this section.  Where a building assembly is required to have both fire dampers and smoke dampers, combination fire/smoke dampers or a fire damper and a smoke damper shall be required.

9XXX.X.1 Leakage rating.  Smoke damper leakage ratings shall not be less than Class II. Elevated temperature ratings shall not be less than 250°F (121°C).

9XXX.X.2 Testing. Smoke dampers shall comply with the requirements of UL 555S. Combination fire/smoke dampers shall comply with the requirements of both UL 555 and UL 555S.

9XXX.X.3 Labeling. Smoke dampers shall be listed and bear the label of an approved testing agency indicating compliance with the referenced standards in this section.

9XXX.X.4 Installation. Smoke dampers and combination fire/smoke dampers located within air distribution and smoke control systems shall be installed in accordance with the requirements of this section, the manufacturer’s installation instructions and the dampers’ listing.

Smoke dampers shall close upon actuation of a listed smoke detector(s) installed in accordance with Section 907.10 and one of the following methods, as applicable:

1. Where a smoke damper is installed within a duct, a smoke detector shall be installed in the duct within 5 feet (1524 mm) of the smoke damper with no air outlets or inlets between the detector and the damper. The smoke detector shall be listed for the air velocity, temperature and humidity anticipated at the point where it is installed. Other than in mechanical smoke control systems, smoke dampers shall be closed upon fan shutdown where local smoke detectors require a minimum velocity to operate.

2. Where a smoke damper is installed above doors in a smoke barrier, a spot-type detector listed for releasing service shall be installed on either side of the smoke barrier door opening.

3. Where a smoke damper is installed within an unducted opening in a wall, a spot-type detector listed for releasing service shall be installed within 5 feet (1524 mm) horizontally of the smoke damper.

4. Where a smoke damper is installed in a corridor wall or ceiling, the damper shall be permitted to be controlled by a smoke detection system installed in the corridor.

5. Where a smoke damper is installed within areas served by a heating, ventilation and air-conditioning (HVAC) system and a total-coverage smoke detector system is provided, smoke dampers shall be permitted to be controlled by the smoke detection system.

Smoke dampers shall be provided with an approved means of access, which is large enough to permit inspection and maintenance of the damper and its operating parts.  The access openings shall not reduce the fire-resistance rating of the building assembly.  The access shall not affect the integrity of fire-resistance-rated building assemblies.  Access points shall be permanently identified on the exterior by a label having letters not less than 0.5 inch (12.7 mm) in height reading: SMOKE DAMPER or FIRE/SMOKE DAMPER.  Access doors in ducts shall be tight fitting and suitable for the required duct construction.

A listed smoke damper designed to resist the passage of smoke shall be provided at each point a duct or air transfer opening penetrates a corridor enclosure required to have smoke and draft control doors in accordance with Section 715.4.3.

Exceptions:

1.	Smoke dampers are not required where the building is equipped throughout with an approved smoke control system in accordance with Section 909, and smoke dampers are not necessary for the operation and control of the system.

2.	Smoke dampers are not required in corridor penetrations where the duct is constructed of steel not less than 0.019 inch (0.48 mm) in thickness and there are no openings serving the corridor.

Where required.

Group I-2 occupancies.

High rise buildings.

Smokeproof exit enclosures.

Elevator shaft enclosures.

Etc.

715.5 Wall construction.  Openings in fire-resistance rated wall construction shall comply with the provisions of this section.

715.5.2.2 Fire walls, fire barriers, fire partitions, smoke barriers and smoke partitions (To Ch 9?).  Openings in fire walls, fire barriers, fire partitions, smoke barriers and smoke partitions shall be protected in accordance with the provisions this section.

715.6.X Smoke dampers.  Smoke dampers shall comply with the provisions of this section.  (Move to Chapter 9 with definitions and procedural requirements?)

Section 910 SMOKE BARRIERS

Section 911 SMOKE PARTITIONS

SECTION 1020

EXIT ENCLOSURES

1020.1 General. Exit enclosures serving as a means of egress component in a means of egress system shall comply with the provisions of this section.  An exit enclosure shall not be used for any purpose other than means of egress. An exit enclosure shall discharge directly to the exterior of a building or into an exit passageway that discharges directly to the exterior of the building.

Exception: An exit enclosure shall be permitted to egress through areas on the level of discharge or vestibules as permitted by Section 1024.

1020.2 Construction. Exit enclosures shall be constructed in accordance with the provisions of Section 713.7.2.

1020.3 Discharge barrier. A stairway in an exit enclosure shall not continue below the level of exit discharge unless an approved barrier is provided at the level of exit discharge to prevent persons from unintentionally continuing into levels below. Directional exit signs shall be provided as specified in Section 1011.

1020.4 Stairway signs. A sign shall be provided at all floor landings in each exit enclosure that connects more than three stories.  Such sign shall identify the stairway and designate the floor level, the terminus of the top and bottom of the exit enclosure, the story of, and the direction to, the exit discharge and the availability of roof access from the stairway for the fire department. Such sign shall be located 5 feet (1524 mm) above the floor landing in a position that is readily visible when the doors are in both the open and closed positions.

1020.5 Smokeproof enclosures. In buildings required to comply with Section 403 or 405, each of the exit enclosures of a building that serves stories where the floor surface is located more than 75 feet (22 860 mm) above the lowest level of fire department vehicle access or more than 30 feet (9144 mm) below the level of exit discharge serving such floor levels shall be a smokeproof enclosure or pressurized stairway in accordance with Section 909.20.

1020.5.1 Enclosure access.  Access to the stairway within a smokeproof enclosure shall be by way of a vestibule or an open exterior egress balcony.

Exception: Pressurized stairways complying with the provisions of Section 909.20.5.

Create definition for travel distance?

1016.1 Travel distance.  …from most remote point to the entrance of an exit.

Exception:  Travel distance shall be permitted to terminate upon arrival at unenclosed interior stairways permitted by Section 713.1.1, exceptions.

SECTION 1021

EXIT PASSAGEWAYS

1021.4 Openings.

Where exit enclosures are extended to the exterior of a building by an exit passageway, the door assembly from the exit enclosure to the exit passageway shall be protected by a fire door assembly conforming to the requirements in Section 715.4.

Exit passageways connecting or extending exit enclosures shall be without other openings and shall be separated from the remainder of the building by 2-hour fire-resistance-rated construction.

Exceptions:

1. Openings in an exit passageway serving a smokeproof enclosure are permitted where the exit passageway is protected and pressurized in the same manner as the smokeproof enclosure, and openings are protected as required for access from other floors.

2. Openings in an exit passageway serving a pressurized stairway are permitted where the exit passageway is protected and pressurized in the same manner as the pressurized stairway.