| IBC S-2 Type IA | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |  |
| --- | --- | --- | --- | --- |
|  | Unlimited | Unlimited | Unlimited |  |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | Unlimited | n/a | n/a | Unlimited |
|  | Basements: Unlimited area |  |  |  |
|  | Specific Fire Resistance: - Structural frame = 3 hours; 2 hours (supporting roof only) - Bearing walls = 3 hours (exterior); 3 hours (interior); 2 hours (interior, supporting roof only) - Interior nonbearing walls & partitions = NR - Floors = 2 hours - Roofs = 1½ hours; NR or fire-retardant treated wood OK if ≥ 20’ above floor immediately below - Fire barriers between fire areas = 2 hours - Fire walls = 2 hours (based on occupancy) - Corridors = 1 hour (unsprinklered) @ occupant load > 30; NR (sprinklered) - 4-story unenclosed escalator or non-MOE stair allowed |  |  |  |
|  | Specific Fire Alarm Threshold: n/a |  |  |  |
|  | Specific Sprinkler Threshold: All buildings w/ S-2 occupancies. 5000 sq ft exemption for commercial truck/bus parking |  |  |  |
|  | Podium Buildings: n/a |  |  |  |

| UBC S-3 Type I-F.R. | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |  |
| --- | --- | --- | --- | --- |
|  | Unlimited | Unlimited | Unlimited |  |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | Unlimited | n/a | n/a | Unlimited |
|  | Basements: Unlimited area |  |  |  |
|  | Specific Fire Resistance: - Structural frame = 3 hours; NR or heavy timber OK for roofs if ≥ 25’ above floor - Bearing walls = 4 hours (exterior); 3 hours (interior) - Interior nonbearing walls & partitions = 1 hour, fire-retardant treated wood OK - Floors = 2 hours - Roofs = 2 hours; NR or fire-retardant treated wood OK if ≥ 25’ above floor - Area separation walls = 4 hours (based on type of construction) - Corridors = 1 hour, triggered by travel distance or >1 intervening room - Hallways = NR, treated as intervening room - Unlimited number of stories unenclosed escalator allowed |  |  |  |
|  | Specific Fire Alarm Threshold: n/a |  |  |  |
|  | Specific Sprinkler Threshold: n/a |  |  |  |
|  | Podium Buildings: n/a |  |  |  |

| IBC S-2 Type IB | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |  |
| --- | --- | --- | --- | --- |
|  | 11 stories, 160’ | 12 stories, 180’ | 12 stories, 180’ |  |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 79,000 | 1.75 | 2 | 888,750 (1-story w/ sprinklers Unlimited) |
|  | Basements: 138,250 (unsprinklered); 375,250 (sprinklered) |  |  |  |
|  | Specific Fire Resistance: - Structural frame = 2 hours; 1 hour (supporting roof only) - Bearing walls = 2 hours (exterior); 2 hours (interior); 1 hour (interior, supporting roof only) - Interior nonbearing walls & partitions = NR - Floors = 2 hours - Roofs = 1 hour; heavy timber OK; NR or fire-retardant treated wood OK if ≥ 20’ above floor immediately below; - Fire barriers between fire areas = 2 hours - Fire walls = 2 hours (based on occupancy) - Corridors = 1 hour (unsprinklered) @ occupant load > 30; NR (sprinklered) - 4-story unenclosed escalator or non-MOE stair allowed |  |  |  |
|  | Specific Fire Alarm Threshold: n/a |  |  |  |
|  | Specific Sprinkler Threshold: All buildings w/ S-2 occupancies. 5000 sq ft exemption for commercial truck/bus parking |  |  |  |
|  | Podium Buildings: Separate bldgs for area & number of stories; height measured fr grade plane |  |  |  |

| UBC S-3 Type II-F.R. | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |  |
| --- | --- | --- | --- | --- |
|  | 12 stories, 160’ | 13 stories, 160’ | 13 stories, 160’ (12 stories, 160’ if spr’s used for area) |  |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 39,900 | 2 | 2 | 319,200 (159,600 if spr’s used for stories) (2-stories w/ sprinklers Unlimited) |
|  | Basements: 79,800 (unsprinklered); 239,400 (sprinklered) |  |  |  |
|  | Specific Fire Resistance: - Structural frame = 2 hours; NR or heavy timber OK for roofs if ≥ 25’ above floor - Bearing walls = 4 hours (exterior); 2 hours (interior); 2 hours (interior, supporting roof only) - Interior nonbearing walls & partitions = 1 hour - Floors = 2 hours - Roofs = 1 hour; NR or fire-retardant treated wood OK if ≥ 25’ above floor - Area separation walls = 4 hours (based on type of construction) - Corridors = 1 hour, triggered by travel distance or >1 intervening room - Hallways = NR, treated as intervening room - Unlimited number of stories unenclosed escalator allowed |  |  |  |
|  | Specific Fire Alarm Threshold: n/a |  |  |  |
|  | Specific Sprinkler Threshold: n/a |  |  |  |
|  | Podium Buildings: Separate bldgs for area and number of stories; height measured from lowest of high grade or low grade + 10’ |  |  |  |

| IBC S-2 Type IIA | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |  |
| --- | --- | --- | --- | --- |
|  | 5 stories, 65’ | 6 stories, 85’ | 6 stories, 85’ |  |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 39,000 | 1.75 | 2 | 438,750 (1-story w/ sprinklers Unlimited) |
|  | Basements: 68,250 (unsprinklered); 185,250 (sprinklered) |  |  |  |
|  | Specific Fire Resistance: - Structural frame = 1 hour - Bearing walls = 1 hour (exterior or interior) - Interior nonbearing walls & partitions = NR - Floors = 1 hour - Roofs = 1 hour; heavy timber OK; NR or fire-retardant treated wood OK if ≥ 20’ above floor immediately below; - Fire barriers between fire areas = 2 hours - Fire walls = 2 hours (based on occupancy) - Corridors = 1 hour (unsprinklered) @ occupant load > 30; NR (sprinklered) - 4-story unenclosed escalator or non-MOE stair allowed |  |  |  |
|  | Specific Fire Alarm Threshold: n/a |  |  |  |
|  | Specific Sprinkler Threshold: All buildings w/ S-2 occupancies. 5000 sq ft exemption for commercial truck/bus parking |  |  |  |
|  | Podium Buildings: Separate bldgs for area & number of stories; height measured fr grade plane |  |  |  |

| UBC S-3 Type II-1 hour | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |  |
| --- | --- | --- | --- | --- |
|  | 4 stories, 65’ | 5 stories, 65’ | 5 stories, 65’ (4 stories, 65’ if spr’s used for area) |  |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 18,000 | 2 | 2 | 144,000 (72,000 if spr’s used for stories) (2-stories w/ sprinklers Unlimited) |
|  | Basements: 36,000 (unsprinklered); 108,000 (sprinklered) |  |  |  |
|  | Specific Fire Resistance: - Structural frame = 1 hour - Bearing walls = 1 hour (exterior or interior) - Interior nonbearing walls & partitions = 1 hour - Floors = 1 hour - Roofs = 1 hour; NR or fire-retardant treated wood OK if ≥ 25’ above floor - Area separation walls = 2 hours (based on type of construction) - Corridors = 1 hour, triggered by travel distance or >1 intervening room - Hallways = NR, treated as intervening room - Unlimited number of stories unenclosed escalator allowed |  |  |  |
|  | Specific Fire Alarm Threshold: n/a |  |  |  |
|  | Specific Sprinkler Threshold: n/a |  |  |  |
|  | Podium Buildings: Separate bldgs for area and number of stories; height measured from lowest of high grade or low grade + 10’ |  |  |  |

| IBC S-2 Type IIB | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |  |
| --- | --- | --- | --- | --- |
|  | 4 stories, 55’ | 5 stories, 75’ | 5 stories, 75’ |  |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 26,000 | 1.75 | 2 | 292,500 (1-story w/ sprinklers Unlimited) |
|  | Basements: 45,500 (unsprinklered); 123,500 (sprinklered) |  |  |  |
|  | Specific Fire Resistance: - Structural frame = NR - Bearing walls = NR (exterior or interior) - Interior nonbearing walls & partitions = NR - Floors = NR - Roofs = NR, heavy timber OK - Fire barriers between fire areas = 2 hours - Fire walls = 2 hours (based on occupancy) - Corridors = 1 hour (unsprinklered) @ occupant load > 30; NR (sprinklered) - 4-story unenclosed escalator or non-MOE stair allowed |  |  |  |
|  | Specific Fire Alarm Threshold: n/a |  |  |  |
|  | Specific Sprinkler Threshold: All buildings w/ S-2 occupancies. 5000 sq ft exemption for commercial truck/bus parking |  |  |  |
|  | Podium Buildings: Separate bldgs for area & number of stories; height measured fr grade plane |  |  |  |

| UBC S-3 Type II-N | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |  |
| --- | --- | --- | --- | --- |
|  | 2 stories, 55’ | 3 stories, 55’ | 3 stories, 55’ (2 stories, 55’ if spr’s used for area) |  |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 12,000 | 2 | 2 | 96,000 (48,000 if spr’s used for stories) (2-stories w/ sprinklers Unlimited) |
|  | Basements: 24,000 (unsprinklered); 72,000 (sprinklered) |  |  |  |
|  | Specific Fire Resistance: - Structural frame = NR - Bearing walls = NR (exterior or interior) - Interior nonbearing walls & partitions = NR - Floors = NR - Roofs = NR - Area separation walls = 2 hours (based on type of construction) - Corridors = 1 hour, triggered by travel distance or >1 intervening room - Hallways = NR, treated as intervening room - Unlimited number of stories unenclosed escalator allowed |  |  |  |
|  | Specific Fire Alarm Threshold: n/a |  |  |  |
|  | Specific Sprinkler Threshold: n/a |  |  |  |
|  | Podium Buildings: Separate bldgs for area and number of stories; height measured from lowest of high grade or low grade + 10’ |  |  |  |

| IBC S-2 Type IIIA | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |  |
| --- | --- | --- | --- | --- |
|  | 4 stories, 65’ | 5 stories, 85’ | 5 stories, 85’ |  |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 39,000 | 1.75 | 2 | 438,750 (1-story w/ sprinklers Unlimited) |
|  | Basements: 68,250 (unsprinklered); 185,250 (sprinklered) |  |  |  |
|  | Specific Fire Resistance: - Structural frame = 1 hour - Bearing walls = 2 hour (exterior); 1 hour (interior) - Interior nonbearing walls & partitions = NR - Floors = 1 hour - Roofs = 1 hour; heavy timber OK; NR or fire-retardant treated wood OK if ≥ 20’ above floor immediately below; - Fire barriers between fire areas = 2 hours - Fire walls = 2 hours (based on occupancy) - Corridors = 1 hour (unsprinklered) @ occupant load > 30; NR (sprinklered) - 4-story unenclosed escalator or non-MOE stair allowed |  |  |  |
|  | Specific Fire Alarm Threshold: n/a |  |  |  |
|  | Specific Sprinkler Threshold: All buildings w/ S-2 occupancies. 5000 sq ft exemption for commercial truck/bus parking |  |  |  |
|  | Podium Buildings: Separate bldgs for area & number of stories; height measured fr grade plane |  |  |  |

| UBC S-3 Type III-1 hour | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |  |
| --- | --- | --- | --- | --- |
|  | 4 stories, 65’ | 5 stories, 65’ | 5 stories, 65’ (4 stories, 65’ if spr’s used for area) |  |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 18,000 | 2 | 2 | 144,000 (72,000 if spr’s used for stories) (2-stories w/ sprinklers Unlimited) |
|  | Basements: 36,000 (unsprinklered); 108,000 (sprinklered) |  |  |  |
|  | Specific Fire Resistance: - Structural frame = 1 hour - Bearing walls = 4 hour NC (exterior); 1 hour (interior) - Interior nonbearing walls & partitions = 1 hour - Floors = 1 hour - Roofs = 1 hour - Area separation walls = 4 hours (based on type of construction) - Corridors = 1 hour, triggered by travel distance or >1 intervening room - Hallways = NR, treated as intervening room - Unlimited number of stories unenclosed escalator allowed |  |  |  |
|  | Specific Fire Alarm Threshold: n/a |  |  |  |
|  | Specific Sprinkler Threshold: n/a |  |  |  |
|  | Podium Buildings: Separate bldgs for area and number of stories; height measured from lowest of high grade or low grade + 10’ |  |  |  |

| IBC S-2 Type IIIB | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |  |
| --- | --- | --- | --- | --- |
|  | 4 stories, 55’ | 5 stories, 75’ | 5 stories, 75’ |  |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 26,000 | 1.75 | 2 | 292,500 (1-story w/ sprinklers Unlimited) |
|  | Basements: 45,500 (unsprinklered); 123,500 (sprinklered) |  |  |  |
|  | Specific Fire Resistance: - Structural frame = NR - Bearing walls = 2 hours (exterior); NR (interior) - Interior nonbearing walls & partitions = NR - Floors = NR - Roofs = NR, heavy timber OK - Fire barriers between fire areas = 2 hours - Fire walls = 2 hours (based on occupancy) - Corridors = 1 hour (unsprinklered) @ occupant load > 30; NR (sprinklered) - 4-story unenclosed escalator or non-MOE stair allowed |  |  |  |
|  | Specific Fire Alarm Threshold: n/a |  |  |  |
|  | Specific Sprinkler Threshold: All buildings w/ S-2 occupancies. 5000 sq ft exemption for commercial truck/bus parking |  |  |  |
|  | Podium Buildings: Separate bldgs for area & number of stories; A’s occ ld < 300; height measured fr grade plane |  |  |  |

| UBC S-3 Type III-N | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |  |
| --- | --- | --- | --- | --- |
|  | 2 stories, 55’ | 3 stories, 55’ | 3 stories, 55’ (2 stories, 55’ if spr’s used for area) |  |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 12,000 | 2 | 2 | 96,000 (48,000 if spr’s used for stories) (2-stories w/ sprinklers Unlimited) |
|  | Basements: 24,000 (unsprinklered); 72,000 (sprinklered) |  |  |  |
|  | Specific Fire Resistance: - Structural frame = NR - Bearing walls = 4 hours, N/C (exterior); NR (interior) - Interior nonbearing walls & partitions = NR - Floors = NR - Roofs = NR - Area separation walls = 4 hours (based on type of construction) - Corridors = 1 hour, triggered by travel distance or >1 intervening room - Hallways = NR, treated as intervening room - Unlimited number of stories unenclosed escalator allowed |  |  |  |
|  | Specific Fire Alarm Threshold: n/a |  |  |  |
|  | Specific Sprinkler Threshold: n/a |  |  |  |
|  | Podium Buildings: Separate bldgs for area and number of stories; height measured from lowest of high grade or low grade + 10’ |  |  |  |

| IBC S-2 Type IV HT | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |  |
| --- | --- | --- | --- | --- |
|  | 5 stories, 65’ | 6 stories, 85’ | 6 stories, 85’ |  |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 38,500 | 1.75 | 2 | 433,125 (1-story w/ sprinklers Unlimited) |
|  | Basements: 67,375 (unsprinklered); 182,875 (sprinklered) |  |  |  |
|  | Specific Fire Resistance: - Structural frame = HT - Bearing walls = 2 hour (exterior); 1 hour or HT (interior) - Interior nonbearing walls & partitions = 1 hour or solid wood - Floors = HT - Roofs = HT - Fire barriers between fire areas = 2 hours - Fire walls = 2 hours (based on occupancy) - Corridors = 1 hour (unsprinklered) @ occupant load > 30; NR (sprinklered) - 4-story unenclosed escalator or non-MOE stair allowed |  |  |  |
|  | Specific Fire Alarm Threshold: n/a |  |  |  |
|  | Specific Sprinkler Threshold: All buildings w/ S-2 occupancies. 5000 sq ft exemption for commercial truck/bus parking |  |  |  |
|  | Podium Buildings: Separate bldgs for area & number of stories; height measured fr grade plane |  |  |  |

| UBC S-3 Type IV HT | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |  |
| --- | --- | --- | --- | --- |
|  | 4 stories, 65’ | 5 stories, 65’ | 5 stories, 65’ (4 stories, 65’ if spr’s used for area) |  |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 18,000 | 2 | 2 | 144,000 (72,000 if spr’s used for stories) (2-stories w/ sprinklers Unlimited) |
|  | Basements: 36,000 (unsprinklered); 108,000 (sprinklered) |  |  |  |
|  | Specific Fire Resistance: - Structural frame = 1 hour or HT - Bearing walls = 4 hour NC (exterior); 1 hour (interior) - Interior nonbearing walls & partitions = 1 hour or HT - Floors = HT - Roofs = HT - Area separation walls = 4 hours (based on type of construction) - Corridors = 1 hour, triggered by travel distance or >1 intervening room - Hallways = NR, treated as intervening room - Unlimited number of stories unenclosed escalator allowed |  |  |  |
|  | Specific Fire Alarm Threshold: n/a |  |  |  |
|  | Specific Sprinkler Threshold: n/a |  |  |  |
|  | Podium Buildings: Separate bldgs for area and number of stories; height measured from lowest of high grade or low grade + 10’ |  |  |  |

| IBC S-2 Type VA | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |  |
| --- | --- | --- | --- | --- |
|  | 4 stories, 50’ | 5 stories, 70’ | 5 stories, 70’ |  |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 21,000 | 1.75 | 2 | 236,250 |
|  | Basements: 36,750 (unsprinklered); 99,750 (sprinklered) |  |  |  |
|  | Specific Fire Resistance: - Structural frame = 1 hour - Bearing walls = 1 hour (exterior or interior) - Interior nonbearing walls & partitions = NR - Floors = 1 hour - Roofs = 1 hour; heavy timber OK; NR or fire-retardant treated wood OK if ≥ 20’ above floor immediately below; - Fire barriers between fire areas = 2 hours - Fire walls = 2 hours (based on occupancy) - Corridors = 1 hour (unsprinklered) @ occupant load > 30; NR (sprinklered) - 4-story unenclosed escalator or non-MOE stair allowed |  |  |  |
|  | Specific Fire Alarm Threshold: n/a |  |  |  |
|  | Specific Sprinkler Threshold: All buildings w/ S-2 occupancies. 5000 sq ft exemption for commercial truck/bus parking |  |  |  |
|  | Podium Buildings: Separate bldgs for area & number of stories; height measured fr grade plane |  |  |  |

| UBC S-3 Type V-1 hour | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |  |
| --- | --- | --- | --- | --- |
|  | 3 stories, 50’ | 4 stories, 50’ | 4 stories, 50’ (3 stories, 50’ if spr’s used for area) |  |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 14,000 | 2 | 2 | 112,000 (56,000 if spr’s used for stories) (2-stories w/ sprinklers Unlimited) |
|  | Basements: 28,000 (unsprinklered); 84,000 (sprinklered) |  |  |  |
|  | Specific Fire Resistance: - Structural frame = 1 hour - Bearing walls = 1 hour (exterior or interior) - Interior nonbearing walls & partitions = 1 hour - Floors = 1 hour - Roofs = 1 hour - Area separation walls = 2 hours (based on type of construction) - Corridors = 1 hour, triggered by travel distance or >1 intervening room - Hallways = NR, treated as intervening room - Unlimited number of stories unenclosed escalator allowed |  |  |  |
|  | Specific Fire Alarm Threshold: n/a |  |  |  |
|  | Specific Sprinkler Threshold: n/a |  |  |  |
|  | Podium Buildings: Separate bldgs for area and number of stories; height measured from lowest of high grade or low grade + 10’ |  |  |  |

| IBC S-2 Type VB | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |  |
| --- | --- | --- | --- | --- |
|  | 2 stories, 40’ | 3 stories, 60’ | 3 stories, 60’ |  |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 13,500 | 1.75 | 2 | 151,875 |
|  | Basements: 23,625 (unsprinklered); 64,125 (sprinklered) |  |  |  |
|  | Specific Fire Resistance: - Structural frame = NR - Bearing walls = NR (exterior & interior) - Interior nonbearing walls & partitions = NR - Floors = NR - Roofs = NR - Fire barriers between fire areas = 2 hours - Fire walls = 2 hours (based on occupancy) - Corridors = 1 hour (unsprinklered) @ occupant load > 30; NR (sprinklered) - 4-story unenclosed escalator or non-MOE stair allowed) |  |  |  |
|  | Specific Fire Alarm Threshold: n/a |  |  |  |
|  | Specific Sprinkler Threshold: All buildings w/ S-2 occupancies. 5000 sq ft exemption for commercial truck/bus parking |  |  |  |
|  | Podium Buildings: Separate bldgs for area & number of stories; height measured fr grade plane |  |  |  |

| UBC S-3 Type V-N | Max Height w/o Sprinklers Thresholds | Max Height w/ Sprinklers Thresholds | Max Building Height |  |
| --- | --- | --- | --- | --- |
|  | 2 stories, 40’ | 3 stories, 40’ | 3 stories, 40’ (2 stories, 40’ if spr’s used for area) |  |
|  | Allowable Area per Table | Frontage Increase | Sprinkler Increase | Max Building Area |
|  | 8,000 | 2 | 2 | 64,000 (32,000 if spr’s used for stories) (2-stories w/ sprinklers Unlimited) |
|  | Basements: 16,000 (unsprinklered); 48,000 (sprinklered) |  |  |  |
|  | Specific Fire Resistance: - Structural frame = NR - Bearing walls = NR (exterior or interior) - Interior nonbearing walls & partitions = NR - Floors = NR - Roofs = NR - Area separation walls = 2 hours (based on type of construction) - Corridors = 1 hour, triggered by travel distance or >1 intervening room - Hallways = NR, treated as intervening room - Unlimited number of stories unenclosed escalator allowed |  |  |  |
|  | Specific Fire Alarm Threshold: n/a |  |  |  |
|  | Specific Sprinkler Threshold: n/a |  |  |  |
|  | Podium Buildings: Separate bldgs for area and number of stories; height measured from lowest of high grade or low grade + 10’ |  |  |  |