## One Story
Cells identified at Dec 10 - 11 meeting that result in total building area that is more than 10% greater than total area permitted by largest legacy code.
IBC more than 10% greater than largest legacy code area.
IBC more than 10% less than largest legacy code area.
LNP - Not pemitted by legacy codes but permitted by IBC
INF - Infinity
Ratio of IBC area to largest legacy code area for condition stated:
[19 empty] | Without sprinklers | [11 empty] | With sprinklers
[10 empty] | Tabular area of code | [8 empty] | Open space | [11 empty] | Open space
[10 empty] | IBC | NBC | SBC | UBC | [5 empty] | < 20 | [5 empty] | 40 | [5 empty] | < 20 | [5 empty] | 40
[10 empty] | Tabular Areas (TA) |  |  |  | TA + < 20 ft. open space (no sprinklers) | [5 empty] | TA + 40 ft. open space (no sprinklers) | [5 empty] | TA + < 20 ft. open space + sprinklers | [5 empty] | TA + 40 ft. open space + sprinklers
|  | IBC | NBC | SBC | UBC | IBC | NBC | SBC | UBC | IBC | NBC | SBC | UBC | IBC | NBC | SBC | UBC | Largest Legacy | Ratio IBC/LL | IBC | NBC | SBC | UBC | Largest Legacy | Ratio IBC/LL | IBC | NBC | SBC | UBC | Largest Legacy | Ratio IBC/LL | IBC | NBC | SBC | UBC | Largest Legacy | Ratio IBC/LL
Occup. | Type Const. | Area Increase for Sprinklers? |  |  |  | Ht. | Ht. | Ht. | Ht. | Area | Area | Area | Area | Area | Area | Area | Area | Area |  | Area | Area | Area | Area | Area |  | Area | Area | Area | Area | Area |  | Area | Area | Area | Area | Area
A-1 | IB | Y | Y | Y | Y | 5 | 5 | UL | 4 | UL | 19950 | UL | 29900 | UL | 19950 | UL | 29900 | UL | 1 | UL | 49875 | UL | 59800 | UL | 1 | UL | 59850 | UL | 89700 | UL | 1 | UL | 89775 | UL | 179400 | UL | 1
| IIA | Y | Y | Y | Y | 3 | 3 | 4 | 2 | 15500 | 13125 | 12000 | 13500 | 15500 | 13125 | 12000 | 13500 | 13500 | 1.1481 | 27125 | 32812.5 | 24000 | 27000 | 32812.5 | 0.82667 | 62000 | 39375 | 36000 | 40500 | 40500 | 1.5309 | 73625 | 59062.5 | 48000 | 81000 | 81000 | 0.90895
| IIB | Y | Y | Y | Y | 2 | 2 | 2 | NP | 8500 | 8400 | 8000 | NP | 8500 | 8400 | 8000 | NP | 8400 | 1.0119 | 14875 | 21000 | 16000 | NP | 21000 | 0.70833 | 34000 | 25200 | 24000 | NP | 25200 | 1.3492 | 40375 | 37800 | 32000 | NP | 37800 | 1.0681
| IIIA | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 14000 | 11550 | 12000 | 13500 | 14000 | 11550 | 12000 | 13500 | 13500 | 1.037 | 24500 | 28875 | 24000 | 27000 | 28875 | 0.84848 | 56000 | 34650 | 36000 | 40500 | 40500 | 1.3827 | 66500 | 51975 | 48000 | 81000 | 81000 | 0.82099
| IIIB | Y | Y | Y | Y | 2 | 2 | 2 | NP | 8500 | 8400 | 8000 | NP | 8500 | 8400 | 8000 | NP | 8400 | 1.0119 | 14875 | 21000 | 16000 | NP | 21000 | 0.70833 | 34000 | 25200 | 24000 | NP | 25200 | 1.3492 | 40375 | 37800 | 32000 | NP | 37800 | 1.0681
| IV | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 15000 | 12600 | 12000 | 13500 | 15000 | 12600 | 12000 | 13500 | 13500 | 1.1111 | 26250 | 31500 | 24000 | 27000 | 31500 | 0.83333 | 60000 | 37800 | 36000 | 40500 | 40500 | 1.4815 | 71250 | 56700 | 48000 | 81000 | 81000 | 0.87963
| VA | Y | Y | Y | Y | 2 | 1 | 1 | 2 | 11500 | 8925 | 7500 | 10500 | 11500 | 8925 | 7500 | 10500 | 10500 | 1.0952 | 20125 | 22312.5 | 15000 | 21000 | 22312.5 | 0.90196 | 46000 | 26775 | 22500 | 31500 | 31500 | 1.4603 | 54625 | 40162.5 | 30000 | 63000 | 63000 | 0.86706
| VB | Y | Y | Y | Y | 1 | 1 | 1 | NP | 5500 | 4200 | 5000 | NP | 5500 | 4200 | 5000 | NP | 5000 | 1.1 | 9625 | 10500 | 10000 | NP | 10500 | 0.91667 | 22000 | 12600 | 15000 | NP | 15000 | 1.4667 | 26125 | 18900 | 20000 | NP | 20000 | 1.3062
A-2 | IB | Y | Y | Y | Y | 11 | 3 | UL | 12 | UL | 5700 | UL | 29900 | UL | 5700 | UL | 29900 | UL | 1 | UL | 14250 | UL | 59800 | UL | 1 | UL | 17100 | UL | 89700 | UL | 1 | UL | 25650 | UL | 179400 | UL | 1
| IIA | Y | Y | Y | Y | 3 | 2 | 2 | 2 | 15500 | 3750 | 12000 | 13500 | 15500 | 3750 | 12000 | 13500 | 13500 | 1.1481 | 27125 | 9375 | 24000 | 27000 | 27000 | 1.0046 | 62000 | 11250 | 36000 | 40500 | 40500 | 1.5309 | 73625 | 16875 | 48000 | 81000 | 81000 | 0.90895
| IIB | Y | Y | Y | Y | 2 | 1 | 2 | 1 | 9500 | 2400 | 8000 | 9100 | 9500 | 2400 | 8000 | 9100 | 9100 | 1.044 | 16625 | 6000 | 16000 | 18200 | 18200 | 0.91346 | 38000 | 7200 | 24000 | 27300 | 27300 | 1.3919 | 45125 | 10800 | 32000 | 54600 | 54600 | 0.82647
| IIIA | Y | Y | Y | Y | 3 | 2 | 2 | 2 | 14000 | 3300 | 12000 | 13500 | 14000 | 3300 | 12000 | 13500 | 13500 | 1.037 | 24500 | 8250 | 24000 | 27000 | 27000 | 0.90741 | 56000 | 9900 | 36000 | 40500 | 40500 | 1.3827 | 66500 | 14850 | 48000 | 81000 | 81000 | 0.82099
| IIIB | Y | Y | Y | Y | 2 | 1 | 2 | 1 | 9500 | 2400 | 8000 | 9100 | 9500 | 2400 | 8000 | 9100 | 9100 | 1.044 | 16625 | 6000 | 16000 | 18200 | 18200 | 0.91346 | 38000 | 7200 | 24000 | 27300 | 27300 | 1.3919 | 45125 | 10800 | 32000 | 54600 | 54600 | 0.82647
| IV | Y | Y | Y | Y | 3 | 2 | 2 | 2 | 15000 | 3600 | 12000 | 13500 | 15000 | 3600 | 12000 | 13500 | 13500 | 1.1111 | 26250 | 9000 | 24000 | 27000 | 27000 | 0.97222 | 60000 | 10800 | 36000 | 40500 | 40500 | 1.4815 | 71250 | 16200 | 48000 | 81000 | 81000 | 0.87963
| VA | Y | Y | Y | Y | 2 | 1 | 1 | 2 | 11500 | 2550 | 7500 | 10500 | 11500 | 2550 | 7500 | 10500 | 10500 | 1.0952 | 20125 | 6375 | 15000 | 21000 | 21000 | 0.95833 | 46000 | 7650 | 22500 | 31500 | 31500 | 1.4603 | 54625 | 11475 | 30000 | 63000 | 63000 | 0.86706
| VB | Y | Y | Y | Y | 1 | 1 | 1 | 1 | 6000 | 1200 | 5000 | 6000 | 6000 | 1200 | 5000 | 6000 | 6000 | 1 | 10500 | 3000 | 10000 | 12000 | 12000 | 0.875 | 24000 | 3600 | 15000 | 18000 | 18000 | 1.3333 | 28500 | 5400 | 20000 | 36000 | 36000 | 0.79167
A-3 | IB | Y | Y | Y | Y | 11 | 5 | UL | 12 | UL | 19950 | UL | 29900 | UL | 19950 | UL | 29900 | UL | 1 | UL | 49875 | UL | 59800 | UL | 1 | UL | 59850 | UL | 89700 | UL | 1 | UL | 89775 | UL | 179400 | UL | 1
| IIA | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 15500 | 13125 | 12000 | 13500 | 15500 | 13125 | 12000 | 13500 | 13500 | 1.1481 | 27125 | 32812.5 | 24000 | 27000 | 32812.5 | 0.82667 | 62000 | 39375 | 36000 | 40500 | 40500 | 1.5309 | 73625 | 59062.5 | 48000 | 81000 | 81000 | 0.90895
| IIB | Y | Y | Y | Y | 2 | 2 | 2 | 1 | 9500 | 8400 | 8000 | 9100 | 9500 | 8400 | 8000 | 9100 | 9100 | 1.044 | 16625 | 21000 | 16000 | 18200 | 21000 | 0.79167 | 38000 | 25200 | 24000 | 27300 | 27300 | 1.3919 | 45125 | 37800 | 32000 | 54600 | 54600 | 0.82647
| IIIA | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 14000 | 11550 | 12000 | 13500 | 14000 | 11550 | 12000 | 13500 | 13500 | 1.037 | 24500 | 28875 | 24000 | 27000 | 28875 | 0.84848 | 56000 | 34650 | 36000 | 40500 | 40500 | 1.3827 | 66500 | 51975 | 48000 | 81000 | 81000 | 0.82099
| IIIB | Y | Y | Y | Y | 2 | 2 | 2 | 1 | 9500 | 8400 | 8000 | 9100 | 9500 | 8400 | 8000 | 9100 | 9100 | 1.044 | 16625 | 21000 | 16000 | 18200 | 21000 | 0.79167 | 38000 | 25200 | 24000 | 27300 | 27300 | 1.3919 | 45125 | 37800 | 32000 | 54600 | 54600 | 0.82647
| IV | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 15000 | 12600 | 12000 | 13500 | 15000 | 12600 | 12000 | 13500 | 13500 | 1.1111 | 26250 | 31500 | 24000 | 27000 | 31500 | 0.83333 | 60000 | 37800 | 36000 | 40500 | 40500 | 1.4815 | 71250 | 56700 | 48000 | 81000 | 81000 | 0.87963
| VA | Y | Y | Y | Y | 2 | 1 | 2 | 2 | 11500 | 8925 | 7500 | 10500 | 11500 | 8925 | 7500 | 10500 | 10500 | 1.0952 | 20125 | 22312.5 | 15000 | 21000 | 22312.5 | 0.90196 | 46000 | 26775 | 22500 | 31500 | 31500 | 1.4603 | 54625 | 40162.5 | 30000 | 63000 | 63000 | 0.86706
| VB | Y | Y | Y | Y | 1 | 1 | 2 | 1 | 6000 | 4200 | 5000 | 6000 | 6000 | 4200 | 5000 | 6000 | 6000 | 1 | 10500 | 10500 | 10000 | 12000 | 12000 | 0.875 | 24000 | 12600 | 15000 | 18000 | 18000 | 1.3333 | 28500 | 18900 | 20000 | 36000 | 36000 | 0.79167
A-4 | IB | Y | Y | Y | Y | 11 | 5 | UL | 12 | UL | 19950 | UL | 29900 | UL | 19950 | UL | 29900 | UL | 1 | UL | 49875 | UL | 59800 | UL | 1 | UL | 59850 | UL | 89700 | UL | 1 | UL | 89775 | UL | 179400 | UL | 1
| IIA | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 15500 | 13125 | 12000 | 13500 | 15500 | 13125 | 12000 | 13500 | 13500 | 1.1481 | 27125 | 32812.5 | 24000 | 27000 | 32812.5 | 0.82667 | 62000 | 39375 | 36000 | 40500 | 40500 | 1.5309 | 73625 | 59062.5 | 48000 | 81000 | 81000 | 0.90895
| IIB | Y | Y | Y | Y | 2 | 2 | 2 | 1 | 9500 | 8400 | 8000 | 9100 | 9500 | 8400 | 8000 | 9100 | 9100 | 1.044 | 16625 | 21000 | 16000 | 18200 | 21000 | 0.79167 | 38000 | 25200 | 24000 | 27300 | 27300 | 1.3919 | 45125 | 37800 | 32000 | 54600 | 54600 | 0.82647
| IIIA | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 14000 | 11550 | 12000 | 13500 | 14000 | 11550 | 12000 | 13500 | 13500 | 1.037 | 24500 | 28875 | 24000 | 27000 | 28875 | 0.84848 | 56000 | 34650 | 36000 | 40500 | 40500 | 1.3827 | 66500 | 51975 | 48000 | 81000 | 81000 | 0.82099
| IIIB | Y | Y | Y | Y | 2 | 2 | 2 | 1 | 9500 | 8400 | 8000 | 9100 | 9500 | 8400 | 8000 | 9100 | 9100 | 1.044 | 16625 | 21000 | 16000 | 18200 | 21000 | 0.79167 | 38000 | 25200 | 24000 | 27300 | 27300 | 1.3919 | 45125 | 37800 | 32000 | 54600 | 54600 | 0.82647
| IV | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 15000 | 12600 | 12000 | 13500 | 15000 | 12600 | 12000 | 13500 | 13500 | 1.1111 | 26250 | 31500 | 24000 | 27000 | 31500 | 0.83333 | 60000 | 37800 | 36000 | 40500 | 40500 | 1.4815 | 71250 | 56700 | 48000 | 81000 | 81000 | 0.87963
| VA | Y | Y | Y | Y | 2 | 1 | 1 | 2 | 11500 | 8925 | 7500 | 10500 | 11500 | 8925 | 7500 | 10500 | 10500 | 1.0952 | 20125 | 22312.5 | 15000 | 21000 | 22312.5 | 0.90196 | 46000 | 26775 | 22500 | 31500 | 31500 | 1.4603 | 54625 | 40162.5 | 30000 | 63000 | 63000 | 0.86706
| VB | Y | Y | Y | Y | 1 | 1 | 1 | 1 | 6000 | 4200 | 5000 | 6000 | 6000 | 4200 | 5000 | 6000 | 6000 | 1 | 10500 | 10500 | 10000 | 12000 | 12000 | 0.875 | 24000 | 12600 | 15000 | 18000 | 18000 | 1.3333 | 28500 | 18900 | 20000 | 36000 | 36000 | 0.79167
A-5 | IB | Y | Y | Y | Y | UL |  | UL | 12 | UL |  | UL | 29000 | UL | 0 | UL | 29000 | UL | 1 | UL | 0 | UL | 58000 | UL | 1 | UL | 0 | UL | 87000 | UL | 1 | UL | 0 | UL | 174000 | UL | 1
| IIA | Y | Y | Y | Y | UL |  | 2 | 2 | UL |  | 12000 | 13500 | UL | 0 | 12000 | 13500 | 13500 | INF | UL | 0 | 24000 | 27000 | 27000 | INF | UL | 0 | 36000 | 40500 | 40500 | INF | UL | 0 | 48000 | 81000 | 81000 | INF
| IIB | Y | Y | Y | Y | UL |  | 2 | 1 | UL |  | 8000 | 9100 | UL | 0 | 8000 | 9100 | 9100 | INF | UL | 0 | 16000 | 18200 | 18200 | INF | UL | 0 | 24000 | 27300 | 27300 | INF | UL | 0 | 32000 | 54600 | 54600 | INF
| IIIA | Y | Y | Y | Y | UL |  | 2 | 2 | UL |  | 12000 | 13500 | UL | 0 | 12000 | 13500 | 13500 | INF | UL | 0 | 24000 | 27000 | 27000 | INF | UL | 0 | 36000 | 40500 | 40500 | INF | UL | 0 | 48000 | 81000 | 81000 | INF
| IIIB | Y | Y | Y | Y | UL |  | 2 | 1 | UL |  | 8000 | 9100 | UL | 0 | 8000 | 9100 | 9100 | INF | UL | 0 | 16000 | 18200 | 18200 | INF | UL | 0 | 24000 | 27300 | 27300 | INF | UL | 0 | 32000 | 54600 | 54600 | INF
| IV | Y | Y | Y | Y | UL |  | 2 | 2 | UL |  | 12000 | 13500 | UL | 0 | 12000 | 13500 | 13500 | INF | UL | 0 | 24000 | 27000 | 27000 | INF | UL | 0 | 36000 | 40500 | 40500 | INF | UL | 0 | 48000 | 81000 | 81000 | INF
| VA | Y | Y | Y | Y | UL |  | 1 | 2 | UL |  | 7500 | 10500 | UL | 0 | 7500 | 10500 | 10500 | INF | UL | 0 | 15000 | 21000 | 21000 | INF | UL | 0 | 22500 | 31500 | 31500 | INF | UL | 0 | 30000 | 63000 | 63000 | INF
| VB | Y | Y | Y | Y | UL |  | 1 | 1 | UL |  | 5000 | 6000 | UL | 0 | 5000 | 6000 | 6000 | INF | UL | 0 | 10000 | 12000 | 12000 | INF | UL | 0 | 15000 | 18000 | 18000 | INF | UL | 0 | 20000 | 36000 | 36000 | INF
B | IB | Y | Y | Y | Y | 11 | 7 | UL | 12 | UL | 34200 | UL | 39900 | UL | 34200 | UL | 39900 | UL | 1 | UL | 85500 | UL | 79800 | UL | 1 | UL | 102600 | UL | 119700 | UL | 1 | UL | 153900 | UL | 239400 | UL | 1
| IIA | Y | Y | Y | Y | 5 | 5 | 5 | 4 | 37500 | 22500 | 25500 | 18000 | 37500 | 22500 | 25500 | 18000 | 25500 | 1.4706 | 65625 | 56250 | 51000 | 36000 | 56250 | 1.1667 | 150000 | 67500 | 76500 | 54000 | 76500 | 1.9608 | 178125 | 101250 | 102000 | 108000 | 108000 | 1.6493
| IIB | Y | Y | Y | Y | 4 | 3 | 5 | 2 | 23000 | 14400 | 17000 | 12000 | 23000 | 14400 | 17000 | 12000 | 17000 | 1.3529 | 40250 | 36000 | 34000 | 24000 | 36000 | 1.1181 | 92000 | 43200 | 51000 | 36000 | 51000 | 1.8039 | 109250 | 64800 | 68000 | 72000 | 72000 | 1.5174
| IIIA | Y | Y | Y | Y | 5 | 4 | 5 | 4 | 28500 | 19800 | 21000 | 18000 | 28500 | 19800 | 21000 | 18000 | 21000 | 1.3571 | 49875 | 49500 | 42000 | 36000 | 49500 | 1.0076 | 114000 | 59400 | 63000 | 54000 | 63000 | 1.8095 | 135375 | 89100 | 84000 | 108000 | 108000 | 1.2535
| IIIB | Y | Y | Y | Y | 4 | 3 | 5 | 2 | 19000 | 14400 | 14000 | 12000 | 19000 | 14400 | 14000 | 12000 | 14400 | 1.3194 | 33250 | 36000 | 28000 | 24000 | 36000 | 0.92361 | 76000 | 43200 | 42000 | 36000 | 43200 | 1.7593 | 90250 | 64800 | 56000 | 72000 | 72000 | 1.2535
| IV | Y | Y | Y | Y | 5 | 5 | 5 | 4 | 36000 | 21600 | 25500 | 18000 | 36000 | 21600 | 25500 | 18000 | 25500 | 1.4118 | 63000 | 54000 | 51000 | 36000 | 54000 | 1.1667 | 144000 | 64800 | 76500 | 54000 | 76500 | 1.8824 | 171000 | 97200 | 102000 | 108000 | 108000 | 1.5833
| VA | Y | Y | Y | Y | 3 | 3 | 2 | 3 | 18000 | 15300 | 13500 | 14000 | 18000 | 15300 | 13500 | 14000 | 15300 | 1.1765 | 31500 | 38250 | 27000 | 28000 | 38250 | 0.82353 | 72000 | 45900 | 40500 | 42000 | 45900 | 1.5686 | 85500 | 68850 | 54000 | 84000 | 84000 | 1.0179
| VB | Y | Y | Y | Y | 2 | 2 | 2 | 2 | 9000 | 7200 | 9000 | 8000 | 9000 | 7200 | 9000 | 8000 | 9000 | 1 | 15750 | 18000 | 18000 | 16000 | 18000 | 0.875 | 36000 | 21600 | 27000 | 24000 | 27000 | 1.3333 | 42750 | 32400 | 36000 | 48000 | 48000 | 0.89062
E | IB | Y | Y | Y | Y | 11 | 5 | UL | 4 | UL | 34200 | UL | 45200 | UL | 34200 | UL | 45200 | UL | 1 | UL | 85500 | UL | 90400 | UL | 1 | UL | 102600 | UL | 135600 | UL | 1 | UL | 153900 | UL | 271200 | UL | 1
| IIA | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 26500 | 22500 | 18000 | 20200 | 26500 | 22500 | 18000 | 20200 | 22500 | 1.1778 | 46375 | 56250 | 36000 | 40400 | 56250 | 0.82444 | 106000 | 67500 | 54000 | 60600 | 67500 | 1.5704 | 125875 | 101250 | 72000 | 121200 | 121200 | 1.0386
| IIB | Y | Y | Y | Y | 2 | 2 | 1 | 1 | 14500 | 14400 | 12000 | 13500 | 14500 | 14400 | 12000 | 13500 | 14400 | 1.0069 | 25375 | 36000 | 24000 | 27000 | 36000 | 0.70486 | 58000 | 43200 | 36000 | 40500 | 43200 | 1.3426 | 68875 | 64800 | 48000 | 81000 | 81000 | 0.85031
| IIIA | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 23500 | 19800 | 18000 | 20200 | 23500 | 19800 | 18000 | 20200 | 20200 | 1.1634 | 41125 | 49500 | 36000 | 40400 | 49500 | 0.83081 | 94000 | 59400 | 54000 | 60600 | 60600 | 1.5512 | 111625 | 89100 | 72000 | 121200 | 121200 | 0.921
| IIIB | Y | Y | Y | Y | 2 | 2 | 1 | 1 | 14500 | 14400 | 12000 | 13500 | 14500 | 14400 | 12000 | 13500 | 14400 | 1.0069 | 25375 | 36000 | 24000 | 27000 | 36000 | 0.70486 | 58000 | 43200 | 36000 | 40500 | 43200 | 1.3426 | 68875 | 64800 | 48000 | 81000 | 81000 | 0.85031
| IV | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 25500 | 21600 | 18000 | 20200 | 25500 | 21600 | 18000 | 20200 | 21600 | 1.1806 | 44625 | 54000 | 36000 | 40400 | 54000 | 0.82639 | 102000 | 64800 | 54000 | 60600 | 64800 | 1.5741 | 121125 | 97200 | 72000 | 121200 | 121200 | 0.99938
| VA | Y | Y | Y | Y | 1 | 1 | 2 | 2 | 18500 | 15300 | 12000 | 15700 | 18500 | 15300 | 12000 | 15700 | 15700 | 1.1783 | 32375 | 38250 | 24000 | 31400 | 38250 | 0.84641 | 74000 | 45900 | 36000 | 47100 | 47100 | 1.5711 | 87875 | 68850 | 48000 | 94200 | 94200 | 0.93286
| VB | Y | Y | Y | Y | 1 | 1 | 1 | 1 | 9500 | 7200 | 8000 | 9100 | 9500 | 7200 | 8000 | 9100 | 9100 | 1.044 | 16625 | 18000 | 16000 | 18200 | 18200 | 0.91346 | 38000 | 21600 | 24000 | 27300 | 27300 | 1.3919 | 45125 | 32400 | 32000 | 54600 | 54600 | 0.82647
F-1 | IB | Y | Y | Y | Y | 11 | 6 | UL | 12 | UL | 22800 | UL | 39900 | UL | 22800 | UL | 39900 | UL | 1 | UL | 57000 | UL | 79800 | UL | 1 | UL | 68400 | UL | 119700 | UL | 1 | UL | 102600 | UL | 239400 | UL | 1
| IIA | Y | Y | Y | Y | 4 | 4 | 4 | 4 | 25000 | 15000 | 31500 | 18000 | 25000 | 15000 | 31500 | 18000 | 31500 | 0.79365 | 43750 | 37500 | 63000 | 36000 | 63000 | 0.69444 | 100000 | 45000 | 94500 | 54000 | 94500 | 1.0582 | 118750 | 67500 | 126000 | 108000 | 126000 | 0.94246
| IIB | Y | Y | Y | Y | 2 | 2 | 4 | 2 | 15500 | 9600 | 21000 | 12000 | 15500 | 9600 | 21000 | 12000 | 21000 | 0.7381 | 27125 | 24000 | 42000 | 24000 | 42000 | 0.64583 | 62000 | 28800 | 63000 | 36000 | 63000 | 0.98413 | 73625 | 43200 | 84000 | 72000 | 84000 | 0.87649
| IIIA | Y | Y | Y | Y | 3 | 3 | 4 | 4 | 19000 | 13200 | 22500 | 18000 | 19000 | 13200 | 22500 | 18000 | 22500 | 0.84444 | 33250 | 33000 | 45000 | 36000 | 45000 | 0.73889 | 76000 | 39600 | 67500 | 54000 | 67500 | 1.1259 | 90250 | 59400 | 90000 | 108000 | 108000 | 0.83565
| IIIB | Y | Y | Y | Y | 2 | 2 | 4 | 2 | 12000 | 9600 | 15000 | 12000 | 12000 | 9600 | 15000 | 12000 | 15000 | 0.8 | 21000 | 24000 | 30000 | 24000 | 30000 | 0.7 | 48000 | 28800 | 45000 | 36000 | 45000 | 1.0667 | 57000 | 43200 | 60000 | 72000 | 72000 | 0.79167
| IV | Y | Y | Y | Y | 4 | 4 | 6 | 4 | 33500 | 14400 | 31500 | 18000 | 33500 | 14400 | 31500 | 18000 | 31500 | 1.0635 | 58625 | 36000 | 63000 | 36000 | 63000 | 0.93056 | 134000 | 43200 | 94500 | 54000 | 94500 | 1.418 | 159125 | 64800 | 126000 | 108000 | 126000 | 1.2629
| VA | Y | Y | Y | Y | 2 | 2 | 1 | 3 | 14000 | 10200 | 15000 | 14000 | 14000 | 10200 | 15000 | 14000 | 15000 | 0.93333 | 24500 | 25500 | 30000 | 28000 | 30000 | 0.81667 | 56000 | 30600 | 45000 | 42000 | 45000 | 1.2444 | 66500 | 45900 | 60000 | 84000 | 84000 | 0.79167
| VB | Y | Y | Y | Y | 1 | 1 | 1 | 2 | 8500 | 4800 | 10000 | 8000 | 8500 | 4800 | 10000 | 8000 | 10000 | 0.85 | 14875 | 12000 | 20000 | 16000 | 20000 | 0.74375 | 34000 | 14400 | 30000 | 24000 | 30000 | 1.1333 | 40375 | 21600 | 40000 | 48000 | 48000 | 0.84115
F-2 | IB | Y | Y | Y | Y | 11 | 7 | UL | 12 | UL | 34200 | UL | 59900 | UL | 34200 | UL | 59900 | UL | 1 | UL | 85500 | UL | 119800 | UL | 1 | UL | 102600 | UL | 179700 | UL | 1 | UL | 153900 | UL | 359400 | UL | 1
| IIA | Y | Y | Y | Y | 5 | 5 | 4 | 4 | 37500 | 22500 | 31500 | 27000 | 37500 | 22500 | 31500 | 27000 | 31500 | 1.1905 | 65625 | 56250 | 63000 | 54000 | 63000 | 1.0417 | 150000 | 67500 | 94500 | 81000 | 94500 | 1.5873 | 178125 | 101250 | 126000 | 162000 | 162000 | 1.0995
| IIB | Y | Y | Y | Y | 3 | 3 | 4 | 2 | 23000 | 14400 | 21000 | 18000 | 23000 | 14400 | 21000 | 18000 | 21000 | 1.0952 | 40250 | 36000 | 42000 | 36000 | 42000 | 0.95833 | 92000 | 43200 | 63000 | 54000 | 63000 | 1.4603 | 109250 | 64800 | 84000 | 108000 | 108000 | 1.0116
| IIIA | Y | Y | Y | Y | 4 | 4 | 4 | 4 | 28500 | 19800 | 22500 | 27000 | 28500 | 19800 | 22500 | 27000 | 27000 | 1.0556 | 49875 | 49500 | 45000 | 54000 | 54000 | 0.92361 | 114000 | 59400 | 67500 | 81000 | 81000 | 1.4074 | 135375 | 89100 | 90000 | 162000 | 162000 | 0.83565
| IIIB | Y | Y | Y | Y | 3 | 3 | 4 | 2 | 18000 | 14400 | 15000 | 18000 | 18000 | 14400 | 15000 | 18000 | 18000 | 1 | 31500 | 36000 | 30000 | 36000 | 36000 | 0.875 | 72000 | 43200 | 45000 | 54000 | 54000 | 1.3333 | 85500 | 64800 | 60000 | 108000 | 108000 | 0.79167
| IV | Y | Y | Y | Y | 5 | 5 | 6 | 4 | 50500 | 21600 | 31500 | 27000 | 50500 | 21600 | 31500 | 27000 | 31500 | 1.6032 | 88375 | 54000 | 63000 | 54000 | 63000 | 1.4028 | 202000 | 64800 | 94500 | 81000 | 94500 | 2.1376 | 239875 | 97200 | 126000 | 162000 | 162000 | 1.4807
| VA | Y | Y | Y | Y | 3 | 3 | 1 | 3 | 21000 | 15300 | 15000 | 21000 | 21000 | 15300 | 15000 | 21000 | 21000 | 1 | 36750 | 38250 | 30000 | 42000 | 42000 | 0.875 | 84000 | 45900 | 45000 | 63000 | 63000 | 1.3333 | 99750 | 68850 | 60000 | 126000 | 126000 | 0.79167
| VB | Y | Y | Y | Y | 2 | 2 | 1 | 2 | 13000 | 7200 | 10000 | 12000 | 13000 | 7200 | 10000 | 12000 | 12000 | 1.0833 | 22750 | 18000 | 20000 | 24000 | 24000 | 0.94792 | 52000 | 21600 | 30000 | 36000 | 36000 | 1.4444 | 61750 | 32400 | 40000 | 72000 | 72000 | 0.85764
H-1 | 1A | N | N | Y | N | 1 | 1 | 1 | 1 | 21000 | 14400 | 5000 | 15000 | 21000 | 14400 | 5000 | 15000 | 15000 | 1.4 | 36750 | 36000 | 10000 | 30000 | 36000 | 1.0208 | 21000 | 14400 | 15000 | 15000 | 15000 | 1.4 | 36750 | 36000 | 20000 | 30000 | 36000 | 1.0208
| IB | N | N | Y | N | 1 | 1 | 1 | 1 | 16500 | 11400 | 4000 | 12400 | 16500 | 11400 | 4000 | 12400 | 12400 | 1.3306 | 28875 | 28500 | 8000 | 24800 | 28500 | 1.0132 | 16500 | 11400 | 12000 | 12400 | 12400 | 1.3306 | 28875 | 28500 | 16000 | 24800 | 28500 | 1.0132
| IIA | N | N | Y | N | 1 | 1 | 1 | 1 | 11000 | 7500 | 2500 | 5600 | 11000 | 7500 | 2500 | 5600 | 7500 | 1.4667 | 19250 | 18750 | 5000 | 11200 | 18750 | 1.0267 | 11000 | 7500 | 7500 | 5600 | 7500 | 1.4667 | 19250 | 18750 | 10000 | 11200 | 18750 | 1.0267
| IIB | N | N | Y | N | 1 | 1 | 1 | 1 | 7000 | 4800 | 1666.6667 | 3700 | 7000 | 4800 | 1666.6667 | 3700 | 4800 | 1.4583 | 12250 | 12000 | 3333.3333 | 7400 | 12000 | 1.0208 | 7000 | 4800 | 5000 | 3700 | 5000 | 1.4 | 12250 | 12000 | 6666.6667 | 7400 | 12000 | 1.0208
| IIIA | N | N | Y | N | 1 | 1 | 1 | NP | 9500 | 6600 | 2500 | NP | 9500 | 6600 | 2500 | NP | 6600 | 1.4394 | 16625 | 16500 | 5000 | NP | 16500 | 1.0076 | 9500 | 6600 | 7500 | NP | 7500 | 1.2667 | 16625 | 16500 | 10000 | NP | 16500 | 1.0076
| IIIB | N | N | Y | N | 1 | 1 | NP | NP | 7000 | 4800 | NP | NP | 7000 | 4800 | NP | NP | 4800 | 1.4583 | 12250 | 12000 | NP | NP | 12000 | 1.0208 | 7000 | 4800 | NP | NP | 4800 | 1.4583 | 12250 | 12000 | NP | NP | 12000 | 1.0208
| IV | N | N | Y | N | 1 | 1 | 1 | NP | 10500 | 7200 | 2500 | NP | 10500 | 7200 | 2500 | NP | 7200 | 1.4583 | 18375 | 18000 | 5000 | NP | 18000 | 1.0208 | 10500 | 7200 | 7500 | NP | 7500 | 1.4 | 18375 | 18000 | 10000 | NP | 18000 | 1.0208
| VA | N | N | Y | N | 1 | 1 | NP | NP | 7500 | 5100 | NP | NP | 7500 | 5100 | NP | NP | 5100 | 1.4706 | 13125 | 12750 | NP | NP | 12750 | 1.0294 | 7500 | 5100 | NP | NP | 5100 | 1.4706 | 13125 | 12750 | NP | NP | 12750 | 1.0294
| VB | N | N | Y | N | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
H-2 | 1A | N | N | Y | N | UL | 3 | 1 | UL | 21000 | 14400 | 5000 | 15000 | 21000 | 14400 | 5000 | 15000 | 15000 | 1.4 | 36750 | 36000 | 10000 | 30000 | 36000 | 1.0208 | 21000 | 14400 | 15000 | 15000 | 15000 | 1.4 | 36750 | 36000 | 20000 | 30000 | 36000 | 1.0208
| IB | N | N | Y | N | 3 | 3 | 1 | 2 | 16500 | 11400 | 4000 | 12400 | 16500 | 11400 | 4000 | 12400 | 12400 | 1.3306 | 28875 | 28500 | 8000 | 24800 | 28500 | 1.0132 | 16500 | 11400 | 12000 | 12400 | 12400 | 1.3306 | 28875 | 28500 | 16000 | 24800 | 28500 | 1.0132
| IIA | N | N | Y | N | 2 | 2 | 1 | 1 | 11000 | 7500 | 2500 | 5600 | 11000 | 7500 | 2500 | 5600 | 7500 | 1.4667 | 19250 | 18750 | 5000 | 11200 | 18750 | 1.0267 | 11000 | 7500 | 7500 | 5600 | 7500 | 1.4667 | 19250 | 18750 | 10000 | 11200 | 18750 | 1.0267
| IIB | N | N | Y | N | 1 | 1 | 1 | 1 | 7000 | 4800 | 1666.6667 | 3700 | 7000 | 4800 | 1666.6667 | 3700 | 4800 | 1.4583 | 12250 | 12000 | 3333.3333 | 7400 | 12000 | 1.0208 | 7000 | 4800 | 5000 | 3700 | 5000 | 1.4 | 12250 | 12000 | 6666.6667 | 7400 | 12000 | 1.0208
| IIIA | N | N | Y | N | 2 | 2 | 1 | 1 | 9500 | 6600 | 2500 | 5600 | 9500 | 6600 | 2500 | 5600 | 6600 | 1.4394 | 16625 | 16500 | 5000 | 11200 | 16500 | 1.0076 | 9500 | 6600 | 7500 | 5600 | 7500 | 1.2667 | 16625 | 16500 | 10000 | 11200 | 16500 | 1.0076
| IIIB | N | N | Y | N | 1 | 1 | 1 | 1 | 7000 | 4800 | 1333.3333 | 3700 | 7000 | 4800 | 1333.3333 | 3700 | 4800 | 1.4583 | 12250 | 12000 | 2666.6667 | 7400 | 12000 | 1.0208 | 7000 | 4800 | 4000 | 3700 | 4800 | 1.4583 | 12250 | 12000 | 5333.3333 | 7400 | 12000 | 1.0208
| IV | N | N | Y | N | 2 | 2 | 1 | 1 | 10500 | 7200 | 2500 | 5600 | 10500 | 7200 | 2500 | 5600 | 7200 | 1.4583 | 18375 | 18000 | 5000 | 11200 | 18000 | 1.0208 | 10500 | 7200 | 7500 | 5600 | 7500 | 1.4 | 18375 | 18000 | 10000 | 11200 | 18000 | 1.0208
| VA | N | N | Y | N | 1 | 1 | 1 | 1 | 7500 | 5100 | 833.3333 | 4400 | 7500 | 5100 | 833.3333 | 4400 | 5100 | 1.4706 | 13125 | 12750 | 1666.6667 | 8800 | 12750 | 1.0294 | 7500 | 5100 | 2500 | 4400 | 5100 | 1.4706 | 13125 | 12750 | 3333.3333 | 8800 | 12750 | 1.0294
| VB | N | N | Y | N | 1 | NP | NP | 1 | 3000 | NP | NP | 2500 | 3000 | NP | NP | 2500 | 2500 | 1.2 | 5250 | NP | NP | 5000 | 5000 | 1.05 | 3000 | NP | NP | 2500 | 2500 | 1.2 | 5250 | NP | NP | 5000 | 5000 | 1.05
H-3 | IA | N | N | Y | N | UL | 7 | Y | UL | UL | 28800 | 10000 | UL | UL | 28800 | 10000 | UL | UL | 1 | UL | 72000 | 20000 | UL | UL | 1 | UL | 28800 | 30000 | UL | UL | 1 | UL | 72000 | 40000 | UL | UL | 1
| IB | N | N | Y | N | 6 | 6 | 3 | 5 | 60000 | 22800 | 6666.6667 | 24800 | 60000 | 22800 | 6666.6667 | 24800 | 24800 | 2.4194 | 105000 | 57000 | 13333.3333 | 49600 | 57000 | 1.8421 | 60000 | 22800 | 20000 | 24800 | 24800 | 2.4194 | 105000 | 57000 | 26666.6667 | 49600 | 57000 | 1.8421
| IIA | N | N | Y | N | 4 | 4 | 2 | 2 | 26500 | 15000 | 3333.3333 | 11200 | 26500 | 15000 | 3333.3333 | 11200 | 15000 | 1.7667 | 46375 | 37500 | 6666.6667 | 22400 | 37500 | 1.2367 | 26500 | 15000 | 10000 | 11200 | 15000 | 1.7667 | 46375 | 37500 | 13333.3333 | 22400 | 37500 | 1.2367
| IIB | N | N | Y | N | 2 | 2 | 1 | 1 | 14000 | 9600 | 2500 | 7500 | 14000 | 9600 | 2500 | 7500 | 9600 | 1.4583 | 24500 | 24000 | 5000 | 15000 | 24000 | 1.0208 | 14000 | 9600 | 7500 | 7500 | 9600 | 1.4583 | 24500 | 24000 | 10000 | 15000 | 24000 | 1.0208
| IIIA | N | N | Y | N | 4 | 3 | 2 | 2 | 17500 | 13200 | 3333.3333 | 11200 | 17500 | 13200 | 3333.3333 | 11200 | 13200 | 1.3258 | 30625 | 33000 | 6666.6667 | 22400 | 33000 | 0.92803 | 17500 | 13200 | 10000 | 11200 | 13200 | 1.3258 | 30625 | 33000 | 13333.3333 | 22400 | 33000 | 0.92803
| IIIB | N | N | Y | N | 2 | 2 | 1 | 1 | 13000 | 9600 | 2500 | 7500 | 13000 | 9600 | 2500 | 7500 | 9600 | 1.3542 | 22750 | 24000 | 5000 | 15000 | 24000 | 0.94792 | 13000 | 9600 | 7500 | 7500 | 9600 | 1.3542 | 22750 | 24000 | 10000 | 15000 | 24000 | 0.94792
| IV | N | N | Y | N | 4 | 4 | 2 | 2 | 25500 | 14400 | 3333.3333 | 11200 | 25500 | 14400 | 3333.3333 | 11200 | 14400 | 1.7708 | 44625 | 36000 | 6666.6667 | 22400 | 36000 | 1.2396 | 25500 | 14400 | 10000 | 11200 | 14400 | 1.7708 | 44625 | 36000 | 13333.3333 | 22400 | 36000 | 1.2396
| VA | N | N | Y | N | 2 | 2 | 1 | 2 | 10000 | 10200 | 1333.3333 | 8800 | 10000 | 10200 | 1333.3333 | 8800 | 10200 | 0.98039 | 17500 | 25500 | 2666.6667 | 17600 | 25500 | 0.68627 | 10000 | 10200 | 4000 | 8800 | 10200 | 0.98039 | 17500 | 25500 | 5333.3333 | 17600 | 25500 | 0.68627
| VB | N | N | Y | N | 1 | 1 | NP | 1 | 5000 | 4800 | NP | 5100 | 5000 | 4800 | NP | 5100 | 5100 | 0.98039 | 8750 | 12000 | NP | 10200 | 12000 | 0.72917 | 5000 | 4800 | NP | 5100 | 5100 | 0.98039 | 8750 | 12000 | NP | 10200 | 12000 | 0.72917
H-4 | IB | Y | Y | Y | Y | 7 | 7 | 6 | 3 | UL | 34200 | UL | 39900 | UL | 34200 | UL | 39900 | UL | 1 | UL | 85500 | UL | 79800 | UL | 1 | UL | 102600 | UL | 119700 | UL | 1 | UL | 153900 | UL | 239400 | UL | 1
| IIA | Y | Y | Y | Y | 5 | 5 | 4 | 3 | 37000 | 22500 | 48000 | 18000 | 37000 | 22500 | 48000 | 18000 | 48000 | 0.77083 | 64750 | 56250 | 96000 | 36000 | 96000 | 0.67448 | 148000 | 67500 | 144000 | 54000 | 144000 | 1.0278 | 175750 | 101250 | 192000 | 108000 | 192000 | 0.91536
| IIB | Y | Y | Y | Y | 3 | 3 | 4 | 2 | 17500 | 14400 | 32000 | 12000 | 17500 | 14400 | 32000 | 12000 | 32000 | 0.54688 | 30625 | 36000 | 64000 | 24000 | 64000 | 0.47852 | 70000 | 43200 | 96000 | 36000 | 96000 | 0.72917 | 83125 | 64800 | 128000 | 72000 | 128000 | 0.64941
| IIIA | Y | Y | Y | Y | 5 | 4 | 4 | 3 | 28500 | 19800 | 48000 | 18000 | 28500 | 19800 | 48000 | 18000 | 48000 | 0.59375 | 49875 | 49500 | 96000 | 36000 | 96000 | 0.51953 | 114000 | 59400 | 144000 | 54000 | 144000 | 0.79167 | 135375 | 89100 | 192000 | 108000 | 192000 | 0.70508
| IIIB | Y | Y | Y | Y | 3 | 3 | 4 | 2 | 17500 | 14400 | 32000 | 12000 | 17500 | 14400 | 32000 | 12000 | 32000 | 0.54688 | 30625 | 36000 | 64000 | 24000 | 64000 | 0.47852 | 70000 | 43200 | 96000 | 36000 | 96000 | 0.72917 | 83125 | 64800 | 128000 | 72000 | 128000 | 0.64941
| IV | Y | Y | Y | Y | 5 | 5 | 3 | 3 | 36000 | 21600 | 48000 | 18000 | 36000 | 21600 | 48000 | 18000 | 48000 | 0.75 | 63000 | 54000 | 96000 | 36000 | 96000 | 0.65625 | 144000 | 64800 | 144000 | 54000 | 144000 | 1 | 171000 | 97200 | 192000 | 108000 | 192000 | 0.89062
| VA | Y | Y | Y | Y | 3 | 3 | 1 | 3 | 18000 | 15300 | 27000 | 14000 | 18000 | 15300 | 27000 | 14000 | 27000 | 0.66667 | 31500 | 38250 | 54000 | 28000 | 54000 | 0.58333 | 72000 | 45900 | 81000 | 42000 | 81000 | 0.88889 | 85500 | 68850 | 108000 | 84000 | 108000 | 0.79167
| VB | Y | Y | Y | Y | 2 | 2 | 1 | 1 | 6500 | 7200 | 18000 | 8000 | 6500 | 7200 | 18000 | 8000 | 18000 | 0.36111 | 11375 | 18000 | 36000 | 16000 | 36000 | 0.31597 | 26000 | 21600 | 54000 | 24000 | 54000 | 0.48148 | 30875 | 32400 | 72000 | 48000 | 72000 | 0.42882
H-5 | IB | Y | Y | Y | Y | 3 | 7 | 3 | 3 | UL | 34400 | UL | 39900 | UL | 34400 | UL | 39900 | UL | 1 | UL | 86000 | UL | 79800 | UL | 1 | UL | 103200 | UL | 119700 | UL | 1 | UL | 154800 | UL | 239400 | UL | 1
| IIA | Y | Y | Y | Y | 3 | 5 | 3 | 3 | 37500 | 22500 | 63000 | 18000 | 37500 | 22500 | 63000 | 18000 | 63000 | 0.59524 | 65625 | 56250 | 126000 | 36000 | 126000 | 0.52083 | 150000 | 67500 | 189000 | 54000 | 189000 | 0.79365 | 178125 | 101250 | 252000 | 108000 | 252000 | 0.70685
| IIB | Y | Y | Y | Y | 3 | 3 | 3 | 2 | 23000 | 14400 | 42000 | 12000 | 23000 | 14400 | 42000 | 12000 | 42000 | 0.54762 | 40250 | 36000 | 84000 | 24000 | 84000 | 0.47917 | 92000 | 43200 | 126000 | 36000 | 126000 | 0.73016 | 109250 | 64800 | 168000 | 72000 | 168000 | 0.6503
| IIIA | Y | Y | Y | Y | 3 | 4 | 3 | 3 | 28500 | 19800 | 45000 | 18000 | 28500 | 19800 | 45000 | 18000 | 45000 | 0.63333 | 49875 | 49500 | 90000 | 36000 | 90000 | 0.55417 | 114000 | 59400 | 135000 | 54000 | 135000 | 0.84444 | 135375 | 89100 | 180000 | 108000 | 180000 | 0.75208
| IIIB | Y | Y | Y | Y | 3 | 3 | 3 | 2 | 19000 | 14400 | 30000 | 12000 | 19000 | 14400 | 30000 | 12000 | 30000 | 0.63333 | 33250 | 36000 | 60000 | 24000 | 60000 | 0.55417 | 76000 | 43200 | 90000 | 36000 | 90000 | 0.84444 | 90250 | 64800 | 120000 | 72000 | 120000 | 0.75208
| IV | Y | Y | Y | Y | 3 | 5 | 3 | 3 | 36000 | 21600 | 63000 | 18000 | 36000 | 21600 | 63000 | 18000 | 63000 | 0.57143 | 63000 | 54000 | 126000 | 36000 | 126000 | 0.5 | 144000 | 64800 | 189000 | 54000 | 189000 | 0.7619 | 171000 | 97200 | 252000 | 108000 | 252000 | 0.67857
| VA | Y | Y | Y | Y | 3 | 3 | 1 | 3 | 18000 | 15300 | 45000 | 14000 | 18000 | 15300 | 45000 | 14000 | 45000 | 0.4 | 31500 | 38250 | 90000 | 28000 | 90000 | 0.35 | 72000 | 45900 | 135000 | 42000 | 135000 | 0.53333 | 85500 | 68850 | 180000 | 84000 | 180000 | 0.475
| VB | Y | Y | Y | Y | 2 | 2 | 1 | 1 | 9000 | 7200 | 45000 | 8000 | 9000 | 7200 | 45000 | 8000 | 45000 | 0.2 | 15750 | 18000 | 90000 | 16000 | 90000 | 0.175 | 36000 | 21600 | 135000 | 24000 | 135000 | 0.26667 | 42750 | 32400 | 180000 | 48000 | 180000 | 0.2375
I-1 | IB | Y | Y | Y | Y | 9 | 9 |  | 3 | 55000 | 19950 |  | 15100 | 55000 | 19950 | 0 | 15100 | 19950 | 2.7569 | 96250 | 49875 | 0 | 30200 | 49875 | 1.9298 | 220000 | 59850 | 0 | 45300 | 59850 | 3.6759 | 261250 | 89775 | 0 | 90600 | 90600 | 2.8836
Ass't | IIA | Y | Y | Y | Y | 4 | 4 |  | 2 | 19000 | 13125 |  | 6800 | 19000 | 13125 | 0 | 6800 | 13125 | 1.4476 | 33250 | 32812.5 | 0 | 13600 | 32812.5 | 1.0133 | 76000 | 39375 | 0 | 20400 | 39375 | 1.9302 | 90250 | 59062.5 | 0 | 40800 | 59062.5 | 1.528
| IIB | Y | Y | Y | Y | 3 | 3 |  | NP | 10000 | 8400 |  | NP | 10000 | 8400 | 0 | NP | 8400 | 1.1905 | 17500 | 21000 | 0 | NP | 21000 | 0.83333 | 40000 | 25200 | 0 | NP | 25200 | 1.5873 | 47500 | 37800 | 0 | NP | 37800 | 1.2566
| IIIA | Y | Y | Y | Y | 4 | 4 |  | 2 | 16500 | 11550 |  | 6800 | 16500 | 11550 | 0 | 6800 | 11550 | 1.4286 | 28875 | 28875 | 0 | 13600 | 28875 | 1 | 66000 | 34650 | 0 | 20400 | 34650 | 1.9048 | 78375 | 51975 | 0 | 40800 | 51975 | 1.5079
| IIIB | Y | Y | Y | Y | 3 | 3 |  | NP | 10000 | 8400 |  | NP | 10000 | 8400 | 0 | NP | 8400 | 1.1905 | 17500 | 21000 | 0 | NP | 21000 | 0.83333 | 40000 | 25200 | 0 | NP | 25200 | 1.5873 | 47500 | 37800 | 0 | NP | 37800 | 1.2566
| IV | Y | Y | Y | Y | 4 | 4 |  | 2 | 18000 | 12600 |  | 6800 | 18000 | 12600 | 0 | 6800 | 12600 | 1.4286 | 31500 | 31500 | 0 | 13600 | 31500 | 1 | 72000 | 37800 | 0 | 20400 | 37800 | 1.9048 | 85500 | 56700 | 0 | 40800 | 56700 | 1.5079
| VA | Y | Y | Y | Y | 3 | 3 |  | 2 | 10500 | 8925 |  | 5200 | 10500 | 8925 | 0 | 5200 | 8925 | 1.1765 | 18375 | 22312.5 | 0 | 10400 | 22312.5 | 0.82353 | 42000 | 26775 | 0 | 15600 | 26775 | 1.5686 | 49875 | 40162.5 | 0 | 31200 | 40162.5 | 1.2418
| VB | Y | Y | Y | Y | 2 | 2 |  | NP | 4500 | 4200 |  | NP | 4500 | 4200 | 0 | NP | 4200 | 1.0714 | 7875 | 10500 | 0 | NP | 10500 | 0.75 | 18000 | 12600 | 0 | NP | 12600 | 1.4286 | 21375 | 18900 | 0 | NP | 18900 | 1.131
I-2 | IB | Y | Y | Y | Y | 4 | 4 | UL | 3 | UL | 17100 | UL | 15100 | UL | 17100 | UL | 15100 | UL | 1 | UL | 42750 | UL | 30200 | UL | 1 | UL | 51300 | UL | 45300 | UL | 1 | UL | 76950 | UL | 90600 | UL | 1
Hos | IIA | Y | Y | Y | Y | 2 | 2 | 3 | 1 | 15000 | 11250 | 15000 | 6800 | 15000 | 11250 | 15000 | 6800 | 15000 | 1 | 26250 | 28125 | 30000 | 13600 | 30000 | 0.875 | 60000 | 33750 | 45000 | 20400 | 45000 | 1.3333 | 71250 | 50625 | 60000 | 40800 | 60000 | 1.1875
| IIB | Y | Y | Y | Y | 1 | 1 | 1 | NP | 11000 | 7200 | 10000 | NP | 11000 | 7200 | 10000 | NP | 10000 | 1.1 | 19250 | 18000 | 20000 | NP | 20000 | 0.9625 | 44000 | 21600 | 30000 | NP | 30000 | 1.4667 | 52250 | 32400 | 40000 | NP | 40000 | 1.3062
| IIIA | Y | Y | Y | Y | 1 | 1 | 1 | 1 | 12000 | 9900 | 10500 | 6800 | 12000 | 9900 | 10500 | 6800 | 10500 | 1.1429 | 21000 | 24750 | 21000 | 13600 | 24750 | 0.84848 | 48000 | 29700 | 31500 | 20400 | 31500 | 1.5238 | 57000 | 44550 | 42000 | 40800 | 44550 | 1.2795
| IIIB | Y | Y | Y | Y | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
| IV | Y | Y | Y | Y | 1 | 1 | 2 | 1 | 12000 | 10800 | 12000 | 6800 | 12000 | 10800 | 12000 | 6800 | 12000 | 1 | 21000 | 27000 | 24000 | 13600 | 27000 | 0.77778 | 48000 | 32400 | 36000 | 20400 | 36000 | 1.3333 | 57000 | 48600 | 48000 | 40800 | 48600 | 1.1728
| VA | Y | Y | Y | Y | 1 | 1 | 1 | 1 | 9500 | 7650 | 7500 | 5200 | 9500 | 7650 | 7500 | 5200 | 7650 | 1.2418 | 16625 | 19125 | 15000 | 10400 | 19125 | 0.86928 | 38000 | 22950 | 22500 | 15600 | 22950 | 1.6558 | 45125 | 34425 | 30000 | 31200 | 34425 | 1.3108
| VB | Y | Y | Y | Y | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
I-3 | IB | Y | Y | Y | Y | 4 | 4 | UL | 2 | UL | 14250 | UL | 15100 | UL | 14250 | UL | 15100 | UL | 1 | UL | 35625 | UL | 30200 | UL | 1 | UL | 42750 | UL | 45300 | UL | 1 | UL | 64125 | UL | 90600 | UL | 1
| IIA | Y | Y | Y | Y | 2 | 2 | 3 | NP | 15000 | 9375 | 15000 | NP | 15000 | 9375 | 15000 | NP | 15000 | 1 | 26250 | 23437.5 | 30000 | NP | 30000 | 0.875 | 60000 | 28125 | 45000 | NP | 45000 | 1.3333 | 71250 | 42187.5 | 60000 | NP | 60000 | 1.1875
| IIB | Y | Y | Y | Y | 1 | 1 | 2 | NP | 10000 | 6000 | 10000 | NP | 10000 | 6000 | 10000 | NP | 10000 | 1 | 17500 | 15000 | 20000 | NP | 20000 | 0.875 | 40000 | 18000 | 30000 | NP | 30000 | 1.3333 | 47500 | 27000 | 40000 | NP | 40000 | 1.1875
| IIIA | Y | Y | Y | Y | 2 | 2 | 3 | NP | 10500 | 8250 | 10500 | NP | 10500 | 8250 | 10500 | NP | 10500 | 1 | 18375 | 20625 | 21000 | NP | 21000 | 0.875 | 42000 | 24750 | 31500 | NP | 31500 | 1.3333 | 49875 | 37125 | 42000 | NP | 42000 | 1.1875
| IIIB | Y | Y | Y | Y | 1 | 1 | 2 | NP | 7500 | 6000 | 7000 | NP | 7500 | 6000 | 7000 | NP | 7000 | 1.0714 | 13125 | 15000 | 14000 | NP | 15000 | 0.875 | 30000 | 18000 | 21000 | NP | 21000 | 1.4286 | 35625 | 27000 | 28000 | NP | 28000 | 1.2723
| IV | Y | Y | Y | Y | 2 | 2 | 2 | NP | 12000 | 9000 | 12000 | NP | 12000 | 9000 | 12000 | NP | 12000 | 1 | 21000 | 22500 | 24000 | NP | 24000 | 0.875 | 48000 | 27000 | 36000 | NP | 36000 | 1.3333 | 57000 | 40500 | 48000 | NP | 48000 | 1.1875
| VA | Y | Y | Y | Y | 2 | 1 | 3 | NP | 7500 | 6375 | 7500 | NP | 7500 | 6375 | 7500 | NP | 7500 | 1 | 13125 | 15937.5 | 15000 | NP | 15937.5 | 0.82353 | 30000 | 19125 | 22500 | NP | 22500 | 1.3333 | 35625 | 28687.5 | 30000 | NP | 30000 | 1.1875
| VB | Y | Y | Y | Y | 1 | NP | 2 | NP | 5000 | NP | 5000 | NP | 5000 | NP | 5000 | NP | 5000 | 1 | 8750 | NP | 10000 | NP | 10000 | 0.875 | 20000 | NP | 15000 | NP | 15000 | 1.3333 | 23750 | NP | 20000 | NP | 20000 | 1.1875
I-4 | IB | Y | Y | Y | Y | 5 | 5 |  | 4 | 60500 | 34200 |  | 45200 | 60500 | 34200 | 0 | 45200 | 45200 | 1.3385 | 105875 | 85500 | 0 | 90400 | 90400 | 1.1712 | 242000 | 102600 | 0 | 135600 | 135600 | 1.7847 | 287375 | 153900 | 0 | 271200 | 271200 | 1.0596
| IIA | Y | Y | Y | Y | 3 | 3 |  | 2 | 26500 | 22500 |  | 20200 | 26500 | 22500 | 0 | 20200 | 22500 | 1.1778 | 46375 | 56250 | 0 | 40400 | 56250 | 0.82444 | 106000 | 67500 | 0 | 60600 | 67500 | 1.5704 | 125875 | 101250 | 0 | 121200 | 121200 | 1.0386
| IIB | Y | Y | Y | Y | 2 | 2 |  | 1 | 13000 | 14400 |  | 13500 | 13000 | 14400 | 0 | 13500 | 14400 | 0.90278 | 22750 | 36000 | 0 | 27000 | 36000 | 0.63194 | 52000 | 43200 | 0 | 40500 | 43200 | 1.2037 | 61750 | 64800 | 0 | 81000 | 81000 | 0.76235
| IIIA | Y | Y | Y | Y | 3 | 3 |  | 2 | 23500 | 19800 |  | 20200 | 23500 | 19800 | 0 | 20200 | 20200 | 1.1634 | 41125 | 49500 | 0 | 40400 | 49500 | 0.83081 | 94000 | 59400 | 0 | 60600 | 60600 | 1.5512 | 111625 | 89100 | 0 | 121200 | 121200 | 0.921
| IIIB | Y | Y | Y | Y | 2 | 2 |  | 1 | 13000 | 14400 |  | 13500 | 13000 | 14400 | 0 | 13500 | 14400 | 0.90278 | 22750 | 36000 | 0 | 27000 | 36000 | 0.63194 | 52000 | 43200 | 0 | 40500 | 43200 | 1.2037 | 61750 | 64800 | 0 | 81000 | 81000 | 0.76235
| IV | Y | Y | Y | Y | 3 | 3 |  | 2 | 25500 | 21600 |  | 20200 | 25500 | 21600 | 0 | 20200 | 21600 | 1.1806 | 44625 | 54000 | 0 | 40400 | 54000 | 0.82639 | 102000 | 64800 | 0 | 60600 | 64800 | 1.5741 | 121125 | 97200 | 0 | 121200 | 121200 | 0.99938
| VA | Y | Y | Y | Y | 1 | 1 |  | 2 | 18500 | 15300 |  | 15700 | 18500 | 15300 | 0 | 15700 | 15700 | 1.1783 | 32375 | 38250 | 0 | 31400 | 38250 | 0.84641 | 74000 | 45900 | 0 | 47100 | 47100 | 1.5711 | 87875 | 68850 | 0 | 94200 | 94200 | 0.93286
| VB | Y | Y | Y | Y | 1 | 1 |  | 1 | 9000 | 7200 |  | 9100 | 9000 | 7200 | 0 | 9100 | 9100 | 0.98901 | 15750 | 18000 | 0 | 18200 | 18200 | 0.86538 | 36000 | 21600 | 0 | 27300 | 27300 | 1.3187 | 42750 | 32400 | 0 | 54600 | 54600 | 0.78297
M | IB | Y | Y | Y | Y | 11 | 6 | UL | 12 | UL | 22800 | 15000 | 39900 | UL | 22800 | 15000 | 39900 | 39900 | INF | UL | 57000 | 30000 | 79800 | 79800 | INF | UL | 68400 | 45000 | 119700 | 119700 | INF | UL | 102600 | 60000 | 239400 | 239400 | INF
| IIA | Y | Y | Y | Y | 4 | 4 | 5 | 4 | 21500 | 15000 | 13500 | 18000 | 21500 | 15000 | 13500 | 18000 | 18000 | 1.1944 | 37625 | 37500 | 27000 | 36000 | 37500 | 1.0033 | 86000 | 45000 | 40500 | 54000 | 54000 | 1.5926 | 102125 | 67500 | 54000 | 108000 | 108000 | 0.9456
| IIB | Y | Y | Y | Y | 4 | 2 | 5 | 2 | 12500 | 9600 | 9000 | 12000 | 12500 | 9600 | 9000 | 12000 | 12000 | 1.0417 | 21875 | 24000 | 18000 | 24000 | 24000 | 0.91146 | 50000 | 28800 | 27000 | 36000 | 36000 | 1.3889 | 59375 | 43200 | 36000 | 72000 | 72000 | 0.82465
| IIIA | Y | Y | Y | Y | 4 | 3 | 5 | 4 | 18500 | 13200 | 13500 | 18000 | 18500 | 13200 | 13500 | 18000 | 18000 | 1.0278 | 32375 | 33000 | 27000 | 36000 | 36000 | 0.89931 | 74000 | 39600 | 40500 | 54000 | 54000 | 1.3704 | 87875 | 59400 | 54000 | 108000 | 108000 | 0.81366
| IIIB | Y | Y | Y | Y | 4 | 2 | 5 | 2 | 12500 | 9600 | 9000 | 12000 | 12500 | 9600 | 9000 | 12000 | 12000 | 1.0417 | 21875 | 24000 | 18000 | 24000 | 24000 | 0.91146 | 50000 | 28800 | 27000 | 36000 | 36000 | 1.3889 | 59375 | 43200 | 36000 | 72000 | 72000 | 0.82465
| IV | Y | Y | Y | Y | 4 | 4 | 5 | 4 | 20500 | 14400 | 13500 | 18000 | 20500 | 14400 | 13500 | 18000 | 18000 | 1.1389 | 35875 | 36000 | 27000 | 36000 | 36000 | 0.99653 | 82000 | 43200 | 40500 | 54000 | 54000 | 1.5185 | 97375 | 64800 | 54000 | 108000 | 108000 | 0.90162
| VA | Y | Y | Y | Y | 3 | 2 | 2 | 3 | 14000 | 10200 | 9000 | 14000 | 14000 | 10200 | 9000 | 14000 | 14000 | 1 | 24500 | 25500 | 18000 | 28000 | 28000 | 0.875 | 56000 | 30600 | 27000 | 42000 | 42000 | 1.3333 | 66500 | 45900 | 36000 | 84000 | 84000 | 0.79167
| VB | Y | Y | Y | Y | 1 | 1 | 2 | 2 | 9000 | 4800 | 6000 | 8000 | 9000 | 4800 | 6000 | 8000 | 8000 | 1.125 | 15750 | 12000 | 12000 | 16000 | 16000 | 0.98438 | 36000 | 14400 | 18000 | 24000 | 24000 | 1.5 | 42750 | 21600 | 24000 | 48000 | 48000 | 0.89062
R-1 | IB | Y | Y | Y | Y | 11 | 9 | UL | 12 | UL | 22800 | UL | 29900 | UL | 22800 | UL | 29900 | UL | 1 | UL | 57000 | UL | 59800 | UL | 1 | UL | 68400 | UL | 89700 | UL | 1 | UL | 102600 | UL | 179400 | UL | 1
| IIA | Y | Y | Y | Y | 4 | 4 | 5 | 4 | 24000 | 15000 | 18000 | 13500 | 24000 | 15000 | 18000 | 13500 | 18000 | 1.3333 | 42000 | 37500 | 36000 | 27000 | 37500 | 1.12 | 96000 | 45000 | 54000 | 40500 | 54000 | 1.7778 | 114000 | 67500 | 72000 | 81000 | 81000 | 1.4074
| IIB | Y | Y | Y | Y | 4 | 3 | 5 | 2 | 16000 | 9600 | 12000 | 9100 | 16000 | 9600 | 12000 | 9100 | 12000 | 1.3333 | 28000 | 24000 | 24000 | 18200 | 24000 | 1.1667 | 64000 | 28800 | 36000 | 27300 | 36000 | 1.7778 | 76000 | 43200 | 48000 | 54600 | 54600 | 1.3919
| IIIA | Y | Y | Y | Y | 4 | 4 | 5 | 4 | 24000 | 13200 | 18000 | 13500 | 24000 | 13200 | 18000 | 13500 | 18000 | 1.3333 | 42000 | 33000 | 36000 | 27000 | 36000 | 1.1667 | 96000 | 39600 | 54000 | 40500 | 54000 | 1.7778 | 114000 | 59400 | 72000 | 81000 | 81000 | 1.4074
| IIIB | Y | Y | Y | Y | 4 | 3 | 5 | 2 | 16000 | 9600 | 12000 | 9100 | 16000 | 9600 | 12000 | 9100 | 12000 | 1.3333 | 28000 | 24000 | 24000 | 18200 | 24000 | 1.1667 | 64000 | 28800 | 36000 | 27300 | 36000 | 1.7778 | 76000 | 43200 | 48000 | 54600 | 54600 | 1.3919
| IV | Y | Y | Y | Y | 4 | 4 | 3 | 4 | 20500 | 14400 | 18000 | 13500 | 20500 | 14400 | 18000 | 13500 | 18000 | 1.1389 | 35875 | 36000 | 36000 | 27000 | 36000 | 0.99653 | 82000 | 43200 | 54000 | 40500 | 54000 | 1.5185 | 97375 | 64800 | 72000 | 81000 | 81000 | 1.2022
| VA | Y | Y | Y | Y | 3 | 3 | 3 | 3 | 12000 | 10200 | 10500 | 10500 | 12000 | 10200 | 10500 | 10500 | 10500 | 1.1429 | 21000 | 25500 | 21000 | 21000 | 25500 | 0.82353 | 48000 | 30600 | 31500 | 31500 | 31500 | 1.5238 | 57000 | 45900 | 42000 | 63000 | 63000 | 0.90476
| VB | Y | Y | Y | Y | 2 | 2 | 2 | 2 | 7000 | 4800 | 7000 | 6000 | 7000 | 4800 | 7000 | 6000 | 7000 | 1 | 12250 | 12000 | 14000 | 12000 | 14000 | 0.875 | 28000 | 14400 | 21000 | 18000 | 21000 | 1.3333 | 33250 | 21600 | 28000 | 36000 | 36000 | 0.92361
R-2 | IB | Y | Y | Y | Y | 11 | 9 | UL | 12 | UL | 22800 | UL | 29900 | UL | 22800 | UL | 29900 | UL | 1 | UL | 57000 | UL | 59800 | UL | 1 | UL | 68400 | UL | 89700 | UL | 1 | UL | 102600 | UL | 179400 | UL | 1
| IIA | Y | Y | Y | Y | 4 | 4 | 5 | 4 | 24000 | 15000 | 18000 | 13500 | 24000 | 15000 | 18000 | 13500 | 18000 | 1.3333 | 42000 | 37500 | 36000 | 27000 | 37500 | 1.12 | 96000 | 45000 | 54000 | 40500 | 54000 | 1.7778 | 114000 | 67500 | 72000 | 81000 | 81000 | 1.4074
| IIB | Y | Y | Y | Y | 4 | 3 | 5 | 2 | 16000 | 9600 | 12000 | 9100 | 16000 | 9600 | 12000 | 9100 | 12000 | 1.3333 | 28000 | 24000 | 24000 | 18200 | 24000 | 1.1667 | 64000 | 28800 | 36000 | 27300 | 36000 | 1.7778 | 76000 | 43200 | 48000 | 54600 | 54600 | 1.3919
| IIIA | Y | Y | Y | Y | 4 | 4 | 5 | 4 | 24000 | 13200 | 18000 | 13500 | 24000 | 13200 | 18000 | 13500 | 18000 | 1.3333 | 42000 | 33000 | 36000 | 27000 | 36000 | 1.1667 | 96000 | 39600 | 54000 | 40500 | 54000 | 1.7778 | 114000 | 59400 | 72000 | 81000 | 81000 | 1.4074
| IIIB | Y | Y | Y | Y | 4 | 3 | 3 | 2 | 16000 | 9600 | 12000 | 9100 | 16000 | 9600 | 12000 | 9100 | 12000 | 1.3333 | 28000 | 24000 | 24000 | 18200 | 24000 | 1.1667 | 64000 | 28800 | 36000 | 27300 | 36000 | 1.7778 | 76000 | 43200 | 48000 | 54600 | 54600 | 1.3919
| IV | Y | Y | Y | Y | 4 | 4 | 3 | 4 | 20500 | 14400 | 18000 | 13500 | 20500 | 14400 | 18000 | 13500 | 18000 | 1.1389 | 35875 | 36000 | 36000 | 27000 | 36000 | 0.99653 | 82000 | 43200 | 54000 | 40500 | 54000 | 1.5185 | 97375 | 64800 | 72000 | 81000 | 81000 | 1.2022
| VA | Y | Y | Y | Y | 3 | 3 | 3 | 3 | 12000 | 10200 | 10500 | 10500 | 12000 | 10200 | 10500 | 10500 | 10500 | 1.1429 | 21000 | 25500 | 21000 | 21000 | 25500 | 0.82353 | 48000 | 30600 | 31500 | 31500 | 31500 | 1.5238 | 57000 | 45900 | 42000 | 63000 | 63000 | 0.90476
| VB | Y | Y | Y | Y | 2 | 2 | 2 | 2 | 7000 | 4800 | 7000 | 6000 | 7000 | 4800 | 7000 | 6000 | 7000 | 1 | 12250 | 12000 | 14000 | 12000 | 14000 | 0.875 | 28000 | 14400 | 21000 | 18000 | 21000 | 1.3333 | 33250 | 21600 | 28000 | 36000 | 36000 | 0.92361
R-3 | IB | Y | Y | Y | Y | 11 | 4 | UL | 3 | UL | 22800 | UL | UL | UL | 22800 | UL | UL | UL | 1 | UL | 57000 | UL | UL | UL | 1 | UL | 68400 | UL | UL | UL | 1 | UL | 102600 | UL | UL | UL | 1
| IIA | Y | Y | Y | Y | 4 | 4 | 5 | 3 | UL | 15000 | 18000 | UL | UL | 15000 | 18000 | UL | UL | 1 | UL | 37500 | 36000 | UL | UL | 1 | UL | 45000 | 54000 | UL | UL | 1 | UL | 67500 | 72000 | UL | UL | 1
| IIB | Y | Y | Y | Y | 4 | 3 | 5 | 3 | UL | 9600 | 12000 | UL | UL | 9600 | 12000 | UL | UL | 1 | UL | 24000 | 24000 | UL | UL | 1 | UL | 28800 | 36000 | UL | UL | 1 | UL | 43200 | 48000 | UL | UL | 1
| IIIA | Y | Y | Y | Y | 4 | 4 | 5 | 3 | UL | 13200 | 18000 | UL | UL | 13200 | 18000 | UL | UL | 1 | UL | 33000 | 36000 | UL | UL | 1 | UL | 39600 | 54000 | UL | UL | 1 | UL | 59400 | 72000 | UL | UL | 1
| IIIB | Y | Y | Y | Y | 4 | 3 | 5 | 3 | UL | 9600 | 12000 | UL | UL | 9600 | 12000 | UL | UL | 1 | UL | 24000 | 24000 | UL | UL | 1 | UL | 28800 | 36000 | UL | UL | 1 | UL | 43200 | 48000 | UL | UL | 1
| IV | Y | Y | Y | Y | 4 | 4 | 3 | 3 | UL | 14400 | 18000 | UL | UL | 14400 | 18000 | UL | UL | 1 | UL | 36000 | 36000 | UL | UL | 1 | UL | 43200 | 54000 | UL | UL | 1 | UL | 64800 | 72000 | UL | UL | 1
| VA | Y | Y | Y | Y | 3 | 3 | 3 | 3 | UL | 10200 | 10500 | UL | UL | 10200 | 10500 | UL | UL | 1 | UL | 25500 | 21000 | UL | UL | 1 | UL | 30600 | 31500 | UL | UL | 1 | UL | 45900 | 42000 | UL | UL | 1
| VB | Y | Y | Y | Y | 3 | 2 | 2 | 3 | UL | 4800 | 7000 | UL | UL | 4800 | 7000 | UL | UL | 1 | UL | 12000 | 14000 | UL | UL | 1 | UL | 14400 | 21000 | UL | UL | 1 | UL | 21600 | 28000 | UL | UL | 1
S-1 | IB | Y | Y | Y | Y | 11 | 5 | 6 | 12 | 48000 | 19950 | 30000 | 39900 | 48000 | 19950 | 30000 | 39900 | 39900 | 1.203 | 84000 | 49875 | 60000 | 79800 | 79800 | 1.0526 | 192000 | 59850 | 90000 | 119700 | 119700 | 1.604 | 228000 | 89775 | 120000 | 239400 | 239400 | 0.95238
| IIA | Y | Y | Y | Y | 4 | 4 | 4 | 4 | 26000 | 13125 | 24000 | 18000 | 26000 | 13125 | 24000 | 18000 | 24000 | 1.0833 | 45500 | 32812.5 | 48000 | 36000 | 48000 | 0.94792 | 104000 | 39375 | 72000 | 54000 | 72000 | 1.4444 | 123500 | 59062.5 | 96000 | 108000 | 108000 | 1.1435
| IIB | Y | Y | Y | Y | 3 | 2 | 4 | 2 | 17500 | 8400 | 16000 | 12000 | 17500 | 8400 | 16000 | 12000 | 16000 | 1.0938 | 30625 | 21000 | 32000 | 24000 | 32000 | 0.95703 | 70000 | 25200 | 48000 | 36000 | 48000 | 1.4583 | 83125 | 37800 | 64000 | 72000 | 72000 | 1.1545
| IIIA | Y | Y | Y | Y | 3 | 3 | 4 | 4 | 26000 | 11550 | 24000 | 18000 | 26000 | 11550 | 24000 | 18000 | 24000 | 1.0833 | 45500 | 28875 | 48000 | 36000 | 48000 | 0.94792 | 104000 | 34650 | 72000 | 54000 | 72000 | 1.4444 | 123500 | 51975 | 96000 | 108000 | 108000 | 1.1435
| IIIB | Y | Y | Y | Y | 3 | 2 | 4 | 2 | 17500 | 8400 | 16000 | 12000 | 17500 | 8400 | 16000 | 12000 | 16000 | 1.0938 | 30625 | 21000 | 32000 | 24000 | 32000 | 0.95703 | 70000 | 25200 | 48000 | 36000 | 48000 | 1.4583 | 83125 | 37800 | 64000 | 72000 | 72000 | 1.1545
| IV | Y | Y | Y | Y | 4 | 4 | 6 | 4 | 25500 | 12600 | 24000 | 18000 | 25500 | 12600 | 24000 | 18000 | 24000 | 1.0625 | 44625 | 31500 | 48000 | 36000 | 48000 | 0.92969 | 102000 | 37800 | 72000 | 54000 | 72000 | 1.4167 | 121125 | 56700 | 96000 | 108000 | 108000 | 1.1215
| VA | Y | Y | Y | Y | 3 | 2 | 1 | 3 | 14000 | 8925 | 9000 | 14000 | 14000 | 8925 | 9000 | 14000 | 14000 | 1 | 24500 | 22312.5 | 18000 | 28000 | 28000 | 0.875 | 56000 | 26775 | 27000 | 42000 | 42000 | 1.3333 | 66500 | 40162.5 | 36000 | 84000 | 84000 | 0.79167
| VB | Y | Y | Y | Y | 1 | 1 | 1 | 2 | 9000 | 4200 | 6000 | 8000 | 9000 | 4200 | 6000 | 8000 | 8000 | 1.125 | 15750 | 10500 | 12000 | 16000 | 16000 | 0.98438 | 36000 | 12600 | 18000 | 24000 | 24000 | 1.5 | 42750 | 18900 | 24000 | 48000 | 48000 | 0.89062
S-2 | IB | Y | Y | Y | Y | 11 | 7 | 6 | 12 | 79000 | 34200 | 30000 | 59900 | 79000 | 34200 | 30000 | 59900 | 59900 | 1.3189 | 138250 | 85500 | 60000 | 119800 | 119800 | 1.154 | 316000 | 102600 | 90000 | 179700 | 179700 | 1.7585 | 375250 | 153900 | 120000 | 359400 | 359400 | 1.0441
| IIA | Y | Y | Y | Y | 5 | 5 | 4 | 4 | 39000 | 22500 | 24000 | 27000 | 39000 | 22500 | 24000 | 27000 | 27000 | 1.4444 | 68250 | 56250 | 48000 | 54000 | 56250 | 1.2133 | 156000 | 67500 | 72000 | 81000 | 81000 | 1.9259 | 185250 | 101250 | 96000 | 162000 | 162000 | 1.1435
| IIB | Y | Y | Y | Y | 4 | 3 | 4 | 2 | 26000 | 14400 | 16000 | 18000 | 26000 | 14400 | 16000 | 18000 | 18000 | 1.4444 | 45500 | 36000 | 32000 | 36000 | 36000 | 1.2639 | 104000 | 43200 | 48000 | 54000 | 54000 | 1.9259 | 123500 | 64800 | 64000 | 108000 | 108000 | 1.1435
| IIIA | Y | Y | Y | Y | 4 | 4 | 4 | 4 | 39000 | 19800 | 24000 | 27000 | 39000 | 19800 | 24000 | 27000 | 27000 | 1.4444 | 68250 | 49500 | 48000 | 54000 | 54000 | 1.2639 | 156000 | 59400 | 72000 | 81000 | 81000 | 1.9259 | 185250 | 89100 | 96000 | 162000 | 162000 | 1.1435
| IIIB | Y | Y | Y | Y | 4 | 3 | 4 | 2 | 26000 | 14400 | 16000 | 18000 | 26000 | 14400 | 16000 | 18000 | 18000 | 1.4444 | 45500 | 36000 | 32000 | 36000 | 36000 | 1.2639 | 104000 | 43200 | 48000 | 54000 | 54000 | 1.9259 | 123500 | 64800 | 64000 | 108000 | 108000 | 1.1435
| IV | Y | Y | Y | Y | 5 | 5 | 6 | 4 | 38500 | 21600 | 24000 | 27000 | 38500 | 21600 | 24000 | 27000 | 27000 | 1.4259 | 67375 | 54000 | 48000 | 54000 | 54000 | 1.2477 | 154000 | 64800 | 72000 | 81000 | 81000 | 1.9012 | 182875 | 97200 | 96000 | 162000 | 162000 | 1.1289
| VA | Y | Y | Y | Y | 4 | 3 | 1 | 3 | 21000 | 15300 | 9000 | 21000 | 21000 | 15300 | 9000 | 21000 | 21000 | 1 | 36750 | 38250 | 18000 | 42000 | 42000 | 0.875 | 84000 | 45900 | 27000 | 63000 | 63000 | 1.3333 | 99750 | 68850 | 36000 | 126000 | 126000 | 0.79167
| VB | Y | Y | Y | Y | 2 | 2 | 1 | 2 | 13500 | 7200 | 6000 | 12000 | 13500 | 7200 | 6000 | 12000 | 12000 | 1.125 | 23625 | 18000 | 12000 | 24000 | 24000 | 0.98438 | 54000 | 21600 | 18000 | 36000 | 36000 | 1.5 | 64125 | 32400 | 24000 | 72000 | 72000 | 0.89062

## Two Stories
Cells identified at Dec 10 - 11 meeting that result in total building area that is more than 10% greater than total area permitted by largest legacy code.
IBC more than 10% greater than largest legacy code area.
IBC more than 10% less than largest legacy code area.
LNP - Not pemitted by legacy codes but permitted by IBC
INF - Infinity
Ratio of IBC area to largest legacy code area for condition stated:
[23 empty] | Without sprinklers | [11 empty] | With sprinklers
[14 empty] | Tabular area of code | [8 empty] | Open space | [11 empty] | Open space
[14 empty] | IBC | NBC | SBC | UBC | [5 empty] | < 20 | [5 empty] | 40 | [5 empty] | < 20 | [5 empty] | 40
[14 empty] | Tabular Areas (TA) |  |  |  | TA + < 20 ft. open space (no sprinklers) | [5 empty] | TA + 40 ft. open space (no sprinklers) | [5 empty] | TA + < 20 ft. open space + sprinklers | [5 empty] | TA + 40 ft. open space + sprinklers
|  | IBC | NBC | SBC | UBC | IBC | NBC | SBC | UBC | IBC | NBC | SBC | UBC | IBC | NBC | SBC | UBC | IBC | NBC | SBC | UBC | Largest Legacy | Ratio IBC/LL | IBC | NBC | SBC | UBC | Largest Legacy | Ratio IBC/LL | IBC | NBC | SBC | UBC | Largest Legacy | Ratio IBC/LL | IBC | NBC | SBC | UBC | Largest Legacy | Ratio IBC/LL
Occup. | Type Const. | Area Increase for Sprinklers? |  |  |  | Height Increase for Sprinklers? |  |  |  | Ht. | Ht. | Ht. | Ht. | Area | Area | Area | Area | Area | Area | Area | Area | Area |  | Area | Area | Area | Area | Area |  | Area | Area | Area | Area | Area |  | Area | Area | Area | Area | Area
A-1 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 5 | 5 | UL | 4 | UL | 19950 | UL | 29900 | UL | 39900 | UL | 59800 | UL | 1 | UL | 99750 | UL | 119600 | UL | 1 | UL | 119700 | UL | 119600 | UL | 1 | UL | 179550 | UL | 239200 | UL | 1
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 4 | 2 | 15500 | 13125 | 12000 | 13500 | 31000 | 26250 | 24000 | 27000 | 27000 | 1.1481 | 54250 | 65625 | 48000 | 54000 | 65625 | 0.82667 | 93000 | 78750 | 48000 | 54000 | 78750 | 1.181 | 116250 | 118125 | 72000 | 108000 | 118125 | 0.98413
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | NP | 8500 | 8400 | 8000 | NP | 17000 | 16800 | 16000 | NP | 16800 | 1.0119 | 29750 | 42000 | 32000 | NP | 42000 | 0.70833 | 51000 | 50400 | 32000 | NP | 50400 | 1.0119 | 63750 | 75600 | 48000 | NP | 75600 | 0.84325
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 14000 | 11550 | 12000 | 13500 | 28000 | 23100 | 24000 | 27000 | 27000 | 1.037 | 49000 | 57750 | 48000 | 54000 | 57750 | 0.84848 | 84000 | 69300 | 48000 | 54000 | 69300 | 1.2121 | 105000 | 103950 | 72000 | 108000 | 108000 | 0.97222
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | NP | 8500 | 8400 | 8000 | NP | 17000 | 16800 | 16000 | NP | 16800 | 1.0119 | 29750 | 42000 | 32000 | NP | 42000 | 0.70833 | 51000 | 50400 | 32000 | NP | 50400 | 1.0119 | 63750 | 75600 | 48000 | NP | 75600 | 0.84325
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 15000 | 12600 | 12000 | 13500 | 30000 | 25200 | 24000 | 27000 | 27000 | 1.1111 | 52500 | 63000 | 48000 | 54000 | 63000 | 0.83333 | 90000 | 75600 | 48000 | 54000 | 75600 | 1.1905 | 112500 | 113400 | 72000 | 108000 | 113400 | 0.99206
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 1 | 1 | 2 | 11500 | 8925 | 7500 | 10500 | 23000 | 17850 | NP | 21000 | 21000 | 1.0952 | 40250 | NP | NP | 42000 | 42000 | 0.95833 | 69000 | 53550 | 15000 | 42000 | 53550 | 1.2885 | 86250 | 80325 | 30000 | 84000 | 84000 | 1.0268
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 1 | 1 | 1 | NP | 5500 | 4200 | 5000 | NP | NP | 8400 | NP | NP | 8400 | NP | NP | NP | NP | NP | 0 | NP | 33000 | 25200 | 10000 | NP | 25200 | 1.3095 | 41250 | 37800 | 20000 | NP | 37800 | 1.0913
A-2 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 3 | UL | 12 | UL | 5700 | UL | 29900 | UL | 11400 | UL | 59800 | UL | 1 | UL | 28500 | UL | 119600 | UL | 1 | UL | 34200 | UL | 119600 | UL | 1 | UL | 51300 | UL | 239200 | UL | 1
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 2 | 2 | 2 | 15500 | 3750 | 12000 | 13500 | 31000 | 7500 | 24000 | 27000 | 27000 | 1.1481 | 54250 | 18750 | 48000 | 54000 | 54000 | 1.0046 | 93000 | 22500 | 48000 | 54000 | 54000 | 1.7222 | 116250 | 33750 | 72000 | 108000 | 108000 | 1.0764
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 1 | 2 | 1 | 9500 | 2400 | 8000 | 9100 | 19000 | NP | 16000 | NP | 16000 | 1.1875 | 33250 | NP | 32000 | NP | 32000 | 1.0391 | 57000 | 14400 | 32000 | 18200 | 32000 | 1.7812 | 71250 | 21600 | 48000 | 36400 | 48000 | 1.4844
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 2 | 2 | 2 | 14000 | 3300 | 12000 | 13500 | 28000 | NP | 24000 | 27000 | 27000 | 1.037 | 49000 | 16500 | 48000 | 54000 | 54000 | 0.90741 | 84000 | 19800 | 48000 | 54000 | 54000 | 1.5556 | 105000 | 29700 | 72000 | 108000 | 108000 | 0.97222
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 1 | 2 | 1 | 9500 | 2400 | 8000 | 9100 | 19000 | 4800 | 16000 | NP | 16000 | 1.1875 | 33250 | NP | 32000 | NP | 32000 | 1.0391 | 57000 | 14400 | 32000 | 18200 | 32000 | 1.7812 | 71250 | 21600 | 48000 | 36400 | 48000 | 1.4844
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 2 | 2 | 2 | 15000 | 3600 | 12000 | 13500 | 30000 | 7200 | 24000 | 27000 | 27000 | 1.1111 | 52500 | 18000 | 48000 | 54000 | 54000 | 0.97222 | 90000 | 21600 | 48000 | 54000 | 54000 | 1.6667 | 112500 | 32400 | 72000 | 108000 | 108000 | 1.0417
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 1 | 1 | 2 | 11500 | 2550 | 7500 | 10500 | 23000 | NP | NP | 21000 | 21000 | 1.0952 | 40250 | NP | NP | 42000 | 42000 | 0.95833 | 69000 | 15300 | 15000 | 42000 | 42000 | 1.6429 | 86250 | 22950 | 30000 | 84000 | 84000 | 1.0268
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 1 | 1 | 1 | 1 | 6000 | 1200 | 5000 | 6000 | NP | 2400 | NP | NP | 2400 | NP | NP | NP | NP | NP | 0 | NP | 36000 | 7200 | 10000 | 12000 | 12000 | 3 | 45000 | 10800 | 20000 | 24000 | 24000 | 1.875
A-3 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 5 | UL | 12 | UL | 19950 | UL | 29900 | UL | NP | UL | 59800 | UL | 1 | UL | 99750 | UL | 119600 | UL | 1 | UL | 119700 | UL | 119600 | UL | 1 | UL | 179550 | UL | 239200 | UL | 1
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 15500 | 13125 | 12000 | 13500 | 31000 | 26250 | 24000 | 27000 | 27000 | 1.1481 | 54250 | 65625 | 48000 | 54000 | 65625 | 0.82667 | 93000 | 78750 | 48000 | 54000 | 78750 | 1.181 | 116250 | 118125 | 72000 | 108000 | 118125 | 0.98413
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | 1 | 9500 | 8400 | 8000 | 9100 | 19000 | NP | 16000 | NP | 16000 | 1.1875 | 33250 | 42000 | 32000 | NP | 42000 | 0.79167 | 57000 | 50400 | 32000 | 18200 | 50400 | 1.131 | 71250 | 75600 | 48000 | 36400 | 75600 | 0.94246
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 14000 | 11550 | 12000 | 13500 | 28000 | NP | 24000 | 27000 | 27000 | 1.037 | 49000 | 57750 | 48000 | 54000 | 57750 | 0.84848 | 84000 | 69300 | 48000 | 54000 | 69300 | 1.2121 | 105000 | 103950 | 72000 | 108000 | 108000 | 0.97222
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | 1 | 9500 | 8400 | 8000 | 9100 | 19000 | 16800 | 16000 | NP | 16800 | 1.131 | 33250 | 42000 | 32000 | NP | 42000 | 0.79167 | 57000 | 50400 | 32000 | 18200 | 50400 | 1.131 | 71250 | 75600 | 48000 | 36400 | 75600 | 0.94246
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 15000 | 12600 | 12000 | 13500 | 30000 | 25200 | 24000 | 27000 | 27000 | 1.1111 | 52500 | 63000 | 48000 | 54000 | 63000 | 0.83333 | 90000 | 75600 | 48000 | 54000 | 75600 | 1.1905 | 112500 | 113400 | 72000 | 108000 | 113400 | 0.99206
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 1 | 2 | 2 | 11500 | 8925 | 7500 | 10500 | 23000 | 17850 | 15000 | 21000 | 21000 | 1.0952 | 40250 | NP | 30000 | 42000 | 42000 | 0.95833 | 69000 | 53550 | 30000 | 42000 | 53550 | 1.2885 | 86250 | 80325 | 45000 | 84000 | 84000 | 1.0268
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 1 | 1 | 2 | 1 | 6000 | 4200 | 5000 | 6000 | NP | 8400 | 10000 | NP | 10000 | NP | NP | NP | 20000 | NP | 20000 | NP | 36000 | 25200 | 20000 | 12000 | 25200 | 1.4286 | 45000 | 37800 | 30000 | 24000 | 37800 | 1.1905
A-4 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 5 | UL | 12 | UL | 19950 | UL | 29900 | UL | 39900 | UL | 59800 | UL | 1 | UL | 99750 | UL | 119600 | UL | 1 | UL | 119700 | UL | 119600 | UL | 1 | UL | 179550 | UL | 239200 | UL | 1
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 15500 | 13125 | 12000 | 13500 | 31000 | 26250 | 24000 | 27000 | 27000 | 1.1481 | 54250 | 65625 | 48000 | 54000 | 65625 | 0.82667 | 93000 | 78750 | 48000 | 54000 | 78750 | 1.181 | 116250 | 118125 | 72000 | 108000 | 118125 | 0.98413
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | 1 | 9500 | 8400 | 8000 | 9100 | 19000 | NP | 16000 | NP | 16000 | 1.1875 | 33250 | 42000 | 32000 | NP | 42000 | 0.79167 | 57000 | 50400 | 32000 | 18200 | 50400 | 1.131 | 71250 | 75600 | 48000 | 36400 | 75600 | 0.94246
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 14000 | 11550 | 12000 | 13500 | 28000 | NP | 24000 | 27000 | 27000 | 1.037 | 49000 | 57750 | 48000 | 54000 | 57750 | 0.84848 | 84000 | 69300 | 48000 | 54000 | 69300 | 1.2121 | 105000 | 103950 | 72000 | 108000 | 108000 | 0.97222
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | 1 | 9500 | 8400 | 8000 | 9100 | 19000 | 16800 | 16000 | NP | 16800 | 1.131 | 33250 | 42000 | 32000 | NP | 42000 | 0.79167 | 57000 | 50400 | 32000 | 18200 | 50400 | 1.131 | 71250 | 75600 | 48000 | 36400 | 75600 | 0.94246
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 15000 | 12600 | 12000 | 13500 | 30000 | 25200 | 24000 | 27000 | 27000 | 1.1111 | 52500 | 63000 | 48000 | 54000 | 63000 | 0.83333 | 90000 | 75600 | 48000 | 54000 | 75600 | 1.1905 | 112500 | 113400 | 72000 | 108000 | 113400 | 0.99206
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 1 | 1 | 2 | 11500 | 8925 | 7500 | 10500 | 23000 | 17850 | NP | 21000 | 21000 | 1.0952 | 40250 | NP | NP | 42000 | 42000 | 0.95833 | 69000 | 53550 | 15000 | 42000 | 53550 | 1.2885 | 86250 | 80325 | 30000 | 84000 | 84000 | 1.0268
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 1 | 1 | 1 | 1 | 6000 | 4200 | 5000 | 6000 | NP | 8400 | NP | NP | 8400 | NP | NP | NP | NP | NP | 0 | NP | 36000 | 25200 | 10000 | 12000 | 25200 | 1.4286 | 45000 | 37800 | 20000 | 24000 | 37800 | 1.1905
A-5 | IB | Y | Y | Y | Y | Y | Y | Y | Y | UL |  | UL | 12 | UL |  | UL | 29000 | UL | 0 | UL | 58000 | UL | 1 | UL | 0 | UL | 116000 | UL | 1 | UL | 0 | UL | 116000 | UL | 1 | UL | 0 | UL | 232000 | UL | 1
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | UL |  | 2 | 2 | UL |  | 12000 | 13500 | UL | 0 | 24000 | 27000 | 27000 | INF | UL | 0 | 48000 | 54000 | 54000 | INF | UL | 0 | 48000 | 54000 | 54000 | INF | UL | 0 | 72000 | 108000 | 108000 | INF
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | UL |  | 2 | 1 | UL |  | 8000 | 9100 | UL | NP | 16000 | NP | 16000 | INF | UL | 0 | 32000 | NP | 32000 | INF | UL | 0 | 32000 | 18200 | 32000 | INF | UL | 0 | 48000 | 36400 | 48000 | INF
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | UL |  | 2 | 2 | UL |  | 12000 | 13500 | UL | NP | 24000 | 27000 | 27000 | INF | UL | 0 | 48000 | 54000 | 54000 | INF | UL | 0 | 48000 | 54000 | 54000 | INF | UL | 0 | 72000 | 108000 | 108000 | INF
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | UL |  | 2 | 1 | UL |  | 8000 | 9100 | UL | 0 | 16000 | NP | 16000 | INF | UL | 0 | 32000 | NP | 32000 | INF | UL | 0 | 32000 | 18200 | 32000 | INF | UL | 0 | 48000 | 36400 | 48000 | INF
| IV | Y | Y | Y | Y | Y | Y | Y | Y | UL |  | 2 | 2 | UL |  | 12000 | 13500 | UL | 0 | 24000 | 27000 | 27000 | INF | UL | 0 | 48000 | 54000 | 54000 | INF | UL | 0 | 48000 | 54000 | 54000 | INF | UL | 0 | 72000 | 108000 | 108000 | INF
| VA | Y | Y | Y | Y | Y | Y | Y | Y | UL |  | 1 | 2 | UL |  | 7500 | 10500 | UL | 0 | NP | 21000 | 21000 | INF | UL | 0 | NP | 42000 | 42000 | INF | UL | 0 | 15000 | 42000 | 42000 | INF | UL | 0 | 30000 | 84000 | 84000 | INF
| VB | Y | Y | Y | Y | Y | Y | Y | Y | UL |  | 1 | 1 | UL |  | 5000 | 6000 | UL | 0 | NP | NP | 0 | INF | UL | 0 | NP | NP | 0 | INF | UL | 0 | 10000 | 12000 | 12000 | INF | UL | 0 | 20000 | 24000 | 24000 | INF
B | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 7 | UL | 12 | UL | 34200 | UL | 39900 | UL | 68400 | UL | 79800 | UL | 1 | UL | 171000 | UL | 159600 | UL | 1 | UL | 205200 | UL | 159600 | UL | 1 | UL | 307800 | UL | 319200 | UL | 1
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 5 | 5 | 5 | 4 | 37500 | 22500 | 25500 | 18000 | 75000 | 45000 | 51000 | 36000 | 51000 | 1.4706 | 131250 | 112500 | 102000 | 72000 | 112500 | 1.1667 | 225000 | 135000 | 102000 | 72000 | 135000 | 1.6667 | 281250 | 202500 | 153000 | 144000 | 202500 | 1.3889
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 5 | 2 | 23000 | 14400 | 17000 | 12000 | 46000 | 28800 | 34000 | 24000 | 34000 | 1.3529 | 80500 | 72000 | 68000 | 48000 | 72000 | 1.1181 | 138000 | 86400 | 68000 | 48000 | 86400 | 1.5972 | 172500 | 129600 | 102000 | 96000 | 129600 | 1.331
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 5 | 4 | 5 | 4 | 28500 | 19800 | 21000 | 18000 | 57000 | 39600 | 42000 | 36000 | 42000 | 1.3571 | 99750 | 99000 | 84000 | 72000 | 99000 | 1.0076 | 171000 | 118800 | 84000 | 72000 | 118800 | 1.4394 | 213750 | 178200 | 126000 | 144000 | 178200 | 1.1995
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 5 | 2 | 19000 | 14400 | 14000 | 12000 | 38000 | 28800 | 28000 | 24000 | 28800 | 1.3194 | 66500 | 72000 | 56000 | 48000 | 72000 | 0.92361 | 114000 | 86400 | 56000 | 48000 | 86400 | 1.3194 | 142500 | 129600 | 84000 | 96000 | 129600 | 1.0995
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 5 | 5 | 5 | 4 | 36000 | 21600 | 25500 | 18000 | 72000 | 43200 | 51000 | 36000 | 51000 | 1.4118 | 126000 | 108000 | 102000 | 72000 | 108000 | 1.1667 | 216000 | 129600 | 102000 | 72000 | 129600 | 1.6667 | 270000 | 194400 | 153000 | 144000 | 194400 | 1.3889
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 3 | 18000 | 15300 | 13500 | 14000 | 36000 | 30600 | 27000 | 28000 | 30600 | 1.1765 | 63000 | 76500 | 54000 | 56000 | 76500 | 0.82353 | 108000 | 91800 | 54000 | 56000 | 91800 | 1.1765 | 135000 | 137700 | 81000 | 112000 | 137700 | 0.98039
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | 2 | 9000 | 7200 | 9000 | 8000 | 18000 | 14400 | 18000 | 16000 | 18000 | 1 | 31500 | 36000 | 36000 | 32000 | 36000 | 0.875 | 54000 | 43200 | 36000 | 32000 | 43200 | 1.25 | 67500 | 64800 | 54000 | 64000 | 64800 | 1.0417
E | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 5 | UL | 4 | UL | 34200 | UL | 45200 | UL | 68400 | UL | 90400 | UL | 1 | UL | 171000 | UL | 180800 | UL | 1 | UL | 205200 | UL | 180800 | UL | 1 | UL | 307800 | UL | 361600 | UL | 1
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 26500 | 22500 | 18000 | 20200 | 53000 | 45000 | 36000 | 40400 | 45000 | 1.1778 | 92750 | 112500 | 72000 | 80800 | 112500 | 0.82444 | 159000 | 135000 | 72000 | 80800 | 135000 | 1.1778 | 198750 | 202500 | 108000 | 161600 | 202500 | 0.98148
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 1 | 1 | 14500 | 14400 | 12000 | 13500 | 29000 | 28800 | NP | NP | 28800 | 1.0069 | 50750 | 72000 | NP | NP | 72000 | 0.70486 | 87000 | 86400 | 24000 | 27000 | 86400 | 1.0069 | 108750 | 129600 | 48000 | 54000 | 129600 | 0.83912
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 23500 | 19800 | 18000 | 20200 | 47000 | 39600 | 36000 | 40400 | 40400 | 1.1634 | 82250 | 99000 | 72000 | 80800 | 99000 | 0.83081 | 141000 | 118800 | 72000 | 80800 | 118800 | 1.1869 | 176250 | 178200 | 108000 | 161600 | 178200 | 0.98906
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 1 | 1 | 14500 | 14400 | 12000 | 13500 | 29000 | 28800 | NP | NP | 28800 | 1.0069 | 50750 | 72000 | NP | NP | 72000 | 0.70486 | 87000 | 86400 | 24000 | 27000 | 86400 | 1.0069 | 108750 | 129600 | 48000 | 54000 | 129600 | 0.83912
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 25500 | 21600 | 18000 | 20200 | 51000 | 43200 | 36000 | 40400 | 43200 | 1.1806 | 89250 | 108000 | 72000 | 80800 | 108000 | 0.82639 | 153000 | 129600 | 72000 | 80800 | 129600 | 1.1806 | 191250 | 194400 | 108000 | 161600 | 194400 | 0.9838
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 1 | 1 | 2 | 2 | 18500 | 15300 | 12000 | 15700 | NP | 30600 | 24000 | 31400 | 31400 | NP | NP | NP | 48000 | 62800 | 62800 | NP | 111000 | 91800 | 48000 | 62800 | 91800 | 1.2092 | 138750 | 137700 | 72000 | 125600 | 137700 | 1.0076
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 1 | 1 | 1 | 1 | 9500 | 7200 | 8000 | 9100 | NP | 14400 | NP | NP | 14400 | NP | NP | NP | NP | NP | 0 | NP | 57000 | 43200 | 16000 | 18200 | 43200 | 1.3194 | 71250 | 64800 | 32000 | 36400 | 64800 | 1.0995
F-1 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 6 | UL | 12 | UL | 22800 | UL | 39900 | UL | 45600 | UL | 79800 | UL | 1 | UL | 114000 | UL | 159600 | UL | 1 | UL | 136800 | UL | 159600 | UL | 1 | UL | 205200 | UL | 319200 | UL | 1
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 4 | 4 | 25000 | 15000 | 31500 | 18000 | 50000 | 30000 | 63000 | 36000 | 63000 | 0.79365 | 87500 | 75000 | 126000 | 72000 | 126000 | 0.69444 | 150000 | 90000 | 126000 | 72000 | 126000 | 1.1905 | 187500 | 135000 | 189000 | 144000 | 189000 | 0.99206
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 4 | 2 | 15500 | 9600 | 21000 | 12000 | 31000 | NP | 42000 | 24000 | 42000 | 0.7381 | 54250 | 48000 | 84000 | 48000 | 84000 | 0.64583 | 93000 | 57600 | 84000 | 48000 | 84000 | 1.1071 | 116250 | 86400 | 126000 | 96000 | 126000 | 0.92262
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 4 | 4 | 19000 | 13200 | 22500 | 18000 | 38000 | NP | 45000 | 36000 | 45000 | 0.84444 | 66500 | 66000 | 90000 | 72000 | 90000 | 0.73889 | 114000 | 79200 | 90000 | 72000 | 90000 | 1.2667 | 142500 | 118800 | 135000 | 144000 | 144000 | 0.98958
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 4 | 2 | 12000 | 9600 | 15000 | 12000 | 24000 | 19200 | 30000 | 24000 | 30000 | 0.8 | 42000 | 48000 | 60000 | 48000 | 60000 | 0.7 | 72000 | 57600 | 60000 | 48000 | 60000 | 1.2 | 90000 | 86400 | 90000 | 96000 | 96000 | 0.9375
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 6 | 4 | 33500 | 14400 | 31500 | 18000 | 67000 | 28800 | 63000 | 36000 | 63000 | 1.0635 | 117250 | 72000 | 126000 | 72000 | 126000 | 0.93056 | 201000 | 86400 | 126000 | 72000 | 126000 | 1.5952 | 251250 | 129600 | 189000 | 144000 | 189000 | 1.3294
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 1 | 3 | 14000 | 10200 | 15000 | 14000 | 28000 | 20400 | NP | 28000 | 28000 | 1 | 49000 | 51000 | NP | 56000 | 56000 | 0.875 | 84000 | 61200 | 30000 | 56000 | 61200 | 1.3725 | 105000 | 91800 | 60000 | 112000 | 112000 | 0.9375
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 1 | 1 | 1 | 2 | 8500 | 4800 | 10000 | 8000 | NP | 9600 | NP | 16000 | 16000 | NP | NP | NP | NP | 32000 | 32000 | NP | 51000 | 28800 | 20000 | 32000 | 32000 | 1.5938 | 63750 | 43200 | 40000 | 64000 | 64000 | 0.99609
F-2 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 7 | UL | 12 | UL | 34200 | UL | 59900 | UL | 68400 | UL | 119800 | UL | 1 | UL | 171000 | UL | 239600 | UL | 1 | UL | 205200 | UL | 239600 | UL | 1 | UL | 307800 | UL | 479200 | UL | 1
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 5 | 5 | 4 | 4 | 37500 | 22500 | 31500 | 27000 | 75000 | 45000 | 63000 | 54000 | 63000 | 1.1905 | 131250 | 112500 | 126000 | 108000 | 126000 | 1.0417 | 225000 | 135000 | 126000 | 108000 | 135000 | 1.6667 | 281250 | 202500 | 189000 | 216000 | 216000 | 1.3021
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 4 | 2 | 23000 | 14400 | 21000 | 18000 | 46000 | 28800 | 42000 | 36000 | 42000 | 1.0952 | 80500 | 72000 | 84000 | 72000 | 84000 | 0.95833 | 138000 | 86400 | 84000 | 72000 | 86400 | 1.5972 | 172500 | 129600 | 126000 | 144000 | 144000 | 1.1979
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 4 | 4 | 28500 | 19800 | 22500 | 27000 | 57000 | NP | 45000 | 54000 | 54000 | 1.0556 | 99750 | 99000 | 90000 | 108000 | 108000 | 0.92361 | 171000 | 118800 | 90000 | 108000 | 118800 | 1.4394 | 213750 | 178200 | 135000 | 216000 | 216000 | 0.98958
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 4 | 2 | 18000 | 14400 | 15000 | 18000 | 36000 | 28800 | 30000 | 36000 | 36000 | 1 | 63000 | 72000 | 60000 | 72000 | 72000 | 0.875 | 108000 | 86400 | 60000 | 72000 | 86400 | 1.25 | 135000 | 129600 | 90000 | 144000 | 144000 | 0.9375
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 5 | 5 | 6 | 4 | 50500 | 21600 | 31500 | 27000 | 101000 | 43200 | 63000 | 54000 | 63000 | 1.6032 | 176750 | 108000 | 126000 | 108000 | 126000 | 1.4028 | 303000 | 129600 | 126000 | 108000 | 129600 | 2.338 | 378750 | 194400 | 189000 | 216000 | 216000 | 1.7535
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 1 | 3 | 21000 | 15300 | 15000 | 21000 | 42000 | 30600 | NP | 42000 | 42000 | 1 | 73500 | 76500 | NP | 84000 | 84000 | 0.875 | 126000 | 91800 | 30000 | 84000 | 91800 | 1.3725 | 157500 | 137700 | 60000 | 168000 | 168000 | 0.9375
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 1 | 2 | 13000 | 7200 | 10000 | 12000 | 26000 | 14400 | NP | 24000 | 24000 | 1.0833 | 45500 | 36000 | NP | 48000 | 48000 | 0.94792 | 78000 | 43200 | 20000 | 48000 | 48000 | 1.625 | 97500 | 64800 | 40000 | 96000 | 96000 | 1.0156
H-1 | 1A | N | N | Y | N | N | N | N | N | 1 | 1 | 1 | 1 | 21000 | 14400 | 5000 | 15000 | NP | 28800 | NP | NP | 28800 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
| IB | N | N | Y | N | N | N | N | N | 1 | 1 | 1 | 1 | 16500 | 11400 | 4000 | 12400 | NP | 22800 | NP | NP | 22800 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
| IIA | N | N | Y | N | N | N | N | N | 1 | 1 | 1 | 1 | 11000 | 7500 | 2500 | 5600 | NP | 15000 | NP | NP | 15000 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
| IIB | N | N | Y | N | N | N | N | N | 1 | 1 | 1 | 1 | 7000 | 4800 | 1666.6667 | 3700 | NP | 9600 | NP | NP | 9600 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
| IIIA | N | N | Y | N | N | N | N | N | 1 | 1 | 1 | NP | 9500 | 6600 | 2500 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
| IIIB | N | N | Y | N | N | N | N | N | 1 | 1 | NP | NP | 7000 | 4800 | NP | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
| IV | N | N | Y | N | N | N | N | N | 1 | 1 | 1 | NP | 10500 | 7200 | 2500 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
| VA | N | N | Y | N | N | N | N | N | 1 | 1 | NP | NP | 7500 | 5100 | NP | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
| VB | N | N | Y | N | N | N | N | N | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
H-2 | 1A | N | N | Y | N | N | N | N | N | UL | 3 | 1 | UL | 21000 | 14400 | 5000 | 15000 | 42000 | NP | NP | 30000 | 30000 | 1.4 | 73500 | 72000 | NP | 60000 | 72000 | 1.0208 | 42000 | 28800 | NP | 30000 | 30000 | 1.4 | 73500 | 72000 | NP | 60000 | 72000 | 1.0208
| IB | N | N | Y | N | N | N | N | N | 3 | 3 | 1 | 2 | 16500 | 11400 | 4000 | 12400 | 33000 | NP | NP | 24800 | 24800 | 1.3306 | 57750 | 57000 | NP | 49600 | 57000 | 1.0132 | 33000 | 22800 | NP | 24800 | 24800 | 1.3306 | 57750 | 57000 | NP | 49600 | 57000 | 1.0132
| IIA | N | N | Y | N | N | N | N | N | 2 | 2 | 1 | 1 | 11000 | 7500 | 2500 | 5600 | 22000 | NP | NP | NP | 0 | LNP | 38500 | 37500 | NP | NP | 37500 | 1.0267 | 22000 | 15000 | NP | NP | 15000 | 1.4667 | 38500 | 37500 | NP | NP | 37500 | 1.0267
| IIB | N | N | Y | N | N | N | N | N | 1 | 1 | 1 | 1 | 7000 | 4800 | 1666.6667 | 3700 | NP | 9600 | NP | NP | 9600 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
| IIIA | N | N | Y | N | N | N | N | N | 2 | 2 | 1 | 1 | 9500 | 6600 | 2500 | 5600 | 19000 | 13200 | NP | NP | 13200 | 1.4394 | 33250 | 33000 | NP | NP | 33000 | 1.0076 | 19000 | 13200 | NP | NP | 13200 | 1.4394 | 33250 | 33000 | NP | NP | 33000 | 1.0076
| IIIB | N | N | Y | N | N | N | N | N | 1 | 1 | 1 | 1 | 7000 | 4800 | 1333.3333 | 3700 | NP | 9600 | NP | NP | 9600 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
| IV | N | N | Y | N | N | N | N | N | 2 | 2 | 1 | 1 | 10500 | 7200 | 2500 | 5600 | 21000 | 14400 | NP | NP | 14400 | 1.4583 | 36750 | 36000 | NP | NP | 36000 | 1.0208 | 21000 | 14400 | NP | NP | 14400 | 1.4583 | 36750 | 36000 | NP | NP | 36000 | 1.0208
| VA | N | N | Y | N | N | N | N | N | 1 | 1 | 1 | 1 | 7500 | 5100 | 833.3333 | 4400 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
| VB | N | N | Y | N | N | N | N | N | 1 | NP | NP | 1 | 3000 | NP | NP | 2500 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
H-3 | IA | N | N | Y | N | N | N | N | N | UL | 7 | Y | UL | UL | 28800 | 10000 | UL | UL | NP | 20000 | UL | UL | 1 | UL | 144000 | 40000 | UL | UL | 1 | UL | 57600 | 40000 | UL | UL | 1 | UL | 144000 | 60000 | UL | UL | 1
| IB | N | N | Y | N | N | N | N | N | 6 | 6 | 3 | 5 | 60000 | 22800 | 6666.6667 | 24800 | 120000 | 45600 | 13333.3333 | 49600 | 49600 | 2.4194 | 210000 | 114000 | 26666.6667 | 99200 | 114000 | 1.8421 | 120000 | 45600 | 26666.6667 | 49600 | 49600 | 2.4194 | 210000 | 114000 | 40000 | 99200 | 114000 | 1.8421
| IIA | N | N | Y | N | N | N | N | N | 4 | 4 | 2 | 2 | 26500 | 15000 | 3333.3333 | 11200 | 53000 | NP | 6666.6667 | 22400 | 22400 | 2.3661 | 92750 | 75000 | 13333.3333 | 44800 | 75000 | 1.2367 | 53000 | 30000 | 13333.3333 | 22400 | 30000 | 1.7667 | 92750 | 75000 | 20000 | 44800 | 75000 | 1.2367
| IIB | N | N | Y | N | N | N | N | N | 2 | 2 | 1 | 1 | 14000 | 9600 | 2500 | 7500 | 28000 | 19200 | NP | NP | 19200 | 1.4583 | 49000 | 48000 | NP | NP | 48000 | 1.0208 | 28000 | 19200 | NP | NP | 19200 | 1.4583 | 49000 | 48000 | NP | NP | 48000 | 1.0208
| IIIA | N | N | Y | N | N | N | N | N | 4 | 3 | 2 | 2 | 17500 | 13200 | 3333.3333 | 11200 | 35000 | 26400 | 6666.6667 | 22400 | 26400 | 1.3258 | 61250 | 66000 | 13333.3333 | 44800 | 66000 | 0.92803 | 35000 | 26400 | 13333.3333 | 22400 | 26400 | 1.3258 | 61250 | 66000 | 20000 | 44800 | 66000 | 0.92803
| IIIB | N | N | Y | N | N | N | N | N | 2 | 2 | 1 | 1 | 13000 | 9600 | 2500 | 7500 | 26000 | 19200 | NP | NP | 19200 | 1.3542 | 45500 | 48000 | NP | NP | 48000 | 0.94792 | 26000 | 19200 | NP | NP | 19200 | 1.3542 | 45500 | 48000 | NP | NP | 48000 | 0.94792
| IV | N | N | Y | N | N | N | N | N | 4 | 4 | 2 | 2 | 25500 | 14400 | 3333.3333 | 11200 | 51000 | 28800 | 6666.6667 | 22400 | 28800 | 1.7708 | 89250 | 72000 | 13333.3333 | 44800 | 72000 | 1.2396 | 51000 | 28800 | 13333.3333 | 22400 | 28800 | 1.7708 | 89250 | 72000 | 20000 | 44800 | 72000 | 1.2396
| VA | N | N | Y | N | N | N | N | N | 2 | 2 | 1 | 2 | 10000 | 10200 | 1333.3333 | 8800 | 20000 | 20400 | NP | 17600 | 20400 | 0.98039 | 35000 | 51000 | NP | 35200 | 51000 | 0.68627 | 20000 | 20400 | NP | 17600 | 20400 | 0.98039 | 35000 | 51000 | NP | 35200 | 51000 | 0.68627
| VB | N | N | Y | N | N | N | N | N | 1 | 1 | NP | 1 | 5000 | 4800 | NP | 5100 | NP | 9600 | NP | NP | 9600 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
H-4 | IB | Y | Y | Y | Y | Y | Y | N | N | 7 | 7 | 6 | 3 | UL | 34200 | UL | 39900 | UL | 68400 | UL | 79800 | UL | 1 | UL | 171000 | UL | 159600 | UL | 1 | UL | 205200 | UL | 159600 | UL | 1 | UL | 307800 | UL | 319200 | UL | 1
| IIA | Y | Y | Y | Y | Y | Y | N | N | 5 | 5 | 4 | 3 | 37000 | 22500 | 48000 | 18000 | 74000 | 45000 | 96000 | 36000 | 96000 | 0.77083 | 129500 | 112500 | 192000 | 72000 | 192000 | 0.67448 | 222000 | 135000 | 192000 | 72000 | 192000 | 1.1562 | 277500 | 202500 | 288000 | 144000 | 288000 | 0.96354
| IIB | Y | Y | Y | Y | Y | Y | N | N | 3 | 3 | 4 | 2 | 17500 | 14400 | 32000 | 12000 | 35000 | 28800 | 64000 | 24000 | 64000 | 0.54688 | 61250 | 72000 | 128000 | 48000 | 128000 | 0.47852 | 105000 | 86400 | 128000 | 48000 | 128000 | 0.82031 | 131250 | 129600 | 192000 | 96000 | 192000 | 0.68359
| IIIA | Y | Y | Y | Y | Y | Y | N | N | 5 | 4 | 4 | 3 | 28500 | 19800 | 48000 | 18000 | 57000 | NP | 96000 | 36000 | 96000 | 0.59375 | 99750 | 99000 | 192000 | 72000 | 192000 | 0.51953 | 171000 | 118800 | 192000 | 72000 | 192000 | 0.89062 | 213750 | 178200 | 288000 | 144000 | 288000 | 0.74219
| IIIB | Y | Y | Y | Y | Y | Y | N | N | 3 | 3 | 4 | 2 | 17500 | 14400 | 32000 | 12000 | 35000 | 28800 | 64000 | 24000 | 64000 | 0.54688 | 61250 | 72000 | 128000 | 48000 | 128000 | 0.47852 | 105000 | 86400 | 128000 | 48000 | 128000 | 0.82031 | 131250 | 129600 | 192000 | 96000 | 192000 | 0.68359
| IV | Y | Y | Y | Y | Y | Y | N | N | 5 | 5 | 3 | 3 | 36000 | 21600 | 48000 | 18000 | 72000 | 43200 | 96000 | 36000 | 96000 | 0.75 | 126000 | 108000 | 192000 | 72000 | 192000 | 0.65625 | 216000 | 129600 | 192000 | 72000 | 192000 | 1.125 | 270000 | 194400 | 288000 | 144000 | 288000 | 0.9375
| VA | Y | Y | Y | Y | Y | Y | N | N | 3 | 3 | 1 | 3 | 18000 | 15300 | 27000 | 14000 | 36000 | 30600 | NP | 28000 | 30600 | 1.1765 | 63000 | 76500 | NP | 56000 | 76500 | 0.82353 | 108000 | 91800 | NP | 56000 | 91800 | 1.1765 | 135000 | 137700 | NP | 112000 | 137700 | 0.98039
| VB | Y | Y | Y | Y | Y | Y | N | N | 2 | 2 | 1 | 1 | 6500 | 7200 | 18000 | 8000 | 13000 | 14400 | NP | NP | 14400 | 0.90278 | 22750 | 36000 | NP | NP | 36000 | 0.63194 | 39000 | 43200 | NP | NP | 43200 | 0.90278 | 48750 | 64800 | NP | NP | 64800 | 0.75231
H-5 | IB | Y | Y | Y | Y | N | Y | N | N | 3 | 7 | 3 | 3 | UL | 34400 | UL | 39900 | UL | 68800 | UL | 79800 | UL | 1 | UL | 172000 | UL | 159600 | UL | 1 | UL | 206400 | UL | 159600 | UL | 1 | UL | 309600 | UL | 319200 | UL | 1
| IIA | Y | Y | Y | Y | N | Y | N | N | 3 | 5 | 3 | 3 | 37500 | 22500 | 63000 | 18000 | 75000 | 45000 | 126000 | 36000 | 126000 | 0.59524 | 131250 | 112500 | 252000 | 72000 | 252000 | 0.52083 | 225000 | 135000 | 252000 | 72000 | 252000 | 0.89286 | 281250 | 202500 | 378000 | 144000 | 378000 | 0.74405
| IIB | Y | Y | Y | Y | N | Y | N | N | 3 | 3 | 3 | 2 | 23000 | 14400 | 42000 | 12000 | 46000 | 28800 | 84000 | 24000 | 84000 | 0.54762 | 80500 | 72000 | 168000 | 48000 | 168000 | 0.47917 | 138000 | 86400 | 168000 | 48000 | 168000 | 0.82143 | 172500 | 129600 | 252000 | 96000 | 252000 | 0.68452
| IIIA | Y | Y | Y | Y | N | Y | N | N | 3 | 4 | 3 | 3 | 28500 | 19800 | 45000 | 18000 | 57000 | 39600 | 90000 | 36000 | 90000 | 0.63333 | 99750 | 99000 | 180000 | 72000 | 180000 | 0.55417 | 171000 | 118800 | 180000 | 72000 | 180000 | 0.95 | 213750 | 178200 | 270000 | 144000 | 270000 | 0.79167
| IIIB | Y | Y | Y | Y | N | Y | N | N | 3 | 3 | 3 | 2 | 19000 | 14400 | 30000 | 12000 | 38000 | 28800 | 60000 | 24000 | 60000 | 0.63333 | 66500 | 72000 | 120000 | 48000 | 120000 | 0.55417 | 114000 | 86400 | 120000 | 48000 | 120000 | 0.95 | 142500 | 129600 | 180000 | 96000 | 180000 | 0.79167
| IV | Y | Y | Y | Y | N | Y | N | N | 3 | 5 | 3 | 3 | 36000 | 21600 | 63000 | 18000 | 72000 | 43200 | 126000 | 36000 | 126000 | 0.57143 | 126000 | 108000 | 252000 | 72000 | 252000 | 0.5 | 216000 | 129600 | 252000 | 72000 | 252000 | 0.85714 | 270000 | 194400 | 378000 | 144000 | 378000 | 0.71429
| VA | Y | Y | Y | Y | N | Y | N | N | 3 | 3 | 1 | 3 | 18000 | 15300 | 45000 | 14000 | 36000 | 30600 | NP | 28000 | 30600 | 1.1765 | 63000 | 76500 | NP | 56000 | 76500 | 0.82353 | 108000 | 91800 | NP | 56000 | 91800 | 1.1765 | 135000 | 137700 | NP | 112000 | 137700 | 0.98039
| VB | Y | Y | Y | Y | N | Y | N | N | 2 | 2 | 1 | 1 | 9000 | 7200 | 45000 | 8000 | 18000 | 14400 | NP | NP | 14400 | 1.25 | 31500 | 36000 | NP | NP | 36000 | 0.875 | 54000 | 43200 | NP | NP | 43200 | 1.25 | 67500 | 64800 | NP | NP | 64800 | 1.0417
I-1 | IB | Y | Y |  | Y | Y | Y |  | Y | 9 | 9 |  | 3 | 55000 | 19950 |  | 15100 | 110000 | 39900 | 0 | 30200 | 39900 | 2.7569 | 192500 | 99750 | 0 | 60400 | 99750 | 1.9298 | 330000 | 119700 | 0 | 60400 | 119700 | 2.7569 | 412500 | 179550 | 0 | 120800 | 179550 | 2.2974
Ass't | IIA | Y | Y |  | Y | Y | Y |  | Y | 4 | 4 |  | 2 | 19000 | 13125 |  | 6800 | 38000 | 26250 | 0 | 13600 | 26250 | 1.4476 | 66500 | 65625 | 0 | 27200 | 65625 | 1.0133 | 114000 | 78750 | 0 | 27200 | 78750 | 1.4476 | 142500 | 118125 | 0 | 54400 | 118125 | 1.2063
| IIB | Y | Y |  | Y | Y | Y |  | Y | 3 | 3 |  | NP | 10000 | 8400 |  | NP | 20000 | 16800 | 0 | NP | 16800 | 1.1905 | 35000 | 42000 | 0 | NP | 42000 | 0.83333 | 60000 | 50400 | 0 | NP | 50400 | 1.1905 | 75000 | 75600 | 0 | NP | 75600 | 0.99206
| IIIA | Y | Y |  | Y | Y | Y |  | Y | 4 | 4 |  | 2 | 16500 | 11550 |  | 6800 | 33000 | 23100 | 0 | 13600 | 23100 | 1.4286 | 57750 | 57750 | 0 | 27200 | 57750 | 1 | 99000 | 69300 | 0 | 27200 | 69300 | 1.4286 | 123750 | 103950 | 0 | 54400 | 103950 | 1.1905
| IIIB | Y | Y |  | Y | Y | Y |  | Y | 3 | 3 |  | NP | 10000 | 8400 |  | NP | 20000 | 16800 | 0 | NP | 16800 | 1.1905 | 35000 | 42000 | 0 | NP | 42000 | 0.83333 | 60000 | 50400 | 0 | NP | 50400 | 1.1905 | 75000 | 75600 | 0 | NP | 75600 | 0.99206
| IV | Y | Y |  | Y | Y | Y |  | Y | 4 | 4 |  | 2 | 18000 | 12600 |  | 6800 | 36000 | 25200 | 0 | 13600 | 25200 | 1.4286 | 63000 | 63000 | 0 | 27200 | 63000 | 1 | 108000 | 75600 | 0 | 27200 | 75600 | 1.4286 | 135000 | 113400 | 0 | 54400 | 113400 | 1.1905
| VA | Y | Y |  | Y | Y | Y |  | Y | 3 | 3 |  | 2 | 10500 | 8925 |  | 5200 | 21000 | 17850 | 0 | 10400 | 17850 | 1.1765 | 36750 | 44625 | 0 | 20800 | 44625 | 0.82353 | 63000 | 53550 | 0 | 20800 | 53550 | 1.1765 | 78750 | 80325 | 0 | 41600 | 80325 | 0.98039
| VB | Y | Y |  | Y | Y | Y |  | Y | 2 | 2 |  | NP | 4500 | 4200 |  | NP | 9000 | 8400 | 0 | NP | 8400 | 1.0714 | 15750 | 21000 | 0 | NP | 21000 | 0.75 | 27000 | 25200 | 0 | NP | 25200 | 1.0714 | 33750 | 37800 | 0 | NP | 37800 | 0.89286
I-2 | IB | Y | Y | Y | Y | Y | Y | N | Y | 4 | 4 | UL | 3 | UL | 17100 | UL | 15100 | UL | 34200 | UL | 30200 | UL | 1 | UL | 85500 | UL | 60400 | UL | 1 | UL | 102600 | UL | 60400 | UL | 1 | UL | 153900 | UL | 120800 | UL | 1
Hos | IIA | Y | Y | Y | Y | Y | Y | N | N | 2 | 2 | 3 | 1 | 15000 | 11250 | 15000 | 6800 | 30000 | 22500 | 30000 | NP | 30000 | 1 | 52500 | 56250 | 60000 | NP | 60000 | 0.875 | 90000 | 67500 | 60000 | NP | 67500 | 1.3333 | 112500 | 101250 | 90000 | NP | 101250 | 1.1111
| IIB | Y | Y | Y | Y | N | N | N | Y | 1 | 1 | 1 | NP | 11000 | 7200 | 10000 | NP | NP | 14400 | NP | NP | 14400 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
| IIIA | Y | Y | Y | Y | N | N | N | N | 1 | 1 | 1 | 1 | 12000 | 9900 | 10500 | 6800 | NP | 19800 | NP | NP | 19800 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
| IIIB | Y | Y | Y | Y | N | Y | N | Y | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
| IV | Y | Y | Y | Y | N | N | N | N | 1 | 1 | 2 | 1 | 12000 | 10800 | 12000 | 6800 | NP | 21600 | 24000 | NP | 24000 | NP | NP | NP | 48000 | NP | 48000 | NP | NP | NP | 48000 | NP | 48000 | NP | NP | NP | 72000 | NP | 72000 | NP
| VA | Y | Y | Y | Y | N | N | N | N | 1 | 1 | 1 | 1 | 9500 | 7650 | 7500 | 5200 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
| VB | Y | Y | Y | Y | N | Y | N | Y | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
I-3 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | UL | 2 | UL | 14250 | UL | 15100 | UL | 28500 | UL | 30200 | UL | 1 | UL | 71250 | UL | 60400 | UL | 1 | UL | 85500 | UL | 60400 | UL | 1 | UL | 128250 | UL | 120800 | UL | 1
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 3 | NP | 15000 | 9375 | 15000 | NP | 30000 | NP | 30000 | NP | 30000 | 1 | 52500 | 46875 | 60000 | NP | 60000 | 0.875 | 90000 | 56250 | 60000 | NP | 60000 | 1.5 | 112500 | 84375 | 90000 | NP | 90000 | 1.25
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 1 | 1 | 2 | NP | 10000 | 6000 | 10000 | NP | NP | NP | 20000 | NP | 20000 | NP | NP | NP | 40000 | NP | 40000 | NP | 60000 | 36000 | 40000 | NP | 40000 | 1.5 | 75000 | 54000 | 60000 | NP | 60000 | 1.25
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 3 | NP | 10500 | 8250 | 10500 | NP | 21000 | 16500 | 21000 | NP | 21000 | 1 | 36750 | 41250 | 42000 | NP | 42000 | 0.875 | 63000 | 49500 | 42000 | NP | 49500 | 1.2727 | 78750 | 74250 | 63000 | NP | 74250 | 1.0606
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 1 | 1 | 2 | NP | 7500 | 6000 | 7000 | NP | NP | 12000 | 14000 | NP | 14000 | NP | NP | NP | 28000 | NP | 28000 | NP | 45000 | 36000 | 28000 | NP | 36000 | 1.25 | 56250 | 54000 | 42000 | NP | 54000 | 1.0417
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | NP | 12000 | 9000 | 12000 | NP | 24000 | 18000 | 24000 | NP | 24000 | 1 | 42000 | 45000 | 48000 | NP | 48000 | 0.875 | 72000 | 54000 | 48000 | NP | 54000 | 1.3333 | 90000 | 81000 | 72000 | NP | 81000 | 1.1111
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 1 | 3 | NP | 7500 | 6375 | 7500 | NP | 15000 | NP | 15000 | NP | 15000 | 1 | 26250 | NP | 30000 | NP | 30000 | 0.875 | 45000 | 38250 | 30000 | NP | 38250 | 1.1765 | 56250 | 57375 | 45000 | NP | 57375 | 0.98039
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 1 | NP | 2 | NP | 5000 | NP | 5000 | NP | NP | NP | 10000 | NP | 10000 | NP | NP | NP | 20000 | NP | 20000 | NP | 30000 | NP | 20000 | NP | 20000 | 1.5 | 37500 | NP | 30000 | NP | 30000 | 1.25
I-4 | IB | Y | Y |  | Y | Y | Y |  | Y | 5 | 5 |  | 4 | 60500 | 34200 |  | 45200 | 121000 | NP | 0 | 90400 | 90400 | 1.3385 | 211750 | 171000 | 0 | 180800 | 180800 | 1.1712 | 363000 | 205200 | 0 | 180800 | 205200 | 1.769 | 453750 | 307800 | 0 | 361600 | 361600 | 1.2548
| IIA | Y | Y |  | Y | Y | Y |  | Y | 3 | 3 |  | 2 | 26500 | 22500 |  | 20200 | 53000 | 45000 | 0 | 40400 | 45000 | 1.1778 | 92750 | 112500 | 0 | 80800 | 112500 | 0.82444 | 159000 | 135000 | 0 | 80800 | 135000 | 1.1778 | 198750 | 202500 | 0 | 161600 | 202500 | 0.98148
| IIB | Y | Y |  | Y | Y | Y |  | Y | 2 | 2 |  | 1 | 13000 | 14400 |  | 13500 | 26000 | NP | 0 | NP | 0 | LNP | 45500 | 72000 | 0 | NP | 72000 | 0.63194 | 78000 | 86400 | 0 | 27000 | 86400 | 0.90278 | 97500 | 129600 | 0 | 54000 | 129600 | 0.75231
| IIIA | Y | Y |  | Y | Y | Y |  | Y | 3 | 3 |  | 2 | 23500 | 19800 |  | 20200 | 47000 | 39600 | 0 | 40400 | 40400 | 1.1634 | 82250 | 99000 | 0 | 80800 | 99000 | 0.83081 | 141000 | 118800 | 0 | 80800 | 118800 | 1.1869 | 176250 | 178200 | 0 | 161600 | 178200 | 0.98906
| IIIB | Y | Y |  | Y | Y | Y |  | Y | 2 | 2 |  | 1 | 13000 | 14400 |  | 13500 | 26000 | 28800 | 0 | NP | 28800 | 0.90278 | 45500 | 72000 | 0 | NP | 72000 | 0.63194 | 78000 | 86400 | 0 | 27000 | 86400 | 0.90278 | 97500 | 129600 | 0 | 54000 | 129600 | 0.75231
| IV | Y | Y |  | Y | Y | Y |  | Y | 3 | 3 |  | 2 | 25500 | 21600 |  | 20200 | 51000 | 43200 | 0 | 40400 | 43200 | 1.1806 | 89250 | 108000 | 0 | 80800 | 108000 | 0.82639 | 153000 | 129600 | 0 | 80800 | 129600 | 1.1806 | 191250 | 194400 | 0 | 161600 | 194400 | 0.9838
| VA | Y | Y |  | Y | Y | Y |  | Y | 1 | 1 |  | 2 | 18500 | 15300 |  | 15700 | NP | 30600 | 0 | 31400 | 31400 | NP | NP | NP | 0 | 62800 | 62800 | NP | 111000 | 91800 | 0 | 62800 | 91800 | 1.2092 | 138750 | 137700 | 0 | 125600 | 137700 | 1.0076
| VB | Y | Y |  | Y | Y | Y |  | Y | 1 | 1 |  | 1 | 9000 | 7200 |  | 9100 | NP | 14400 | 0 | NP | 14400 | NP | NP | NP | 0 | NP | 0 | NP | 54000 | 43200 | 0 | 18200 | 43200 | 1.25 | 67500 | 64800 | 0 | 36400 | 64800 | 1.0417
M | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 6 | UL | 12 | UL | 22800 | 15000 | 39900 | UL | 45600 | 30000 | 79800 | 79800 | INF | UL | 114000 | 60000 | 159600 | 159600 | INF | UL | 136800 | 60000 | 159600 | 159600 | INF | UL | 205200 | 90000 | 319200 | 319200 | INF
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 5 | 4 | 21500 | 15000 | 13500 | 18000 | 43000 | 30000 | 27000 | 36000 | 36000 | 1.1944 | 75250 | 75000 | 54000 | 72000 | 75000 | 1.0033 | 129000 | 90000 | 54000 | 72000 | 90000 | 1.4333 | 161250 | 135000 | 81000 | 144000 | 144000 | 1.1198
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 2 | 5 | 2 | 12500 | 9600 | 9000 | 12000 | 25000 | NP | 18000 | 24000 | 24000 | 1.0417 | 43750 | 48000 | 36000 | 48000 | 48000 | 0.91146 | 75000 | 57600 | 36000 | 48000 | 57600 | 1.3021 | 93750 | 86400 | 54000 | 96000 | 96000 | 0.97656
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 5 | 4 | 18500 | 13200 | 13500 | 18000 | 37000 | NP | 27000 | 36000 | 36000 | 1.0278 | 64750 | 66000 | 54000 | 72000 | 72000 | 0.89931 | 111000 | 79200 | 54000 | 72000 | 79200 | 1.4015 | 138750 | 118800 | 81000 | 144000 | 144000 | 0.96354
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 2 | 5 | 2 | 12500 | 9600 | 9000 | 12000 | 25000 | 19200 | 18000 | 24000 | 24000 | 1.0417 | 43750 | 48000 | 36000 | 48000 | 48000 | 0.91146 | 75000 | 57600 | 36000 | 48000 | 57600 | 1.3021 | 93750 | 86400 | 54000 | 96000 | 96000 | 0.97656
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 5 | 4 | 20500 | 14400 | 13500 | 18000 | 41000 | 28800 | 27000 | 36000 | 36000 | 1.1389 | 71750 | 72000 | 54000 | 72000 | 72000 | 0.99653 | 123000 | 86400 | 54000 | 72000 | 86400 | 1.4236 | 153750 | 129600 | 81000 | 144000 | 144000 | 1.0677
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 2 | 2 | 3 | 14000 | 10200 | 9000 | 14000 | 28000 | 20400 | 18000 | 28000 | 28000 | 1 | 49000 | 51000 | 36000 | 56000 | 56000 | 0.875 | 84000 | 61200 | 36000 | 56000 | 61200 | 1.3725 | 105000 | 91800 | 54000 | 112000 | 112000 | 0.9375
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 1 | 1 | 2 | 2 | 9000 | 4800 | 6000 | 8000 | NP | 9600 | 12000 | 16000 | 16000 | NP | NP | NP | 24000 | 32000 | 32000 | NP | 54000 | 28800 | 24000 | 32000 | 32000 | 1.6875 | 67500 | 43200 | 36000 | 64000 | 64000 | 1.0547
R-1 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 9 | UL | 12 | UL | 22800 | UL | 29900 | UL | 45600 | UL | 59800 | UL | 1 | UL | 114000 | UL | 119600 | UL | 1 | UL | 136800 | UL | 119600 | UL | 1 | UL | 205200 | UL | 239200 | UL | 1
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 5 | 4 | 24000 | 15000 | 18000 | 13500 | 48000 | 30000 | 36000 | 27000 | 36000 | 1.3333 | 84000 | 75000 | 72000 | 54000 | 75000 | 1.12 | 144000 | 90000 | 72000 | 54000 | 90000 | 1.6 | 180000 | 135000 | 108000 | 108000 | 135000 | 1.3333
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 5 | 2 | 16000 | 9600 | 12000 | 9100 | 32000 | 19200 | 24000 | 18200 | 24000 | 1.3333 | 56000 | 48000 | 48000 | 36400 | 48000 | 1.1667 | 96000 | 57600 | 48000 | 36400 | 57600 | 1.6667 | 120000 | 86400 | 72000 | 72800 | 86400 | 1.3889
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 5 | 4 | 24000 | 13200 | 18000 | 13500 | 48000 | NP | 36000 | 27000 | 36000 | 1.3333 | 84000 | 66000 | 72000 | 54000 | 72000 | 1.1667 | 144000 | 79200 | 72000 | 54000 | 79200 | 1.8182 | 180000 | 118800 | 108000 | 108000 | 118800 | 1.5152
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 5 | 2 | 16000 | 9600 | 12000 | 9100 | 32000 | 19200 | 24000 | 18200 | 24000 | 1.3333 | 56000 | 48000 | 48000 | 36400 | 48000 | 1.1667 | 96000 | 57600 | 48000 | 36400 | 57600 | 1.6667 | 120000 | 86400 | 72000 | 72800 | 86400 | 1.3889
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 3 | 4 | 20500 | 14400 | 18000 | 13500 | 41000 | 28800 | 36000 | 27000 | 36000 | 1.1389 | 71750 | 72000 | 72000 | 54000 | 72000 | 0.99653 | 123000 | 86400 | 72000 | 54000 | 86400 | 1.4236 | 153750 | 129600 | 108000 | 108000 | 129600 | 1.1863
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 3 | 3 | 12000 | 10200 | 10500 | 10500 | 24000 | 20400 | 21000 | 21000 | 21000 | 1.1429 | 42000 | 51000 | 42000 | 42000 | 51000 | 0.82353 | 72000 | 61200 | 42000 | 42000 | 61200 | 1.1765 | 90000 | 91800 | 63000 | 84000 | 91800 | 0.98039
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | 2 | 7000 | 4800 | 7000 | 6000 | 14000 | 9600 | 14000 | 12000 | 14000 | 1 | 24500 | 24000 | 28000 | 24000 | 28000 | 0.875 | 42000 | 28800 | 28000 | 24000 | 28800 | 1.4583 | 52500 | 43200 | 42000 | 48000 | 48000 | 1.0938
R-2 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 9 | UL | 12 | UL | 22800 | UL | 29900 | UL | 45600 | UL | 59800 | UL | 1 | UL | 114000 | UL | 119600 | UL | 1 | UL | 136800 | UL | 119600 | UL | 1 | UL | 205200 | UL | 239200 | UL | 1
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 5 | 4 | 24000 | 15000 | 18000 | 13500 | 48000 | 30000 | 36000 | 27000 | 36000 | 1.3333 | 84000 | 75000 | 72000 | 54000 | 75000 | 1.12 | 144000 | 90000 | 72000 | 54000 | 90000 | 1.6 | 180000 | 135000 | 108000 | 108000 | 135000 | 1.3333
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 5 | 2 | 16000 | 9600 | 12000 | 9100 | 32000 | 19200 | 24000 | 18200 | 24000 | 1.3333 | 56000 | 48000 | 48000 | 36400 | 48000 | 1.1667 | 96000 | 57600 | 48000 | 36400 | 57600 | 1.6667 | 120000 | 86400 | 72000 | 72800 | 86400 | 1.3889
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 5 | 4 | 24000 | 13200 | 18000 | 13500 | 48000 | 26400 | 36000 | 27000 | 36000 | 1.3333 | 84000 | 66000 | 72000 | 54000 | 72000 | 1.1667 | 144000 | 79200 | 72000 | 54000 | 79200 | 1.8182 | 180000 | 118800 | 108000 | 108000 | 118800 | 1.5152
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 3 | 2 | 16000 | 9600 | 12000 | 9100 | 32000 | 19200 | 24000 | 18200 | 24000 | 1.3333 | 56000 | 48000 | 48000 | 36400 | 48000 | 1.1667 | 96000 | 57600 | 48000 | 36400 | 57600 | 1.6667 | 120000 | 86400 | 72000 | 72800 | 86400 | 1.3889
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 3 | 4 | 20500 | 14400 | 18000 | 13500 | 41000 | 28800 | 36000 | 27000 | 36000 | 1.1389 | 71750 | 72000 | 72000 | 54000 | 72000 | 0.99653 | 123000 | 86400 | 72000 | 54000 | 86400 | 1.4236 | 153750 | 129600 | 108000 | 108000 | 129600 | 1.1863
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 3 | 3 | 12000 | 10200 | 10500 | 10500 | 24000 | 20400 | 21000 | 21000 | 21000 | 1.1429 | 42000 | 51000 | 42000 | 42000 | 51000 | 0.82353 | 72000 | 61200 | 42000 | 42000 | 61200 | 1.1765 | 90000 | 91800 | 63000 | 84000 | 91800 | 0.98039
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | 2 | 7000 | 4800 | 7000 | 6000 | 14000 | 9600 | 14000 | 12000 | 14000 | 1 | 24500 | 24000 | 28000 | 24000 | 28000 | 0.875 | 42000 | 28800 | 28000 | 24000 | 28800 | 1.4583 | 52500 | 43200 | 42000 | 48000 | 48000 | 1.0938
R-3 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 4 | UL | 3 | UL | 22800 | UL | UL | UL | 45600 | UL | UL | UL | 1 | UL | 114000 | UL | UL | UL | 1 | UL | 136800 | UL | UL | UL | 1 | UL | 205200 | UL | UL | UL | 1
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 5 | 3 | UL | 15000 | 18000 | UL | UL | 30000 | 36000 | UL | UL | 1 | UL | 75000 | 72000 | UL | UL | 1 | UL | 90000 | 72000 | UL | UL | 1 | UL | 135000 | 108000 | UL | UL | 1
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 5 | 3 | UL | 9600 | 12000 | UL | UL | 19200 | 24000 | UL | UL | 1 | UL | 48000 | 48000 | UL | UL | 1 | UL | 57600 | 48000 | UL | UL | 1 | UL | 86400 | 72000 | UL | UL | 1
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 5 | 3 | UL | 13200 | 18000 | UL | UL | 26400 | 36000 | UL | UL | 1 | UL | 66000 | 72000 | UL | UL | 1 | UL | 79200 | 72000 | UL | UL | 1 | UL | 118800 | 108000 | UL | UL | 1
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 5 | 3 | UL | 9600 | 12000 | UL | UL | 19200 | 24000 | UL | UL | 1 | UL | 48000 | 48000 | UL | UL | 1 | UL | 57600 | 48000 | UL | UL | 1 | UL | 86400 | 72000 | UL | UL | 1
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 3 | 3 | UL | 14400 | 18000 | UL | UL | 28800 | 36000 | UL | UL | 1 | UL | 72000 | 72000 | UL | UL | 1 | UL | 86400 | 72000 | UL | UL | 1 | UL | 129600 | 108000 | UL | UL | 1
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 3 | 3 | UL | 10200 | 10500 | UL | UL | 20400 | 21000 | UL | UL | 1 | UL | 51000 | 42000 | UL | UL | 1 | UL | 61200 | 42000 | UL | UL | 1 | UL | 91800 | 63000 | UL | UL | 1
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 2 | 2 | 3 | UL | 4800 | 7000 | UL | UL | 9600 | 14000 | UL | UL | 1 | UL | 24000 | 28000 | UL | UL | 1 | UL | 28800 | 28000 | UL | UL | 1 | UL | 43200 | 42000 | UL | UL | 1
S-1 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 5 | 6 | 12 | 48000 | 19950 | 30000 | 39900 | 96000 | 39900 | 60000 | 79800 | 79800 | 1.203 | 168000 | 99750 | 120000 | 159600 | 159600 | 1.0526 | 288000 | 119700 | 120000 | 159600 | 159600 | 1.8045 | 360000 | 179550 | 180000 | 319200 | 319200 | 1.1278
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 4 | 4 | 26000 | 13125 | 24000 | 18000 | 52000 | 26250 | 48000 | 36000 | 48000 | 1.0833 | 91000 | 65625 | 96000 | 72000 | 96000 | 0.94792 | 156000 | 78750 | 96000 | 72000 | 96000 | 1.625 | 195000 | 118125 | 144000 | 144000 | 144000 | 1.3542
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 2 | 4 | 2 | 17500 | 8400 | 16000 | 12000 | 35000 | 16800 | 32000 | 24000 | 32000 | 1.0938 | 61250 | 42000 | 64000 | 48000 | 64000 | 0.95703 | 105000 | 50400 | 64000 | 48000 | 64000 | 1.6406 | 131250 | 75600 | 96000 | 96000 | 96000 | 1.3672
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 4 | 4 | 26000 | 11550 | 24000 | 18000 | 52000 | 23100 | 48000 | 36000 | 48000 | 1.0833 | 91000 | 57750 | 96000 | 72000 | 96000 | 0.94792 | 156000 | 69300 | 96000 | 72000 | 96000 | 1.625 | 195000 | 103950 | 144000 | 144000 | 144000 | 1.3542
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 2 | 4 | 2 | 17500 | 8400 | 16000 | 12000 | 35000 | 16800 | 32000 | 24000 | 32000 | 1.0938 | 61250 | 42000 | 64000 | 48000 | 64000 | 0.95703 | 105000 | 50400 | 64000 | 48000 | 64000 | 1.6406 | 131250 | 75600 | 96000 | 96000 | 96000 | 1.3672
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 6 | 4 | 25500 | 12600 | 24000 | 18000 | 51000 | 25200 | 48000 | 36000 | 48000 | 1.0625 | 89250 | 63000 | 96000 | 72000 | 96000 | 0.92969 | 153000 | 75600 | 96000 | 72000 | 96000 | 1.5938 | 191250 | 113400 | 144000 | 144000 | 144000 | 1.3281
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 2 | 1 | 3 | 14000 | 8925 | 9000 | 14000 | 28000 | 17850 | NP | 28000 | 28000 | 1 | 49000 | 44625 | NP | 56000 | 56000 | 0.875 | 84000 | 53550 | 18000 | 56000 | 56000 | 1.5 | 105000 | 80325 | 36000 | 112000 | 112000 | 0.9375
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 1 | 1 | 1 | 2 | 9000 | 4200 | 6000 | 8000 | NP | 8400 | NP | 16000 | 16000 | NP | NP | NP | NP | 32000 | 32000 | NP | 54000 | 25200 | 12000 | 32000 | 32000 | 1.6875 | 67500 | 37800 | 24000 | 64000 | 64000 | 1.0547
S-2 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 7 | 6 | 12 | 79000 | 34200 | 30000 | 59900 | 158000 | 68400 | 60000 | 119800 | 119800 | 1.3189 | 276500 | 171000 | 120000 | 239600 | 239600 | 1.154 | 474000 | 205200 | 120000 | 239600 | 239600 | 1.9783 | 592500 | 307800 | 180000 | 479200 | 479200 | 1.2364
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 5 | 5 | 4 | 4 | 39000 | 22500 | 24000 | 27000 | 78000 | 45000 | 48000 | 54000 | 54000 | 1.4444 | 136500 | 112500 | 96000 | 108000 | 112500 | 1.2133 | 234000 | 135000 | 96000 | 108000 | 135000 | 1.7333 | 292500 | 202500 | 144000 | 216000 | 216000 | 1.3542
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 4 | 2 | 26000 | 14400 | 16000 | 18000 | 52000 | 28800 | 32000 | 36000 | 36000 | 1.4444 | 91000 | 72000 | 64000 | 72000 | 72000 | 1.2639 | 156000 | 86400 | 64000 | 72000 | 86400 | 1.8056 | 195000 | 129600 | 96000 | 144000 | 144000 | 1.3542
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 4 | 4 | 39000 | 19800 | 24000 | 27000 | 78000 | NP | 48000 | 54000 | 54000 | 1.4444 | 136500 | 99000 | 96000 | 108000 | 108000 | 1.2639 | 234000 | 118800 | 96000 | 108000 | 118800 | 1.9697 | 292500 | 178200 | 144000 | 216000 | 216000 | 1.3542
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 4 | 2 | 26000 | 14400 | 16000 | 18000 | 52000 | 28800 | 32000 | 36000 | 36000 | 1.4444 | 91000 | 72000 | 64000 | 72000 | 72000 | 1.2639 | 156000 | 86400 | 64000 | 72000 | 86400 | 1.8056 | 195000 | 129600 | 96000 | 144000 | 144000 | 1.3542
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 5 | 5 | 6 | 4 | 38500 | 21600 | 24000 | 27000 | 77000 | 43200 | 48000 | 54000 | 54000 | 1.4259 | 134750 | 108000 | 96000 | 108000 | 108000 | 1.2477 | 231000 | 129600 | 96000 | 108000 | 129600 | 1.7824 | 288750 | 194400 | 144000 | 216000 | 216000 | 1.3368
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 1 | 3 | 21000 | 15300 | 9000 | 21000 | 42000 | 30600 | NP | 42000 | 42000 | 1 | 73500 | 76500 | NP | 84000 | 84000 | 0.875 | 126000 | 91800 | 18000 | 84000 | 91800 | 1.3725 | 157500 | 137700 | 36000 | 168000 | 168000 | 0.9375
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 1 | 2 | 13500 | 7200 | 6000 | 12000 | 27000 | 14400 | NP | 24000 | 24000 | 1.125 | 47250 | 36000 | NP | 48000 | 48000 | 0.98438 | 81000 | 43200 | 12000 | 48000 | 48000 | 1.6875 | 101250 | 64800 | 24000 | 96000 | 96000 | 1.0547

## Three Stories
Cells identified at Dec 10 - 11 meeting that result in total building area that is more than 10% greater than total area permitted by largest legacy code.
IBC more than 10% greater than largest legacy code area.
IBC more than 10% less than largest legacy code area.
LNP - Not pemitted by legacy codes but permitted by IBC
INF - Infinity
Ratio of IBC area to largest legacy code area for condition stated:
[24 empty] | Without sprinklers | [11 empty] | With sprinklers
[15 empty] | Tabular area of code | [8 empty] | Open space | [11 empty] | Open space
[10 empty] | IBC | NBC | SBC/uns | SBC/spr |  | IBC | NBC | SBC | UBC | [5 empty] | < 20 | [5 empty] | 40 | [5 empty] | < 20 | [5 empty] | 40
[15 empty] | Tabular Areas (TA) |  |  |  | TA + < 20 ft. open space (no sprinklers) | [5 empty] | TA + 40 ft. open space (no sprinklers) | [5 empty] | TA + < 20 ft. open space + sprinklers | [5 empty] | TA + 40 ft. open space + sprinklers
|  | IBC | NBC | SBC | UBC | IBC | NBC | SBC | UBC | IBC | NBC | SBC | SBC | UBC | IBC | NBC | SBC | UBC | IBC | NBC | SBC | UBC | Largest Legacy | Ratio IBC/LL | IBC | NBC | SBC | UBC | Largest Legacy | Ratio IBC/LL | IBC | NBC | SBC | UBC | Largest Legacy | Ratio IBC/LL | IBC | NBC | SBC | UBC | Largest Legacy | Ratio IBC/LL | BOCA Neight reduction factor
Occup. | Type Const. | Area Increase for Sprinklers? |  |  |  | Height Increase for Sprinklers? |  |  |  | Ht. | Ht. | Ht. | Ht. | Ht. | Area | Area | Area | Area | Area | Area | Area | Area | Area |  | Area | Area | Area | Area | Area |  | Area | Area | Area | Area | Area |  | Area | Area | Area | Area | Area
A-1 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 5 | 5 | UL | UL | 4 | UL | 19950 | UL | 29900 | UL | 56857.5 | UL | 59800 | UL | 1 | UL | 146632.5 | UL | 119600 | UL | 1 | UL | 116707.5 | UL | 119600 | UL | 1 | UL | 206482.5 | UL | 239200 | UL | 1 | 0.05
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 4 | 4 | 2 | 15500 | 13125 | 12000 | 13500 | 46500 | 31500 | 36000 | NP | 36000 | 1.2917 | 81375 | 90562.5 | 72000 | NP | 90562.5 | 0.89855 | 139500 | 70875 | 72000 | 27000 | 72000 | 1.9375 | 174375 | 129937.5 | 108000 | 54000 | 129937.5 | 1.342 | 0.2
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | 2 | NP | 8500 | 8400 | 8000 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 76500 | 45360 | 24000 | NP | 45360 | 1.6865 | 95625 | 83160 | 48000 | NP | 83160 | 1.1499 | 0.2
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 2 | 14000 | 11550 | 12000 | 13500 | 42000 | 27720 | NP | NP | 27720 | 1.5152 | 73500 | 79695 | NP | NP | 79695 | 0.92227 | 126000 | 62370 | 36000 | 27000 | 62370 | 2.0202 | 157500 | 114345 | 72000 | 54000 | 114345 | 1.3774 | 0.2
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | 2 | NP | 8500 | 8400 | 8000 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 76500 | 45360 | 24000 | NP | 45360 | 1.6865 | 95625 | 83160 | 48000 | NP | 83160 | 1.1499 | 0.2
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 2 | 15000 | 12600 | 12000 | 13500 | 45000 | 30240 | NP | NP | 30240 | 1.4881 | 78750 | 86940 | NP | NP | 86940 | 0.9058 | 135000 | 68040 | 36000 | 27000 | 68040 | 1.9841 | 168750 | 124740 | 72000 | 54000 | 124740 | 1.3528 | 0.2
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 1 | 1 | 1 | 2 | 11500 | 8925 | 7500 | 10500 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 103500 | NP | NP | 21000 | 21000 | 4.9286 | 129375 | NP | NP | 42000 | 42000 | 3.0804 | 0.2
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 1 | 1 | 1 | 1 | NP | 5500 | 4200 | 5000 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
A-2 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 3 | UL | UL | 12 | UL | 5700 | UL | 29900 | UL | 16245 | UL | 59800 | UL | 1 | UL | 41895 | UL | 119600 | UL | 1 | UL | 33345 | UL | 119600 | UL | 1 | UL | 58995 | UL | 239200 | UL | 1 | 0.05
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 2 | 2 | 2 | 2 | 15500 | 3750 | 12000 | 13500 | 46500 | NP | NP | NP | 0 | LNP | 81375 | NP | NP | NP | 0 | LNP | 139500 | 20250 | 36000 | 27000 | 36000 | 3.875 | 174375 | 37125 | 72000 | 54000 | 72000 | 2.4219 | 0.2
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 1 | 2 | 2 | 1 | 9500 | 2400 | 8000 | 9100 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 85500 | NP | 24000 | NP | 24000 | 3.5625 | 106875 | NP | 48000 | NP | 48000 | 2.2266 | 0.2
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 2 | 2 | 2 | 2 | 14000 | 3300 | 12000 | 13500 | 42000 | NP | NP | NP | 0 | LNP | 73500 | NP | NP | NP | 0 | LNP | 126000 | 17820 | 36000 | 27000 | 36000 | 3.5 | 157500 | 32670 | 72000 | 54000 | 72000 | 2.1875 | 0.2
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 1 | 2 | 2 | 1 | 9500 | 2400 | 8000 | 9100 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 85500 | NP | 24000 | NP | 24000 | 3.5625 | 106875 | NP | 48000 | NP | 48000 | 2.2266 | 0.2
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 2 | 2 | 2 | 2 | 15000 | 3600 | 12000 | 13500 | 45000 | NP | NP | NP | 0 | LNP | 78750 | NP | NP | NP | 0 | LNP | 135000 | 19440 | 36000 | 27000 | 36000 | 3.75 | 168750 | 35640 | 72000 | 54000 | 72000 | 2.3438 | 0.2
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 1 | 1 | 1 | 2 | 11500 | 2550 | 7500 | 10500 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 103500 | NP | NP | 21000 | 21000 | 4.9286 | 129375 | NP | NP | 42000 | 42000 | 3.0804 | 0.2
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 1 | 1 | 1 | 1 | 1 | 6000 | 1200 | 5000 | 6000 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
A-3 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 5 | UL | UL | 12 | UL | 19950 | UL | 29900 | UL | 56857.5 | UL | 59800 | UL | 1 | UL | 146632.5 | UL | 119600 | UL | 1 | UL | 116707.5 | UL | 119600 | UL | 1 | UL | 206482.5 | UL | 239200 | UL | 1 | 0.05
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 2 | 15500 | 13125 | 12000 | 13500 | 46500 | 31500 | NP | NP | 31500 | 1.4762 | 81375 | 90562.5 | NP | NP | 90562.5 | 0.89855 | 139500 | 70875 | 36000 | 27000 | 70875 | 1.9683 | 174375 | 129937.5 | 72000 | 54000 | 129937.5 | 1.342 | 0.2
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | 2 | 1 | 9500 | 8400 | 8000 | 9100 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 85500 | 45360 | 24000 | NP | 45360 | 1.8849 | 106875 | 83160 | 48000 | NP | 83160 | 1.2852 | 0.2
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 2 | 14000 | 11550 | 12000 | 13500 | 42000 | 27720 | NP | NP | 27720 | 1.5152 | 73500 | 79695 | NP | NP | 79695 | 0.92227 | 126000 | 62370 | 36000 | 27000 | 62370 | 2.0202 | 157500 | 114345 | 72000 | 54000 | 114345 | 1.3774 | 0.2
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | 2 | 1 | 9500 | 8400 | 8000 | 9100 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 85500 | 45360 | 24000 | NP | 45360 | 1.8849 | 106875 | 83160 | 48000 | NP | 83160 | 1.2852 | 0.2
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 2 | 15000 | 12600 | 12000 | 13500 | 45000 | 30240 | NP | NP | 30240 | 1.4881 | 78750 | 86940 | NP | NP | 86940 | 0.9058 | 135000 | 68040 | 36000 | 27000 | 68040 | 1.9841 | 168750 | 124740 | 72000 | 54000 | 124740 | 1.3528 | 0.2
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 1 | 2 | 2 | 2 | 11500 | 8925 | 7500 | 10500 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 103500 | NP | 22500 | 21000 | 22500 | 4.6 | 129375 | NP | 45000 | 42000 | 45000 | 2.875 | 0.2
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 1 | 1 | 2 | 2 | 1 | 6000 | 4200 | 5000 | 6000 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | 15000 | NP | 15000 | NP | NP | NP | 30000 | NP | 30000 | NP | 0.2
A-4 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 5 | UL | UL | 12 | UL | 19950 | UL | 29900 | UL | 56857.5 | UL | 59800 | UL | 1 | UL | 146632.5 | UL | 119600 | UL | 1 | UL | 116707.5 | UL | 119600 | UL | 1 | UL | 206482.5 | UL | 239200 | UL | 1 | 0.05
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 2 | 15500 | 13125 | 12000 | 13500 | 46500 | 31500 | NP | NP | 31500 | 1.4762 | 81375 | 90562.5 | NP | NP | 90562.5 | 0.89855 | 139500 | 70875 | 36000 | 27000 | 70875 | 1.9683 | 174375 | 129937.5 | 72000 | 54000 | 129937.5 | 1.342 | 0.2
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | 2 | 1 | 9500 | 8400 | 8000 | 9100 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 85500 | 45360 | 24000 | NP | 45360 | 1.8849 | 106875 | 83160 | 48000 | NP | 83160 | 1.2852 | 0.2
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 2 | 14000 | 11550 | 12000 | 13500 | 42000 | 27720 | NP | NP | 27720 | 1.5152 | 73500 | 79695 | NP | NP | 79695 | 0.92227 | 126000 | 62370 | 36000 | 27000 | 62370 | 2.0202 | 157500 | 114345 | 72000 | 54000 | 114345 | 1.3774 | 0.2
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | 2 | 1 | 9500 | 8400 | 8000 | 9100 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 85500 | 45360 | 24000 | NP | 45360 | 1.8849 | 106875 | 83160 | 48000 | NP | 83160 | 1.2852 | 0.2
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 2 | 15000 | 12600 | 12000 | 13500 | 45000 | 30240 | NP | NP | 30240 | 1.4881 | 78750 | 86940 | NP | NP | 86940 | 0.9058 | 135000 | 68040 | 36000 | 27000 | 68040 | 1.9841 | 168750 | 124740 | 72000 | 54000 | 124740 | 1.3528 | 0.2
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 1 | 1 | 1 | 2 | 11500 | 8925 | 7500 | 10500 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 103500 | NP | NP | 21000 | 21000 | 4.9286 | 129375 | NP | NP | 42000 | 42000 | 3.0804 | 0.2
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 1 | 1 | 1 | 1 | 1 | 6000 | 4200 | 5000 | 6000 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
A-5 | IB | Y | Y | Y | Y | Y | Y | Y | Y | UL |  | UL | UL | 12 | UL |  | UL | 29000 | UL | NP | UL | 58000 | UL | 1 | UL | NP | UL | 116000 | UL | 1 | UL | 0 | UL | 116000 | UL | 1 | UL | 0 | UL | 232000 | UL | 1 | 0.05
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | UL |  | 2 | 2 | 2 | UL |  | 12000 | 13500 | UL | NP | NP | NP | 0 | INF | UL | NP | NP | NP | 0 | INF | UL | 0 | 36000 | 27000 | 36000 | INF | UL | 0 | 72000 | 54000 | 72000 | INF | 0.2
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | UL |  | 2 | 2 | 1 | UL |  | 8000 | 9100 | UL | NP | NP | NP | 0 | INF | UL | NP | NP | NP | 0 | INF | UL | 0 | 24000 | NP | 24000 | INF | UL | 0 | 48000 | NP | 48000 | INF | 0.2
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | UL |  | 2 | 2 | 2 | UL |  | 12000 | 13500 | UL | NP | NP | NP | 0 | INF | UL | NP | NP | NP | 0 | INF | UL | 0 | 36000 | 27000 | 36000 | INF | UL | 0 | 72000 | 54000 | 72000 | INF | 0.2
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | UL |  | 2 | 2 | 1 | UL |  | 8000 | 9100 | UL | NP | NP | NP | 0 | INF | UL | NP | NP | NP | 0 | INF | UL | 0 | 24000 | NP | 24000 | INF | UL | 0 | 48000 | NP | 48000 | INF | 0.2
| IV | Y | Y | Y | Y | Y | Y | Y | Y | UL |  | 2 | 2 | 2 | UL |  | 12000 | 13500 | UL | NP | NP | NP | 0 | INF | UL | NP | NP | NP | 0 | INF | UL | 0 | 36000 | 27000 | 36000 | INF | UL | 0 | 72000 | 54000 | 72000 | INF | 0.2
| VA | Y | Y | Y | Y | Y | Y | Y | Y | UL |  | 1 | 1 | 2 | UL |  | 7500 | 10500 | UL | NP | NP | NP | 0 | INF | UL | NP | NP | NP | 0 | INF | UL | 0 | NP | 21000 | 21000 | INF | UL | 0 | NP | 42000 | 42000 | INF | 0.2
| VB | Y | Y | Y | Y | Y | Y | Y | Y | UL |  | 1 | 1 | 1 | UL |  | 5000 | 6000 | UL | NP | NP | NP | 0 | INF | UL | NP | NP | NP | 0 | INF | UL | 0 | NP | NP | 0 | INF | UL | 0 | NP | NP | 0 | INF | 0.2
B | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 7 | UL | UL | 12 | UL | 34200 | UL | 39900 | UL | 97470 | UL | 79800 | UL | 1 | UL | 251370 | UL | 159600 | UL | 1 | UL | 200070 | UL | 159600 | UL | 1 | UL | 353970 | UL | 319200 | UL | 1 | 0.05
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 5 | 5 | 5 | 5 | 4 | 37500 | 22500 | 25500 | 18000 | 112500 | 54000 | 76500 | 36000 | 76500 | 1.4706 | 196875 | 155250 | 153000 | 72000 | 155250 | 1.2681 | 337500 | 121500 | 153000 | 72000 | 153000 | 2.2059 | 421875 | 222750 | 229500 | 144000 | 229500 | 1.8382 | 0.2
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 2 | 5 | 2 | 23000 | 14400 | 17000 | 12000 | 69000 | 34560 | NP | NP | 34560 | 1.9965 | 120750 | 99360 | NP | NP | 99360 | 1.2153 | 207000 | 77760 | 102000 | 24000 | 102000 | 2.0294 | 258750 | 142560 | 153000 | 48000 | 153000 | 1.6912 | 0.2
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 5 | 4 | 5 | 5 | 4 | 28500 | 19800 | 21000 | 18000 | 85500 | 47520 | 63000 | 36000 | 63000 | 1.3571 | 149625 | 136620 | 126000 | 72000 | 136620 | 1.0952 | 256500 | 106920 | 126000 | 72000 | 126000 | 2.0357 | 320625 | 196020 | 189000 | 144000 | 196020 | 1.6357 | 0.2
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 2 | 5 | 2 | 19000 | 14400 | 14000 | 12000 | 57000 | 34560 | NP | NP | 34560 | 1.6493 | 99750 | 99360 | NP | NP | 99360 | 1.0039 | 171000 | 77760 | 84000 | 24000 | 84000 | 2.0357 | 213750 | 142560 | 126000 | 48000 | 142560 | 1.4994 | 0.2
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 5 | 5 | 5 | 5 | 4 | 36000 | 21600 | 25500 | 18000 | 108000 | 51840 | 76500 | 36000 | 76500 | 1.4118 | 189000 | 149040 | 153000 | 72000 | 153000 | 1.2353 | 324000 | 116640 | 153000 | 72000 | 153000 | 2.1176 | 405000 | 213840 | 229500 | 144000 | 229500 | 1.7647 | 0.2
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 3 | 18000 | 15300 | 13500 | 14000 | 54000 | 36720 | NP | 28000 | 36720 | 1.4706 | 94500 | 105570 | NP | 56000 | 105570 | 0.89514 | 162000 | 82620 | 40500 | 56000 | 82620 | 1.9608 | 202500 | 151470 | 81000 | 112000 | 151470 | 1.3369 | 0.2
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | 2 | 2 | 9000 | 7200 | 9000 | 8000 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 81000 | 38880 | 27000 | 16000 | 38880 | 2.0833 | 101250 | 71280 | 54000 | 32000 | 71280 | 1.4205 | 0.2
E | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 5 | UL | UL | 4 | UL | 34200 | UL | 45200 | UL | 97470 | UL | 90400 | UL | 1 | UL | 251370 | UL | 180800 | UL | 1 | UL | 200070 | UL | 180800 | UL | 1 | UL | 353970 | UL | 361600 | UL | 1 | 0.05
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 2 | 26500 | 22500 | 18000 | 20200 | 79500 | 54000 | NP | NP | 54000 | 1.4722 | 139125 | 155250 | NP | NP | 155250 | 0.89614 | 238500 | 121500 | 54000 | 40400 | 121500 | 1.963 | 298125 | 222750 | 108000 | 80800 | 222750 | 1.3384 | 0.2
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 1 | 1 | 1 | 14500 | 14400 | 12000 | 13500 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 130500 | 77760 | NP | NP | 77760 | 1.6782 | 163125 | 142560 | NP | NP | 142560 | 1.1443 | 0.2
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 2 | 23500 | 19800 | 18000 | 20200 | 70500 | 47520 | NP | NP | 47520 | 1.4836 | 123375 | 136620 | NP | NP | 136620 | 0.90305 | 211500 | 106920 | 54000 | 40400 | 106920 | 1.9781 | 264375 | 196020 | 108000 | 80800 | 196020 | 1.3487 | 0.2
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 1 | 1 | 1 | 14500 | 14400 | 12000 | 13500 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 130500 | 77760 | NP | NP | 77760 | 1.6782 | 163125 | 142560 | NP | NP | 142560 | 1.1443 | 0.2
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 2 | 2 | 25500 | 21600 | 18000 | 20200 | 76500 | 51840 | NP | NP | 51840 | 1.4757 | 133875 | 149040 | NP | NP | 149040 | 0.89825 | 229500 | 116640 | 54000 | 40400 | 116640 | 1.9676 | 286875 | 213840 | 108000 | 80800 | 213840 | 1.3415 | 0.2
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 1 | 1 | 2 | 2 | 2 | 18500 | 15300 | 12000 | 15700 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | 36000 | 31400 | 36000 | NP | NP | NP | 72000 | 62800 | 72000 | NP | 0.2
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 1 | 1 | 1 | 1 | 1 | 9500 | 7200 | 8000 | 9100 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
F-1 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 6 | UL | UL | 12 | UL | 22800 | UL | 39900 | UL | 64980 | UL | 79800 | UL | 1 | UL | 167580 | UL | 159600 | UL | 1 | UL | 133380 | UL | 159600 | UL | 1 | UL | 235980 | UL | 319200 | UL | 1 | 0.05
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 2 | 4 | 4 | 25000 | 15000 | 31500 | 18000 | 75000 | 36000 | NP | 36000 | 36000 | 2.0833 | 131250 | 103500 | NP | 72000 | 103500 | 1.2681 | 225000 | 81000 | 189000 | 72000 | 189000 | 1.1905 | 281250 | 148500 | 283500 | 144000 | 283500 | 0.99206 | 0.2
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | 4 | 2 | 15500 | 9600 | 21000 | 12000 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 139500 | 51840 | 126000 | 24000 | 126000 | 1.1071 | 174375 | 95040 | 189000 | 48000 | 189000 | 0.92262 | 0.2
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 4 | 4 | 19000 | 13200 | 22500 | 18000 | 57000 | 31680 | NP | 36000 | 36000 | 1.5833 | 99750 | 91080 | NP | 72000 | 91080 | 1.0952 | 171000 | 71280 | 135000 | 72000 | 135000 | 1.2667 | 213750 | 130680 | 202500 | 144000 | 202500 | 1.0556 | 0.2
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | 4 | 2 | 12000 | 9600 | 15000 | 12000 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 108000 | 51840 | 90000 | 24000 | 90000 | 1.2 | 135000 | 95040 | 135000 | 48000 | 135000 | 1 | 0.2
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 3 | 6 | 4 | 33500 | 14400 | 31500 | 18000 | 100500 | 34560 | 94500 | 36000 | 94500 | 1.0635 | 175875 | 99360 | 189000 | 72000 | 189000 | 0.93056 | 301500 | 77760 | 189000 | 72000 | 189000 | 1.5952 | 376875 | 142560 | 283500 | 144000 | 283500 | 1.3294 | 0.2
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 1 | 1 | 3 | 14000 | 10200 | 15000 | 14000 | NP | NP | NP | 28000 | 28000 | NP | NP | NP | NP | 56000 | 56000 | NP | 126000 | 55080 | NP | 56000 | 56000 | 2.25 | 157500 | 100980 | NP | 112000 | 112000 | 1.4062 | 0.2
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 1 | 1 | 1 | 1 | 2 | 8500 | 4800 | 10000 | 8000 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | 16000 | 16000 | NP | NP | NP | NP | 32000 | 32000 | NP | 0.2
F-2 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 7 | UL | UL | 12 | UL | 34200 | UL | 59900 | UL | 97470 | UL | 119800 | UL | 1 | UL | 251370 | UL | 239600 | UL | 1 | UL | 200070 | UL | 239600 | UL | 1 | UL | 353970 | UL | 479200 | UL | 1 | 0.05
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 5 | 5 | 2 | 4 | 4 | 37500 | 22500 | 31500 | 27000 | 112500 | 54000 | NP | 54000 | 54000 | 2.0833 | 196875 | 155250 | NP | 108000 | 155250 | 1.2681 | 337500 | 121500 | 189000 | 108000 | 189000 | 1.7857 | 421875 | 222750 | 283500 | 216000 | 283500 | 1.4881 | 0.2
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 4 | 2 | 23000 | 14400 | 21000 | 18000 | 69000 | 34560 | NP | NP | 34560 | 1.9965 | 120750 | 99360 | NP | NP | 99360 | 1.2153 | 207000 | 77760 | 126000 | 36000 | 126000 | 1.6429 | 258750 | 142560 | 189000 | 72000 | 189000 | 1.369 | 0.2
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 2 | 4 | 4 | 28500 | 19800 | 22500 | 27000 | 85500 | 47520 | NP | 54000 | 54000 | 1.5833 | 149625 | 136620 | NP | 108000 | 136620 | 1.0952 | 256500 | 106920 | 135000 | 108000 | 135000 | 1.9 | 320625 | 196020 | 202500 | 216000 | 216000 | 1.4844 | 0.2
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 4 | 2 | 18000 | 14400 | 15000 | 18000 | 54000 | 34560 | NP | NP | 34560 | 1.5625 | 94500 | 99360 | NP | NP | 99360 | 0.95109 | 162000 | 77760 | 90000 | 36000 | 90000 | 1.8 | 202500 | 142560 | 135000 | 72000 | 142560 | 1.4205 | 0.2
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 5 | 5 | 3 | 6 | 4 | 50500 | 21600 | 31500 | 27000 | 151500 | 51840 | 94500 | 54000 | 94500 | 1.6032 | 265125 | 149040 | 189000 | 108000 | 189000 | 1.4028 | 454500 | 116640 | 189000 | 108000 | 189000 | 2.4048 | 568125 | 213840 | 283500 | 216000 | 283500 | 2.004 | 0.2
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 1 | 1 | 3 | 21000 | 15300 | 15000 | 21000 | 63000 | 36720 | NP | 42000 | 42000 | 1.5 | 110250 | 105570 | NP | 84000 | 105570 | 1.0443 | 189000 | 82620 | NP | 84000 | 84000 | 2.25 | 236250 | 151470 | NP | 168000 | 168000 | 1.4062 | 0.2
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 1 | 1 | 2 | 13000 | 7200 | 10000 | 12000 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 117000 | 38880 | NP | 24000 | 38880 | 3.0093 | 146250 | 71280 | NP | 48000 | 71280 | 2.0518 | 0.2
H-1 | 1A | N | N | Y | N | N | N | N | N | 1 | 1 | 1 | 1 | 1 | 21000 | 14400 | 5000 | 15000 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP
| IB | N | N | Y | N | N | N | N | N | 1 | 1 | 1 | 1 | 1 | 16500 | 11400 | 4000 | 12400 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.05
| IIA | N | N | Y | N | N | N | N | N | 1 | 1 | 1 | 1 | 1 | 11000 | 7500 | 2500 | 5600 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| IIB | N | N | Y | N | N | N | N | N | 1 | 1 | 1 | 1 | 1 | 7000 | 4800 | 1666.6667 | 3700 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| IIIA | N | N | Y | N | N | N | N | N | 1 | 1 | 1 | 1 | NP | 9500 | 6600 | 2500 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| IIIB | N | N | Y | N | N | N | N | N | 1 | 1 | NP | NP | NP | 7000 | 4800 | NP | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| IV | N | N | Y | N | N | N | N | N | 1 | 1 | 1 | 1 | NP | 10500 | 7200 | 2500 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| VA | N | N | Y | N | N | N | N | N | 1 | 1 | NP | NP | NP | 7500 | 5100 | NP | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| VB | N | N | Y | N | N | N | N | N | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
H-2 | 1A | N | N | Y | N | N | N | N | N | UL | 3 | 1 | 1 | UL | 21000 | 14400 | 5000 | 15000 | 63000 | 43200 | NP | 30000 | 43200 | 1.4583 | 110250 | 108000 | NP | 60000 | 108000 | 1.0208 | 63000 | 43200 | NP | 30000 | 43200 | 1.4583 | 110250 | 108000 | NP | 60000 | 108000 | 1.0208
| IB | N | N | Y | N | N | N | N | N | 3 | 3 | 1 | 1 | 2 | 16500 | 11400 | 4000 | 12400 | 49500 | 32490 | NP | NP | 32490 | 1.5235 | 86625 | 83790 | NP | NP | 83790 | 1.0338 | 49500 | 32490 | NP | NP | 32490 | 1.5235 | 86625 | 83790 | NP | NP | 83790 | 1.0338 | 0.05
| IIA | N | N | Y | N | N | N | N | N | 2 | 2 | 1 | 1 | 1 | 11000 | 7500 | 2500 | 5600 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| IIB | N | N | Y | N | N | N | N | N | 1 | 1 | 1 | 1 | 1 | 7000 | 4800 | 1666.6667 | 3700 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| IIIA | N | N | Y | N | N | N | N | N | 2 | 2 | 1 | 1 | 1 | 9500 | 6600 | 2500 | 5600 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| IIIB | N | N | Y | N | N | N | N | N | 1 | 1 | 1 | 1 | 1 | 7000 | 4800 | 1333.3333 | 3700 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| IV | N | N | Y | N | N | N | N | N | 2 | 2 | 1 | 1 | 1 | 10500 | 7200 | 2500 | 5600 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| VA | N | N | Y | N | N | N | N | N | 1 | 1 | 1 | 1 | 1 | 7500 | 5100 | 833.3333 | 4400 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| VB | N | N | Y | N | N | N | N | N | 1 | NP | NP | NP | 1 | 3000 | NP | NP | 2500 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
H-3 | IA | N | N | Y | N | N | N | N | N | UL | 7 | Y | Y | UL | UL | 28800 | 10000 | UL | UL | 86400 | 30000 | UL | UL | 1 | UL | 216000 | 60000 | UL | UL | 1 | UL | 86400 | 60000 | UL | UL | 1 | UL | 216000 | 90000 | UL | UL | 1
| IB | N | N | Y | N | N | N | N | N | 6 | 6 | 3 | 3 | 5 | 60000 | 22800 | 6666.6667 | 24800 | 180000 | 64980 | 20000 | 49600 | 64980 | 2.7701 | 315000 | 167580 | 40000 | 99200 | 167580 | 1.8797 | 180000 | 64980 | 40000 | 49600 | 64980 | 2.7701 | 315000 | 167580 | 60000 | 99200 | 167580 | 1.8797 | 0.05
| IIA | N | N | Y | N | N | N | N | N | 4 | 4 | 2 | 2 | 2 | 26500 | 15000 | 3333.3333 | 11200 | 79500 | 36000 | NP | NP | 36000 | 2.2083 | 139125 | 103500 | NP | NP | 103500 | 1.3442 | 79500 | 36000 | NP | NP | 36000 | 2.2083 | 139125 | 103500 | NP | NP | 103500 | 1.3442 | 0.2
| IIB | N | N | Y | N | N | N | N | N | 2 | 2 | 1 | 1 | 1 | 14000 | 9600 | 2500 | 7500 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| IIIA | N | N | Y | N | N | N | N | N | 4 | 3 | 2 | 2 | 2 | 17500 | 13200 | 3333.3333 | 11200 | 52500 | 31680 | NP | NP | 31680 | 1.6572 | 91875 | 91080 | NP | NP | 91080 | 1.0087 | 52500 | 31680 | NP | NP | 31680 | 1.6572 | 91875 | 91080 | NP | NP | 91080 | 1.0087 | 0.2
| IIIB | N | N | Y | N | N | N | N | N | 2 | 2 | 1 | 1 | 1 | 13000 | 9600 | 2500 | 7500 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| IV | N | N | Y | N | N | N | N | N | 4 | 4 | 2 | 2 | 2 | 25500 | 14400 | 3333.3333 | 11200 | 76500 | 34560 | NP | NP | 34560 | 2.2135 | 133875 | 99360 | NP | NP | 99360 | 1.3474 | 76500 | 34560 | NP | NP | 34560 | 2.2135 | 133875 | 99360 | NP | NP | 99360 | 1.3474 | 0.2
| VA | N | N | Y | N | N | N | N | N | 2 | 2 | 1 | 1 | 2 | 10000 | 10200 | 1333.3333 | 8800 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| VB | N | N | Y | N | N | N | N | N | 1 | 1 | NP | NP | 1 | 5000 | 4800 | NP | 5100 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
H-4 | IB | Y | Y | Y | Y | Y | Y | N | N | 7 | 7 | 6 | 6 | 3 | UL | 34200 | UL | 39900 | UL | 97470 | UL | 79800 | UL | 1 | UL | 251370 | UL | 159600 | UL | 1 | UL | 200070 | UL | 159600 | UL | 1 | UL | 353970 | UL | 319200 | UL | 1 | 0.05
| IIA | Y | Y | Y | Y | Y | Y | N | N | 5 | 5 | 4 | 4 | 3 | 37000 | 22500 | 48000 | 18000 | 111000 | 54000 | 144000 | 36000 | 144000 | 0.77083 | 194250 | 155250 | 288000 | 72000 | 288000 | 0.67448 | 333000 | 121500 | 288000 | 72000 | 288000 | 1.1562 | 416250 | 222750 | 432000 | 144000 | 432000 | 0.96354 | 0.2
| IIB | Y | Y | Y | Y | Y | Y | N | N | 3 | 3 | 4 | 4 | 2 | 17500 | 14400 | 32000 | 12000 | 52500 | 34560 | 96000 | NP | 96000 | 0.54688 | 91875 | 99360 | 192000 | NP | 192000 | 0.47852 | 157500 | 77760 | 192000 | NP | 192000 | 0.82031 | 196875 | 142560 | 288000 | NP | 288000 | 0.68359 | 0.2
| IIIA | Y | Y | Y | Y | Y | Y | N | N | 5 | 4 | 4 | 4 | 3 | 28500 | 19800 | 48000 | 18000 | 85500 | 47520 | 144000 | 36000 | 144000 | 0.59375 | 149625 | 136620 | 288000 | 72000 | 288000 | 0.51953 | 256500 | 106920 | 288000 | 72000 | 288000 | 0.89062 | 320625 | 196020 | 432000 | 144000 | 432000 | 0.74219 | 0.2
| IIIB | Y | Y | Y | Y | Y | Y | N | N | 3 | 3 | 4 | 4 | 2 | 17500 | 14400 | 32000 | 12000 | 52500 | 34560 | 96000 | NP | 96000 | 0.54688 | 91875 | 99360 | 192000 | NP | 192000 | 0.47852 | 157500 | 77760 | 192000 | NP | 192000 | 0.82031 | 196875 | 142560 | 288000 | NP | 288000 | 0.68359 | 0.2
| IV | Y | Y | Y | Y | Y | Y | N | N | 5 | 5 | 3 | 3 | 3 | 36000 | 21600 | 48000 | 18000 | 108000 | 51840 | 144000 | 36000 | 144000 | 0.75 | 189000 | 149040 | 288000 | 72000 | 288000 | 0.65625 | 324000 | 116640 | 288000 | 72000 | 288000 | 1.125 | 405000 | 213840 | 432000 | 144000 | 432000 | 0.9375 | 0.2
| VA | Y | Y | Y | Y | Y | Y | N | N | 3 | 3 | 1 | 1 | 3 | 18000 | 15300 | 27000 | 14000 | 54000 | 36720 | NP | 28000 | 36720 | 1.4706 | 94500 | 105570 | NP | 56000 | 105570 | 0.89514 | 162000 | 82620 | NP | 56000 | 82620 | 1.9608 | 202500 | 151470 | NP | 112000 | 151470 | 1.3369 | 0.2
| VB | Y | Y | Y | Y | Y | Y | N | N | 2 | 2 | 1 | 1 | 1 | 6500 | 7200 | 18000 | 8000 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 58500 | 38880 | NP | NP | 38880 | 1.5046 | 73125 | 71280 | NP | NP | 71280 | 1.0259 | 0.2
H-5 | IB | Y | Y | Y | Y | N | Y | N | N | 3 | 7 | 3 | 3 | 3 | UL | 34400 | UL | 39900 | UL | 98040 | UL | 79800 | UL | 1 | UL | 252840 | UL | 159600 | UL | 1 | UL | 201240 | UL | 159600 | UL | 1 | UL | 356040 | UL | 319200 | UL | 1 | 0.05
| IIA | Y | Y | Y | Y | N | Y | N | N | 3 | 5 | 3 | 3 | 3 | 37500 | 22500 | 63000 | 18000 | 112500 | 54000 | 189000 | 36000 | 189000 | 0.59524 | 196875 | 155250 | 378000 | 72000 | 378000 | 0.52083 | 337500 | 121500 | 378000 | 72000 | 378000 | 0.89286 | 421875 | 222750 | 567000 | 144000 | 567000 | 0.74405 | 0.2
| IIB | Y | Y | Y | Y | N | Y | N | N | 3 | 3 | 3 | 3 | 2 | 23000 | 14400 | 42000 | 12000 | 69000 | 34560 | 126000 | NP | 126000 | 0.54762 | 120750 | 99360 | 252000 | NP | 252000 | 0.47917 | 207000 | 77760 | 252000 | NP | 252000 | 0.82143 | 258750 | 142560 | 378000 | NP | 378000 | 0.68452 | 0.2
| IIIA | Y | Y | Y | Y | N | Y | N | N | 3 | 4 | 3 | 3 | 3 | 28500 | 19800 | 45000 | 18000 | 85500 | 47520 | 135000 | 36000 | 135000 | 0.63333 | 149625 | 136620 | 270000 | 72000 | 270000 | 0.55417 | 256500 | 106920 | 270000 | 72000 | 270000 | 0.95 | 320625 | 196020 | 405000 | 144000 | 405000 | 0.79167 | 0.2
| IIIB | Y | Y | Y | Y | N | Y | N | N | 3 | 3 | 3 | 3 | 2 | 19000 | 14400 | 30000 | 12000 | 57000 | 34560 | 90000 | NP | 90000 | 0.63333 | 99750 | 99360 | 180000 | NP | 180000 | 0.55417 | 171000 | 77760 | 180000 | NP | 180000 | 0.95 | 213750 | 142560 | 270000 | NP | 270000 | 0.79167 | 0.2
| IV | Y | Y | Y | Y | N | Y | N | N | 3 | 5 | 3 | 3 | 3 | 36000 | 21600 | 63000 | 18000 | 108000 | 51840 | 189000 | 36000 | 189000 | 0.57143 | 189000 | 149040 | 378000 | 72000 | 378000 | 0.5 | 324000 | 116640 | 378000 | 72000 | 378000 | 0.85714 | 405000 | 213840 | 567000 | 144000 | 567000 | 0.71429 | 0.2
| VA | Y | Y | Y | Y | N | Y | N | N | 3 | 3 | 1 | 1 | 3 | 18000 | 15300 | 45000 | 14000 | 54000 | 36720 | NP | 28000 | 36720 | 1.4706 | 94500 | 105570 | NP | 56000 | 105570 | 0.89514 | 162000 | 82620 | NP | 56000 | 82620 | 1.9608 | 202500 | 151470 | NP | 112000 | 151470 | 1.3369 | 0.2
| VB | Y | Y | Y | Y | N | Y | N | N | 2 | 2 | 1 | 1 | 1 | 9000 | 7200 | 45000 | 8000 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | 38880 | NP | NP | 38880 | NP | NP | 71280 | NP | NP | 71280 | NP | 0.2
I-1 | IB | Y | Y |  | Y | Y | Y |  | Y | 9 | 9 |  |  | 3 | 55000 | 19950 |  | 15100 | 165000 | 56857.5 | NP | 30200 | 56857.5 | 2.902 | 288750 | 146632.5 | NP | 60400 | 146632.5 | 1.9692 | 495000 | 116707.5 | 0 | 60400 | 116707.5 | 4.2414 | 618750 | 206482.5 | 0 | 120800 | 206482.5 | 2.9966 | 0.05
Ass't | IIA | Y | Y |  | Y | Y | Y |  | Y | 4 | 4 |  |  | 2 | 19000 | 13125 |  | 6800 | 57000 | 31500 | NP | NP | 31500 | 1.8095 | 99750 | 90562.5 | NP | NP | 90562.5 | 1.1014 | 171000 | 70875 | 0 | 13600 | 70875 | 2.4127 | 213750 | 129937.5 | 0 | 27200 | 129937.5 | 1.645 | 0.2
| IIB | Y | Y |  | Y | Y | Y |  | Y | 3 | 3 |  |  | NP | 10000 | 8400 |  | NP | 30000 | 20160 | NP | NP | 20160 | 1.4881 | 52500 | 57960 | NP | NP | 57960 | 0.9058 | 90000 | 45360 | 0 | NP | 45360 | 1.9841 | 112500 | 83160 | 0 | NP | 83160 | 1.3528 | 0.2
| IIIA | Y | Y |  | Y | Y | Y |  | Y | 4 | 4 |  |  | 2 | 16500 | 11550 |  | 6800 | 49500 | 27720 | NP | NP | 27720 | 1.7857 | 86625 | 79695 | NP | NP | 79695 | 1.087 | 148500 | 62370 | 0 | 13600 | 62370 | 2.381 | 185625 | 114345 | 0 | 27200 | 114345 | 1.6234 | 0.2
| IIIB | Y | Y |  | Y | Y | Y |  | Y | 3 | 3 |  |  | NP | 10000 | 8400 |  | NP | 30000 | 20160 | NP | NP | 20160 | 1.4881 | 52500 | 57960 | NP | NP | 57960 | 0.9058 | 90000 | 45360 | 0 | NP | 45360 | 1.9841 | 112500 | 83160 | 0 | NP | 83160 | 1.3528 | 0.2
| IV | Y | Y |  | Y | Y | Y |  | Y | 4 | 4 |  |  | 2 | 18000 | 12600 |  | 6800 | 54000 | 30240 | NP | NP | 30240 | 1.7857 | 94500 | 86940 | NP | NP | 86940 | 1.087 | 162000 | 68040 | 0 | 13600 | 68040 | 2.381 | 202500 | 124740 | 0 | 27200 | 124740 | 1.6234 | 0.2
| VA | Y | Y |  | Y | Y | Y |  | Y | 3 | 3 |  |  | 2 | 10500 | 8925 |  | 5200 | 31500 | 21420 | NP | NP | 21420 | 1.4706 | 55125 | 61582.5 | NP | NP | 61582.5 | 0.89514 | 94500 | 48195 | 0 | 10400 | 48195 | 1.9608 | 118125 | 88357.5 | 0 | 20800 | 88357.5 | 1.3369 | 0.2
| VB | Y | Y |  | Y | Y | Y |  | Y | 2 | 2 |  |  | NP | 4500 | 4200 |  | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 40500 | 22680 | 0 | NP | 22680 | 1.7857 | 50625 | 41580 | 0 | NP | 41580 | 1.2175 | 0.2
I-2 | IB | Y | Y | Y | Y | Y | Y | N | Y | 4 | 4 | UL | UL | 3 | UL | 17100 | UL | 15100 | UL | 48735 | UL | 30200 | UL | 1 | UL | 125685 | UL | 60400 | UL | 1 | UL | 100035 | UL | 60400 | UL | 1 | UL | 176985 | UL | 120800 | UL | 1 | 0.05
Hos | IIA | Y | Y | Y | Y | Y | Y | N | N | 2 | 2 | NP | 3 | 1 | 15000 | 11250 | 15000 | 6800 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 135000 | 60750 | 90000 | NP | 90000 | 1.5 | 168750 | 111375 | 135000 | NP | 135000 | 1.25 | 0.2
| IIB | Y | Y | Y | Y | N | N | N | Y | 1 | 1 | NP | 1 | NP | 11000 | 7200 | 10000 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| IIIA | Y | Y | Y | Y | N | N | N | N | 1 | 1 | NP | 1 | 1 | 12000 | 9900 | 10500 | 6800 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| IIIB | Y | Y | Y | Y | N | Y | N | Y | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| IV | Y | Y | Y | Y | N | N | N | N | 1 | 1 | NP | 2 | 1 | 12000 | 10800 | 12000 | 6800 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| VA | Y | Y | Y | Y | N | N | N | N | 1 | 1 | NP | 1 | 1 | 9500 | 7650 | 7500 | 5200 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| VB | Y | Y | Y | Y | N | Y | N | Y | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
I-3 | IB | Y | Y | Y | Y | Y | Y | N | Y | 4 | 4 | UL | UL | 2 | UL | 14250 | UL | 15100 | UL | 40612.5 | UL | NP | UL | 1 | UL | 104737.5 | UL | NP | UL | 1 | UL | 83362.5 | UL | 30200 | UL | 1 | UL | 147487.5 | UL | 60400 | UL | 1 | 0.05
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | 3 | NP | 15000 | 9375 | 15000 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 135000 | 50625 | 90000 | NP | 90000 | 1.5 | 168750 | 92812.5 | 135000 | NP | 135000 | 1.25 | 0.2
| IIB | Y | Y | Y | Y | Y | Y | N | Y | 1 | 1 | NP | 2 | NP | 10000 | 6000 | 10000 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| IIIA | Y | Y | Y | Y | Y | Y | N | Y | 2 | 2 | NP | 3 | NP | 10500 | 8250 | 10500 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 94500 | 44550 | 63000 | NP | 63000 | 1.5 | 118125 | 81675 | 94500 | NP | 94500 | 1.25 | 0.2
| IIIB | Y | Y | Y | Y | Y | Y | N | Y | 1 | 1 | NP | 2 | NP | 7500 | 6000 | 7000 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
| IV | Y | Y | Y | Y | Y | Y | N | Y | 2 | 2 | NP | 2 | NP | 12000 | 9000 | 12000 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 108000 | 48600 | NP | NP | 48600 | 2.2222 | 135000 | 89100 | NP | NP | 89100 | 1.5152 | 0.2
| VA | Y | Y | Y | Y | Y | Y | N | Y | 2 | 1 | NP | 3 | NP | 7500 | 6375 | 7500 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 67500 | NP | 45000 | NP | 45000 | 1.5 | 84375 | NP | 67500 | NP | 67500 | 1.25 | 0.2
| VB | Y | Y | Y | Y | Y | Y | N | Y | 1 | NP | NP | 2 | NP | 5000 | NP | 5000 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 0.2
I-4 | IB | Y | Y |  | Y | Y | Y |  | Y | 5 | 5 |  |  | 4 | 60500 | 34200 |  | 45200 | 181500 | 97470 | NP | 90400 | 97470 | 1.8621 | 317625 | 251370 | NP | 180800 | 251370 | 1.2636 | 544500 | 200070 | 0 | 180800 | 200070 | 2.7215 | 680625 | 353970 | 0 | 361600 | 361600 | 1.8823 | 0.05
| IIA | Y | Y |  | Y | Y | Y |  | Y | 3 | 3 |  |  | 2 | 26500 | 22500 |  | 20200 | 79500 | 54000 | NP | NP | 54000 | 1.4722 | 139125 | 155250 | NP | NP | 155250 | 0.89614 | 238500 | 121500 | 0 | 40400 | 121500 | 1.963 | 298125 | 222750 | 0 | 80800 | 222750 | 1.3384 | 0.2
| IIB | Y | Y |  | Y | Y | Y |  | Y | 2 | 2 |  |  | 1 | 13000 | 14400 |  | 13500 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 117000 | 77760 | 0 | NP | 77760 | 1.5046 | 146250 | 142560 | 0 | NP | 142560 | 1.0259 | 0.2
| IIIA | Y | Y |  | Y | Y | Y |  | Y | 3 | 3 |  |  | 2 | 23500 | 19800 |  | 20200 | 70500 | 47520 | NP | NP | 47520 | 1.4836 | 123375 | 136620 | NP | NP | 136620 | 0.90305 | 211500 | 106920 | 0 | 40400 | 106920 | 1.9781 | 264375 | 196020 | 0 | 80800 | 196020 | 1.3487 | 0.2
| IIIB | Y | Y |  | Y | Y | Y |  | Y | 2 | 2 |  |  | 1 | 13000 | 14400 |  | 13500 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 117000 | 77760 | 0 | NP | 77760 | 1.5046 | 146250 | 142560 | 0 | NP | 142560 | 1.0259 | 0.2
| IV | Y | Y |  | Y | Y | Y |  | Y | 3 | 3 |  |  | 2 | 25500 | 21600 |  | 20200 | 76500 | 51840 | NP | NP | 51840 | 1.4757 | 133875 | 149040 | NP | NP | 149040 | 0.89825 | 229500 | 116640 | 0 | 40400 | 116640 | 1.9676 | 286875 | 213840 | 0 | 80800 | 213840 | 1.3415 | 0.2
| VA | Y | Y |  | Y | Y | Y |  | Y | 1 | 1 |  |  | 2 | 18500 | 15300 |  | 15700 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | 0 | 31400 | 31400 | NP | NP | NP | 0 | 62800 | 62800 | NP | 0.2
| VB | Y | Y |  | Y | Y | Y |  | Y | 1 | 1 |  |  | 1 | 9000 | 7200 |  | 9100 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | 0 | NP | 0 | NP | NP | NP | 0 | NP | 0 | NP | 0.2
M | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 6 | UL | UL | 12 | UL | 22800 | 15000 | 39900 | UL | 64980 | 45000 | 79800 | 79800 | INF | UL | 167580 | 90000 | 159600 | 167580 | INF | UL | 133380 | 90000 | 159600 | 159600 | INF | UL | 235980 | 135000 | 319200 | 319200 | INF | 0.05
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 5 | 5 | 4 | 21500 | 15000 | 13500 | 18000 | 64500 | 36000 | 40500 | 36000 | 40500 | 1.5926 | 112875 | 103500 | 81000 | 72000 | 103500 | 1.0906 | 193500 | 81000 | 81000 | 72000 | 81000 | 2.3889 | 241875 | 148500 | 121500 | 144000 | 148500 | 1.6288 | 0.2
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 2 | 2 | 5 | 2 | 12500 | 9600 | 9000 | 12000 | 37500 | NP | NP | NP | 0 | LNP | 65625 | NP | NP | NP | 0 | LNP | 112500 | 51840 | 54000 | 24000 | 54000 | 2.0833 | 140625 | 95040 | 81000 | 48000 | 95040 | 1.4796 | 0.2
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 5 | 5 | 4 | 18500 | 13200 | 13500 | 18000 | 55500 | 31680 | 40500 | 36000 | 40500 | 1.3704 | 97125 | 91080 | 81000 | 72000 | 91080 | 1.0664 | 166500 | 71280 | 81000 | 72000 | 81000 | 2.0556 | 208125 | 130680 | 121500 | 144000 | 144000 | 1.4453 | 0.2
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 2 | 2 | 5 | 2 | 12500 | 9600 | 9000 | 12000 | 37500 | NP | NP | NP | 0 | LNP | 65625 | NP | NP | NP | 0 | LNP | 112500 | 51840 | 54000 | 24000 | 54000 | 2.0833 | 140625 | 95040 | 81000 | 48000 | 95040 | 1.4796 | 0.2
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 5 | 5 | 4 | 20500 | 14400 | 13500 | 18000 | 61500 | 34560 | 40500 | 36000 | 40500 | 1.5185 | 107625 | 99360 | 81000 | 72000 | 99360 | 1.0832 | 184500 | 77760 | 81000 | 72000 | 81000 | 2.2778 | 230625 | 142560 | 121500 | 144000 | 144000 | 1.6016 | 0.2
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 2 | 2 | 2 | 3 | 14000 | 10200 | 9000 | 14000 | 42000 | NP | NP | 28000 | 28000 | 1.5 | 73500 | NP | NP | 56000 | 56000 | 1.3125 | 126000 | 55080 | 27000 | 56000 | 56000 | 2.25 | 157500 | 100980 | 54000 | 112000 | 112000 | 1.4062 | 0.2
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 1 | 1 | 2 | 2 | 2 | 9000 | 4800 | 6000 | 8000 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | 18000 | 16000 | 18000 | NP | NP | NP | 36000 | 32000 | 36000 | NP | 0.2
R-1 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 9 | UL | UL | 12 | UL | 22800 | UL | 29900 | UL | 64980 | UL | 59800 | UL | 1 | UL | 167580 | UL | 119600 | UL | 1 | UL | 133380 | UL | 119600 | UL | 1 | UL | 235980 | UL | 239200 | UL | 1 | 0.05
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 5 | 5 | 4 | 24000 | 15000 | 18000 | 13500 | 72000 | 36000 | 54000 | 27000 | 54000 | 1.3333 | 126000 | 103500 | 108000 | 54000 | 108000 | 1.1667 | 216000 | 81000 | 108000 | 54000 | 108000 | 2 | 270000 | 148500 | 162000 | 108000 | 162000 | 1.6667 | 0.2
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 2 | 5 | 2 | 16000 | 9600 | 12000 | 9100 | 48000 | 23040 | NP | NP | 23040 | 2.0833 | 84000 | 66240 | NP | NP | 66240 | 1.2681 | 144000 | 51840 | 72000 | 18200 | 72000 | 2 | 180000 | 95040 | 108000 | 36400 | 108000 | 1.6667 | 0.2
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 5 | 5 | 4 | 24000 | 13200 | 18000 | 13500 | 72000 | 31680 | 54000 | 27000 | 54000 | 1.3333 | 126000 | 91080 | 108000 | 54000 | 108000 | 1.1667 | 216000 | 71280 | 108000 | 54000 | 108000 | 2 | 270000 | 130680 | 162000 | 108000 | 162000 | 1.6667 | 0.2
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 2 | 5 | 2 | 16000 | 9600 | 12000 | 9100 | 48000 | 23040 | NP | NP | 23040 | 2.0833 | 84000 | 66240 | NP | NP | 66240 | 1.2681 | 144000 | 51840 | 72000 | 18200 | 72000 | 2 | 180000 | 95040 | 108000 | 36400 | 108000 | 1.6667 | 0.2
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 3 | 3 | 4 | 20500 | 14400 | 18000 | 13500 | 61500 | 34560 | 54000 | 27000 | 54000 | 1.1389 | 107625 | 99360 | 108000 | 54000 | 108000 | 0.99653 | 184500 | 77760 | 108000 | 54000 | 108000 | 1.7083 | 230625 | 142560 | 162000 | 108000 | 162000 | 1.4236 | 0.2
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 3 | 3 | 3 | 12000 | 10200 | 10500 | 10500 | 36000 | 24480 | 31500 | 21000 | 31500 | 1.1429 | 63000 | 70380 | 63000 | 42000 | 70380 | 0.89514 | 108000 | 55080 | 63000 | 42000 | 63000 | 1.7143 | 135000 | 100980 | 94500 | 84000 | 100980 | 1.3369 | 0.2
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | 2 | 2 | 7000 | 4800 | 7000 | 6000 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 63000 | 25920 | 21000 | 12000 | 25920 | 2.4306 | 78750 | 47520 | 42000 | 24000 | 47520 | 1.6572 | 0.2
R-2 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 9 | UL | UL | 12 | UL | 22800 | UL | 29900 | UL | 64980 | UL | 59800 | UL | 1 | UL | 167580 | UL | 119600 | UL | 1 | UL | 133380 | UL | 119600 | UL | 1 | UL | 235980 | UL | 239200 | UL | 1 | 0.05
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 5 | 5 | 4 | 24000 | 15000 | 18000 | 13500 | 72000 | 36000 | 54000 | 27000 | 54000 | 1.3333 | 126000 | 103500 | 108000 | 54000 | 108000 | 1.1667 | 216000 | 81000 | 108000 | 54000 | 108000 | 2 | 270000 | 148500 | 162000 | 108000 | 162000 | 1.6667 | 0.2
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 2 | 5 | 2 | 16000 | 9600 | 12000 | 9100 | 48000 | 23040 | NP | NP | 23040 | 2.0833 | 84000 | 66240 | NP | NP | 66240 | 1.2681 | 144000 | 51840 | 72000 | 18200 | 72000 | 2 | 180000 | 95040 | 108000 | 36400 | 108000 | 1.6667 | 0.2
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 5 | 5 | 4 | 24000 | 13200 | 18000 | 13500 | 72000 | 31680 | 54000 | 27000 | 54000 | 1.3333 | 126000 | 91080 | 108000 | 54000 | 108000 | 1.1667 | 216000 | 71280 | 108000 | 54000 | 108000 | 2 | 270000 | 130680 | 162000 | 108000 | 162000 | 1.6667 | 0.2
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 2 | 5 | 2 | 16000 | 9600 | 12000 | 9100 | 48000 | 23040 | NP | NP | 23040 | 2.0833 | 84000 | 66240 | NP | NP | 66240 | 1.2681 | 144000 | 51840 | 72000 | 18200 | 72000 | 2 | 180000 | 95040 | 108000 | 36400 | 108000 | 1.6667 | 0.2
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 3 | 3 | 4 | 20500 | 14400 | 18000 | 13500 | 61500 | 34560 | 54000 | 27000 | 54000 | 1.1389 | 107625 | 99360 | 108000 | 54000 | 108000 | 0.99653 | 184500 | 77760 | 108000 | 54000 | 108000 | 1.7083 | 230625 | 142560 | 162000 | 108000 | 162000 | 1.4236 | 0.2
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 3 | 3 | 3 | 12000 | 10200 | 10500 | 10500 | 36000 | 24480 | 31500 | 21000 | 31500 | 1.1429 | 63000 | 70380 | 63000 | 42000 | 70380 | 0.89514 | 108000 | 55080 | 63000 | 42000 | 63000 | 1.7143 | 135000 | 100980 | 94500 | 84000 | 100980 | 1.3369 | 0.2
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 2 | 2 | 2 | 7000 | 4800 | 7000 | 6000 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 63000 | 25920 | 21000 | 12000 | 25920 | 2.4306 | 78750 | 47520 | 42000 | 24000 | 47520 | 1.6572 | 0.2
R-3 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 4 | UL | UL | 3 | UL | 22800 | UL | UL | UL | 64980 | UL | UL | UL | 1 | UL | 167580 | UL | UL | UL | 1 | UL | 133380 | UL | UL | UL | 1 | UL | 235980 | UL | UL | UL | 1 | 0.05
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 5 | 5 | 3 | UL | 15000 | 18000 | UL | UL | 36000 | 54000 | UL | UL | 1 | UL | 103500 | 108000 | UL | UL | 1 | UL | 81000 | 108000 | UL | UL | 1 | UL | 148500 | 162000 | UL | UL | 1 | 0.2
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 2 | 5 | 3 | UL | 9600 | 12000 | UL | UL | 23040 | NP | UL | UL | 1 | UL | 66240 | NP | UL | UL | 1 | UL | 51840 | 72000 | UL | UL | 1 | UL | 95040 | 108000 | UL | UL | 1 | 0.2
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 5 | 5 | 3 | UL | 13200 | 18000 | UL | UL | 31680 | 54000 | UL | UL | 1 | UL | 91080 | 108000 | UL | UL | 1 | UL | 71280 | 108000 | UL | UL | 1 | UL | 130680 | 162000 | UL | UL | 1 | 0.2
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 2 | 5 | 3 | UL | 9600 | 12000 | UL | UL | 23040 | NP | UL | UL | 1 | UL | 66240 | NP | UL | UL | 1 | UL | 51840 | 72000 | UL | UL | 1 | UL | 95040 | 108000 | UL | UL | 1 | 0.2
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 3 | 3 | 3 | UL | 14400 | 18000 | UL | UL | 34560 | 54000 | UL | UL | 1 | UL | 99360 | 108000 | UL | UL | 1 | UL | 77760 | 108000 | UL | UL | 1 | UL | 142560 | 162000 | UL | UL | 1 | 0.2
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 3 | 3 | 3 | UL | 10200 | 10500 | UL | UL | 24480 | 31500 | UL | UL | 1 | UL | 70380 | 63000 | UL | UL | 1 | UL | 55080 | 63000 | UL | UL | 1 | UL | 100980 | 94500 | UL | UL | 1 | 0.2
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 2 | 2 | 2 | 3 | UL | 4800 | 7000 | UL | UL | NP | NP | UL | UL | 1 | UL | NP | NP | UL | UL | 1 | UL | 25920 | 21000 | UL | UL | 1 | UL | 47520 | 42000 | UL | UL | 1 | 0.2
S-1 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 5 | 6 | 6 | 12 | 48000 | 19950 | 30000 | 39900 | 144000 | 56857.5 | 90000 | 79800 | 90000 | 1.6 | 252000 | 146632.5 | 180000 | 159600 | 180000 | 1.4 | 432000 | 116707.5 | 180000 | 159600 | 180000 | 2.4 | 540000 | 206482.5 | 270000 | 319200 | 319200 | 1.6917 | 0.05
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 2 | 4 | 4 | 26000 | 13125 | 24000 | 18000 | 78000 | 31500 | NP | 36000 | 36000 | 2.1667 | 136500 | 90562.5 | NP | 72000 | 90562.5 | 1.5072 | 234000 | 70875 | 144000 | 72000 | 144000 | 1.625 | 292500 | 129937.5 | 216000 | 144000 | 216000 | 1.3542 | 0.2
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 2 | 2 | 4 | 2 | 17500 | 8400 | 16000 | 12000 | 52500 | NP | NP | NP | 0 | LNP | 91875 | NP | NP | NP | 0 | LNP | 157500 | 45360 | 96000 | 24000 | 96000 | 1.6406 | 196875 | 83160 | 144000 | 48000 | 144000 | 1.3672 | 0.2
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 3 | 2 | 4 | 4 | 26000 | 11550 | 24000 | 18000 | 78000 | 27720 | NP | 36000 | 36000 | 2.1667 | 136500 | 79695 | NP | 72000 | 79695 | 1.7128 | 234000 | 62370 | 144000 | 72000 | 144000 | 1.625 | 292500 | 114345 | 216000 | 144000 | 216000 | 1.3542 | 0.2
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 2 | 2 | 4 | 2 | 17500 | 8400 | 16000 | 12000 | 52500 | NP | NP | NP | 0 | LNP | 91875 | NP | NP | NP | 0 | LNP | 157500 | 45360 | 96000 | 24000 | 96000 | 1.6406 | 196875 | 83160 | 144000 | 48000 | 144000 | 1.3672 | 0.2
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 2 | 6 | 4 | 25500 | 12600 | 24000 | 18000 | 76500 | 30240 | NP | 36000 | 36000 | 2.125 | 133875 | 86940 | NP | 72000 | 86940 | 1.5399 | 229500 | 68040 | 144000 | 72000 | 144000 | 1.5938 | 286875 | 124740 | 216000 | 144000 | 216000 | 1.3281 | 0.2
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 3 | 2 | 1 | 1 | 3 | 14000 | 8925 | 9000 | 14000 | 42000 | NP | NP | 28000 | 28000 | 1.5 | 73500 | NP | NP | 56000 | 56000 | 1.3125 | 126000 | 48195 | NP | 56000 | 56000 | 2.25 | 157500 | 88357.5 | NP | 112000 | 112000 | 1.4062 | 0.2
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 1 | 1 | 1 | 1 | 2 | 9000 | 4200 | 6000 | 8000 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | NP | NP | NP | 16000 | 16000 | NP | NP | NP | NP | 32000 | 32000 | NP | 0.2
S-2 | IB | Y | Y | Y | Y | Y | Y | Y | Y | 11 | 7 | 6 | 6 | 12 | 79000 | 34200 | 30000 | 59900 | 237000 | 97470 | 90000 | 119800 | 119800 | 1.9783 | 414750 | 251370 | 180000 | 239600 | 251370 | 1.65 | 711000 | 200070 | 180000 | 239600 | 239600 | 2.9674 | 888750 | 353970 | 270000 | 479200 | 479200 | 1.8547 | 0.05
| IIA | Y | Y | Y | Y | Y | Y | Y | Y | 5 | 5 | 4 | 4 | 4 | 39000 | 22500 | 24000 | 27000 | 117000 | 54000 | 72000 | 54000 | 72000 | 1.625 | 204750 | 155250 | 144000 | 108000 | 155250 | 1.3188 | 351000 | 121500 | 144000 | 108000 | 144000 | 2.4375 | 438750 | 222750 | 216000 | 216000 | 222750 | 1.9697 | 0.2
| IIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 4 | 4 | 2 | 26000 | 14400 | 16000 | 18000 | 78000 | 34560 | 48000 | NP | 48000 | 1.625 | 136500 | 99360 | 96000 | NP | 99360 | 1.3738 | 234000 | 77760 | 96000 | 36000 | 96000 | 2.4375 | 292500 | 142560 | 144000 | 72000 | 144000 | 2.0312 | 0.2
| IIIA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 4 | 4 | 4 | 4 | 39000 | 19800 | 24000 | 27000 | 117000 | 47520 | 72000 | 54000 | 72000 | 1.625 | 204750 | 136620 | 144000 | 108000 | 144000 | 1.4219 | 351000 | 106920 | 144000 | 108000 | 144000 | 2.4375 | 438750 | 196020 | 216000 | 216000 | 216000 | 2.0312 | 0.2
| IIIB | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 4 | 4 | 2 | 26000 | 14400 | 16000 | 18000 | 78000 | 34560 | 48000 | NP | 48000 | 1.625 | 136500 | 99360 | 96000 | NP | 99360 | 1.3738 | 234000 | 77760 | 96000 | 36000 | 96000 | 2.4375 | 292500 | 142560 | 144000 | 72000 | 144000 | 2.0312 | 0.2
| IV | Y | Y | Y | Y | Y | Y | Y | Y | 5 | 5 | 6 | 6 | 4 | 38500 | 21600 | 24000 | 27000 | 115500 | 51840 | 72000 | 54000 | 72000 | 1.6042 | 202125 | 149040 | 144000 | 108000 | 149040 | 1.3562 | 346500 | 116640 | 144000 | 108000 | 144000 | 2.4062 | 433125 | 213840 | 216000 | 216000 | 216000 | 2.0052 | 0.2
| VA | Y | Y | Y | Y | Y | Y | Y | Y | 4 | 3 | 1 | 1 | 3 | 21000 | 15300 | 9000 | 21000 | 63000 | 36720 | NP | 42000 | 42000 | 1.5 | 110250 | 105570 | NP | 84000 | 105570 | 1.0443 | 189000 | 82620 | NP | 84000 | 84000 | 2.25 | 236250 | 151470 | NP | 168000 | 168000 | 1.4062 | 0.2
| VB | Y | Y | Y | Y | Y | Y | Y | Y | 2 | 2 | 1 | 1 | 2 | 13500 | 7200 | 6000 | 12000 | NP | NP | NP | NP | 0 | NP | NP | NP | NP | NP | 0 | NP | 121500 | 38880 | NP | 24000 | 38880 | 3.125 | 151875 | 71280 | NP | 48000 | 71280 | 2.1307 | 0.2

## Summary
Cells identified at Dec 10 - 11 meeting that result in total building area that is more than 10% greater than total area permitted by largest legacy code.
IBC more than 10% greater than largest legacy code area.
IBC more than 10% less than largest legacy code area.
LNP - Not pemitted by legacy codes but permitted by IBC
INF - Infinity
Ratio of IBC area to largest legacy code area for condition stated:
[6 empty] | Without sprinklers | [5 empty] | With sprinklers
Occup. | Type Const. | Tabular area of code |  |  |  | Open space (ft) | [5 empty] | Open space (ft)
[6 empty] | < 20 |  |  | 40 |  |  | < 20 |  |  | 40
|  | IBC | NBC | SBC | UBC | Number of stories |  |  | Number of stories |  |  | Number of stories |  |  | Number of stories
[6 empty] | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
A-1 | IB | UL | 19950 | UL | 29900 | bar: Number of stories 1 to Number of stories 3
| IIA | 15500 | 13125 | 12000 | 13500 | 1.1481 | 1.1481 | 1.2917 | 0.82667 | 0.82667 | 0.89855 | 1.5309 | 1.181 | 1.9375 | 0.90895 | 0.98413 | 1.342
| IIB | 8500 | 8400 | 8000 | NP | 1.0119 | 1.0119 | NP | 0.70833 | 0.70833 | NP | 1.3492 | 1.0119 | 1.6865 | 1.0681 | 0.84325 | 1.1499
| IIIA | 14000 | 11550 | 12000 | 13500 | 1.037 | 1.037 | 1.5152 | 0.84848 | 0.84848 | 0.92227 | 1.3827 | 1.2121 | 2.0202 | 0.82099 | 0.97222 | 1.3774
| IIIB | 8500 | 8400 | 8000 | NP | 1.0119 | 1.0119 | NP | 0.70833 | 0.70833 | NP | 1.3492 | 1.0119 | 1.6865 | 1.0681 | 0.84325 | 1.1499
| IV | 15000 | 12600 | 12000 | 13500 | 1.1111 | 1.1111 | 1.4881 | 0.83333 | 0.83333 | 0.9058 | 1.4815 | 1.1905 | 1.9841 | 0.87963 | 0.99206 | 1.3528
| VA | 11500 | 8925 | 7500 | 10500 | 1.0952 | 1.0952 | NP | 0.90196 | 0.95833 | NP | 1.4603 | 1.2885 | 4.9286 | 0.86706 | 1.0268 | 3.0804
| VB | 5500 | 4200 | 5000 | NP | 1.1 | NP | NP | 0.91667 | NP | NP | 1.4667 | 1.3095 | NP | 1.3062 | 1.0913 | NP
A-2 | IB | UL | 5700 | UL | 29900 | bar: Number of stories 1 to Number of stories 3
| IIA | 15500 | 3750 | 12000 | 13500 | 1.1481 | 1.1481 | LNP | 1.0046 | 1.0046 | LNP | 1.5309 | 1.7222 | 3.875 | 0.90895 | 1.0764 | 2.4219
| IIB | 9500 | 2400 | 8000 | 9100 | 1.044 | 1.1875 | NP | 0.91346 | 1.0391 | NP | 1.3919 | 1.7812 | 3.5625 | 0.82647 | 1.4844 | 2.2266
| IIIA | 14000 | 3300 | 12000 | 13500 | 1.037 | 1.037 | LNP | 0.90741 | 0.90741 | LNP | 1.3827 | 1.5556 | 3.5 | 0.82099 | 0.97222 | 2.1875
| IIIB | 9500 | 2400 | 8000 | 9100 | 1.044 | 1.1875 | NP | 0.91346 | 1.0391 | NP | 1.3919 | 1.7812 | 3.5625 | 0.82647 | 1.4844 | 2.2266
| IV | 15000 | 3600 | 12000 | 13500 | 1.1111 | 1.1111 | LNP | 0.97222 | 0.97222 | LNP | 1.4815 | 1.6667 | 3.75 | 0.87963 | 1.0417 | 2.3438
| VA | 11500 | 2550 | 7500 | 10500 | 1.0952 | 1.0952 | NP | 0.95833 | 0.95833 | NP | 1.4603 | 1.6429 | 4.9286 | 0.86706 | 1.0268 | 3.0804
| VB | 6000 | 1200 | 5000 | 6000 | 1 | NP | NP | 0.875 | NP | NP | 1.3333 | 3 | NP | 0.79167 | 1.875 | NP
A-3 | IB | UL | 19950 | UL | 29900 | bar: Number of stories 1 to Number of stories 3
| IIA | 15500 | 13125 | 12000 | 13500 | 1.1481 | 1.1481 | 1.4762 | 0.82667 | 0.82667 | 0.89855 | 1.5309 | 1.181 | 1.9683 | 0.90895 | 0.98413 | 1.342
| IIB | 9500 | 8400 | 8000 | 9100 | 1.044 | 1.1875 | NP | 0.79167 | 0.79167 | NP | 1.3919 | 1.131 | 1.8849 | 0.82647 | 0.94246 | 1.2852
| IIIA | 14000 | 11550 | 12000 | 13500 | 1.037 | 1.037 | 1.5152 | 0.84848 | 0.84848 | 0.92227 | 1.3827 | 1.2121 | 2.0202 | 0.82099 | 0.97222 | 1.3774
| IIIB | 9500 | 8400 | 8000 | 9100 | 1.044 | 1.131 | NP | 0.79167 | 0.79167 | NP | 1.3919 | 1.131 | 1.8849 | 0.82647 | 0.94246 | 1.2852
| IV | 15000 | 12600 | 12000 | 13500 | 1.1111 | 1.1111 | 1.4881 | 0.83333 | 0.83333 | 0.9058 | 1.4815 | 1.1905 | 1.9841 | 0.87963 | 0.99206 | 1.3528
| VA | 11500 | 8925 | 7500 | 10500 | 1.0952 | 1.0952 | NP | 0.90196 | 0.95833 | NP | 1.4603 | 1.2885 | 4.6 | 0.86706 | 1.0268 | 2.875
| VB | 6000 | 4200 | 5000 | 6000 | 1 | NP | NP | 0.875 | NP | NP | 1.3333 | 1.4286 | NP | 0.79167 | 1.1905 | NP
A-4 | IB | UL | 19950 | UL | 29900 | bar: Number of stories 1 to Number of stories 3
| IIA | 15500 | 13125 | 12000 | 13500 | 1.1481 | 1.1481 | 1.4762 | 0.82667 | 0.82667 | 0.89855 | 1.5309 | 1.181 | 1.9683 | 0.90895 | 0.98413 | 1.342
| IIB | 9500 | 8400 | 8000 | 9100 | 1.044 | 1.1875 | NP | 0.79167 | 0.79167 | NP | 1.3919 | 1.131 | 1.8849 | 0.82647 | 0.94246 | 1.2852
| IIIA | 14000 | 11550 | 12000 | 13500 | 1.037 | 1.037 | 1.5152 | 0.84848 | 0.84848 | 0.92227 | 1.3827 | 1.2121 | 2.0202 | 0.82099 | 0.97222 | 1.3774
| IIIB | 9500 | 8400 | 8000 | 9100 | 1.044 | 1.131 | NP | 0.79167 | 0.79167 | NP | 1.3919 | 1.131 | 1.8849 | 0.82647 | 0.94246 | 1.2852
| IV | 15000 | 12600 | 12000 | 13500 | 1.1111 | 1.1111 | 1.4881 | 0.83333 | 0.83333 | 0.9058 | 1.4815 | 1.1905 | 1.9841 | 0.87963 | 0.99206 | 1.3528
| VA | 11500 | 8925 | 7500 | 10500 | 1.0952 | 1.0952 | NP | 0.90196 | 0.95833 | NP | 1.4603 | 1.2885 | 4.9286 | 0.86706 | 1.0268 | 3.0804
| VB | 6000 | 4200 | 5000 | 6000 | 1 | NP | NP | 0.875 | NP | NP | 1.3333 | 1.4286 | NP | 0.79167 | 1.1905 | NP
A-5 | IB | UL |  | UL | 29000 | bar: Number of stories 1 to Number of stories 3
| IIA | UL |  | 12000 | 13500 | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF
| IIB | UL |  | 8000 | 9100 | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF
| IIIA | UL |  | 12000 | 13500 | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF
| IIIB | UL |  | 8000 | 9100 | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF
| IV | UL |  | 12000 | 13500 | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF
| VA | UL |  | 7500 | 10500 | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF
| VB | UL |  | 5000 | 6000 | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF
B | IB | UL | 34200 | UL | 39900 | bar: Number of stories 1 to Number of stories 3
| IIA | 37500 | 22500 | 25500 | 18000 | 1.4706 | 1.4706 | 1.4706 | 1.1667 | 1.1667 | 1.2681 | 1.9608 | 1.6667 | 2.2059 | 1.6493 | 1.3889 | 1.8382
| IIB | 23000 | 14400 | 17000 | 12000 | 1.3529 | 1.3529 | 1.9965 | 1.1181 | 1.1181 | 1.2153 | 1.8039 | 1.5972 | 2.0294 | 1.5174 | 1.331 | 1.6912
| IIIA | 28500 | 19800 | 21000 | 18000 | 1.3571 | 1.3571 | 1.3571 | 1.0076 | 1.0076 | 1.0952 | 1.8095 | 1.4394 | 2.0357 | 1.2535 | 1.1995 | 1.6357
| IIIB | 19000 | 14400 | 14000 | 12000 | 1.3194 | 1.3194 | 1.6493 | 0.92361 | 0.92361 | 1.0039 | 1.7593 | 1.3194 | 2.0357 | 1.2535 | 1.0995 | 1.4994
| IV | 36000 | 21600 | 25500 | 18000 | 1.4118 | 1.4118 | 1.4118 | 1.1667 | 1.1667 | 1.2353 | 1.8824 | 1.6667 | 2.1176 | 1.5833 | 1.3889 | 1.7647
| VA | 18000 | 15300 | 13500 | 14000 | 1.1765 | 1.1765 | 1.4706 | 0.82353 | 0.82353 | 0.89514 | 1.5686 | 1.1765 | 1.9608 | 1.0179 | 0.98039 | 1.3369
| VB | 9000 | 7200 | 9000 | 8000 | 1 | 1 | NP | 0.875 | 0.875 | NP | 1.3333 | 1.25 | 2.0833 | 0.89062 | 1.0417 | 1.4205
E | IB | UL | 34200 | UL | 45200 | bar: Number of stories 1 to Number of stories 3
| IIA | 26500 | 22500 | 18000 | 20200 | 1.1778 | 1.1778 | 1.4722 | 0.82444 | 0.82444 | 0.89614 | 1.5704 | 1.1778 | 1.963 | 1.0386 | 0.98148 | 1.3384
| IIB | 14500 | 14400 | 12000 | 13500 | 1.0069 | 1.0069 | NP | 0.70486 | 0.70486 | NP | 1.3426 | 1.0069 | 1.6782 | 0.85031 | 0.83912 | 1.1443
| IIIA | 23500 | 19800 | 18000 | 20200 | 1.1634 | 1.1634 | 1.4836 | 0.83081 | 0.83081 | 0.90305 | 1.5512 | 1.1869 | 1.9781 | 0.921 | 0.98906 | 1.3487
| IIIB | 14500 | 14400 | 12000 | 13500 | 1.0069 | 1.0069 | NP | 0.70486 | 0.70486 | NP | 1.3426 | 1.0069 | 1.6782 | 0.85031 | 0.83912 | 1.1443
| IV | 25500 | 21600 | 18000 | 20200 | 1.1806 | 1.1806 | 1.4757 | 0.82639 | 0.82639 | 0.89825 | 1.5741 | 1.1806 | 1.9676 | 0.99938 | 0.9838 | 1.3415
| VA | 18500 | 15300 | 12000 | 15700 | 1.1783 | NP | NP | 0.84641 | NP | NP | 1.5711 | 1.2092 | NP | 0.93286 | 1.0076 | NP
| VB | 9500 | 7200 | 8000 | 9100 | 1.044 | NP | NP | 0.91346 | NP | NP | 1.3919 | 1.3194 | NP | 0.82647 | 1.0995 | NP
F-1 | IB | UL | 22800 | UL | 39900 | bar: Number of stories 1 to Number of stories 3
| IIA | 25000 | 15000 | 31500 | 18000 | 0.79365 | 0.79365 | 2.0833 | 0.69444 | 0.69444 | 1.2681 | 1.0582 | 1.1905 | 1.1905 | 0.94246 | 0.99206 | 0.99206
| IIB | 15500 | 9600 | 21000 | 12000 | 0.7381 | 0.7381 | NP | 0.64583 | 0.64583 | NP | 0.98413 | 1.1071 | 1.1071 | 0.87649 | 0.92262 | 0.92262
| IIIA | 19000 | 13200 | 22500 | 18000 | 0.84444 | 0.84444 | 1.5833 | 0.73889 | 0.73889 | 1.0952 | 1.1259 | 1.2667 | 1.2667 | 0.83565 | 0.98958 | 1.0556
| IIIB | 12000 | 9600 | 15000 | 12000 | 0.8 | 0.8 | NP | 0.7 | 0.7 | NP | 1.0667 | 1.2 | 1.2 | 0.79167 | 0.9375 | 1
| IV | 33500 | 14400 | 31500 | 18000 | 1.0635 | 1.0635 | 1.0635 | 0.93056 | 0.93056 | 0.93056 | 1.418 | 1.5952 | 1.5952 | 1.2629 | 1.3294 | 1.3294
| VA | 14000 | 10200 | 15000 | 14000 | 0.93333 | 1 | NP | 0.81667 | 0.875 | NP | 1.2444 | 1.3725 | 2.25 | 0.79167 | 0.9375 | 1.4062
| VB | 8500 | 4800 | 10000 | 8000 | 0.85 | NP | NP | 0.74375 | NP | NP | 1.1333 | 1.5938 | NP | 0.84115 | 0.99609 | NP
F-2 | IB | UL | 34200 | UL | 59900 | bar: Number of stories 1 to Number of stories 3
| IIA | 37500 | 22500 | 31500 | 27000 | 1.1905 | 1.1905 | 2.0833 | 1.0417 | 1.0417 | 1.2681 | 1.5873 | 1.6667 | 1.7857 | 1.0995 | 1.3021 | 1.4881
| IIB | 23000 | 14400 | 21000 | 18000 | 1.0952 | 1.0952 | 1.9965 | 0.95833 | 0.95833 | 1.2153 | 1.4603 | 1.5972 | 1.6429 | 1.0116 | 1.1979 | 1.369
| IIIA | 28500 | 19800 | 22500 | 27000 | 1.0556 | 1.0556 | 1.5833 | 0.92361 | 0.92361 | 1.0952 | 1.4074 | 1.4394 | 1.9 | 0.83565 | 0.98958 | 1.4844
| IIIB | 18000 | 14400 | 15000 | 18000 | 1 | 1 | 1.5625 | 0.875 | 0.875 | 0.95109 | 1.3333 | 1.25 | 1.8 | 0.79167 | 0.9375 | 1.4205
| IV | 50500 | 21600 | 31500 | 27000 | 1.6032 | 1.6032 | 1.6032 | 1.4028 | 1.4028 | 1.4028 | 2.1376 | 2.338 | 2.4048 | 1.4807 | 1.7535 | 2.004
| VA | 21000 | 15300 | 15000 | 21000 | 1 | 1 | 1.5 | 0.875 | 0.875 | 1.0443 | 1.3333 | 1.3725 | 2.25 | 0.79167 | 0.9375 | 1.4062
| VB | 13000 | 7200 | 10000 | 12000 | 1.0833 | 1.0833 | NP | 0.94792 | 0.94792 | NP | 1.4444 | 1.625 | 3.0093 | 0.85764 | 1.0156 | 2.0518
H-1 | 1A | 21000 | 14400 | 5000 | 15000 | 1.4 | NP | NP | 1.0208 | NP | NP | 1.4 | NP | NP | 1.0208 | NP | NP
| IB | 16500 | 11400 | 4000 | 12400 | 1.3306 | NP | NP | 1.0132 | NP | NP | 1.3306 | NP | NP | 1.0132 | NP | NP
| IIA | 11000 | 7500 | 2500 | 5600 | 1.4667 | NP | NP | 1.0267 | NP | NP | 1.4667 | NP | NP | 1.0267 | NP | NP
| IIB | 7000 | 4800 | 1666.6667 | 3700 | 1.4583 | NP | NP | 1.0208 | NP | NP | 1.4 | NP | NP | 1.0208 | NP | NP
| IIIA | 9500 | 6600 | 2500 | NP | 1.4394 | NP | NP | 1.0076 | NP | NP | 1.2667 | NP | NP | 1.0076 | NP | NP
| IIIB | 7000 | 4800 | NP | NP | 1.4583 | NP | NP | 1.0208 | NP | NP | 1.4583 | NP | NP | 1.0208 | NP | NP
| IV | 10500 | 7200 | 2500 | NP | 1.4583 | NP | NP | 1.0208 | NP | NP | 1.4 | NP | NP | 1.0208 | NP | NP
| VA | 7500 | 5100 | NP | NP | 1.4706 | NP | NP | 1.0294 | NP | NP | 1.4706 | NP | NP | 1.0294 | NP | NP
| VB | NP | NP | NP | NP | bar: Number of stories 1 to Number of stories 3
H-2 | 1A | 21000 | 14400 | 5000 | 15000 | 1.4 | 1.4 | 1.4583 | 1.0208 | 1.0208 | 1.0208 | 1.4 | 1.4 | 1.4583 | 1.0208 | 1.0208 | 1.0208
| IB | 16500 | 11400 | 4000 | 12400 | 1.3306 | 1.3306 | 1.5235 | 1.0132 | 1.0132 | 1.0338 | 1.3306 | 1.3306 | 1.5235 | 1.0132 | 1.0132 | 1.0338
| IIA | 11000 | 7500 | 2500 | 5600 | 1.4667 | LNP | NP | 1.0267 | 1.0267 | NP | 1.4667 | 1.4667 | NP | 1.0267 | 1.0267 | NP
| IIB | 7000 | 4800 | 1666.6667 | 3700 | 1.4583 | NP | NP | 1.0208 | NP | NP | 1.4 | NP | NP | 1.0208 | NP | NP
| IIIA | 9500 | 6600 | 2500 | 5600 | 1.4394 | 1.4394 | NP | 1.0076 | 1.0076 | NP | 1.2667 | 1.4394 | NP | 1.0076 | 1.0076 | NP
| IIIB | 7000 | 4800 | 1333.3333 | 3700 | 1.4583 | NP | NP | 1.0208 | NP | NP | 1.4583 | NP | NP | 1.0208 | NP | NP
| IV | 10500 | 7200 | 2500 | 5600 | 1.4583 | 1.4583 | NP | 1.0208 | 1.0208 | NP | 1.4 | 1.4583 | NP | 1.0208 | 1.0208 | NP
| VA | 7500 | 5100 | 833.3333 | 4400 | 1.4706 | NP | NP | 1.0294 | NP | NP | 1.4706 | NP | NP | 1.0294 | NP | NP
| VB | 3000 | NP | NP | 2500 | 1.2 | NP | NP | 1.05 | NP | NP | 1.2 | NP | NP | 1.05 | NP | NP
H-3 | IA | UL | 28800 | 10000 | UL | bar: Number of stories 1 to Number of stories 3
| IB | 60000 | 22800 | 6666.6667 | 24800 | 2.4194 | 2.4194 | 2.7701 | 1.8421 | 1.8421 | 1.8797 | 2.4194 | 2.4194 | 2.7701 | 1.8421 | 1.8421 | 1.8797
| IIA | 26500 | 15000 | 3333.3333 | 11200 | 1.7667 | 2.3661 | 2.2083 | 1.2367 | 1.2367 | 1.3442 | 1.7667 | 1.7667 | 2.2083 | 1.2367 | 1.2367 | 1.3442
| IIB | 14000 | 9600 | 2500 | 7500 | 1.4583 | 1.4583 | NP | 1.0208 | 1.0208 | NP | 1.4583 | 1.4583 | NP | 1.0208 | 1.0208 | NP
| IIIA | 17500 | 13200 | 3333.3333 | 11200 | 1.3258 | 1.3258 | 1.6572 | 0.92803 | 0.92803 | 1.0087 | 1.3258 | 1.3258 | 1.6572 | 0.92803 | 0.92803 | 1.0087
| IIIB | 13000 | 9600 | 2500 | 7500 | 1.3542 | 1.3542 | NP | 0.94792 | 0.94792 | NP | 1.3542 | 1.3542 | NP | 0.94792 | 0.94792 | NP
| IV | 25500 | 14400 | 3333.3333 | 11200 | 1.7708 | 1.7708 | 2.2135 | 1.2396 | 1.2396 | 1.3474 | 1.7708 | 1.7708 | 2.2135 | 1.2396 | 1.2396 | 1.3474
| VA | 10000 | 10200 | 1333.3333 | 8800 | 0.98039 | 0.98039 | NP | 0.68627 | 0.68627 | NP | 0.98039 | 0.98039 | NP | 0.68627 | 0.68627 | NP
| VB | 5000 | 4800 | NP | 5100 | 0.98039 | NP | NP | 0.72917 | NP | NP | 0.98039 | NP | NP | 0.72917 | NP | NP
H-4 | IB | UL | 34200 | UL | 39900 | bar: Number of stories 1 to Number of stories 3
| IIA | 37000 | 22500 | 48000 | 18000 | 0.77083 | 0.77083 | 0.77083 | 0.67448 | 0.67448 | 0.67448 | 1.0278 | 1.1562 | 1.1562 | 0.91536 | 0.96354 | 0.96354
| IIB | 17500 | 14400 | 32000 | 12000 | 0.54688 | 0.54688 | 0.54688 | 0.47852 | 0.47852 | 0.47852 | 0.72917 | 0.82031 | 0.82031 | 0.64941 | 0.68359 | 0.68359
| IIIA | 28500 | 19800 | 48000 | 18000 | 0.59375 | 0.59375 | 0.59375 | 0.51953 | 0.51953 | 0.51953 | 0.79167 | 0.89062 | 0.89062 | 0.70508 | 0.74219 | 0.74219
| IIIB | 17500 | 14400 | 32000 | 12000 | 0.54688 | 0.54688 | 0.54688 | 0.47852 | 0.47852 | 0.47852 | 0.72917 | 0.82031 | 0.82031 | 0.64941 | 0.68359 | 0.68359
| IV | 36000 | 21600 | 48000 | 18000 | 0.75 | 0.75 | 0.75 | 0.65625 | 0.65625 | 0.65625 | 1 | 1.125 | 1.125 | 0.89062 | 0.9375 | 0.9375
| VA | 18000 | 15300 | 27000 | 14000 | 0.66667 | 1.1765 | 1.4706 | 0.58333 | 0.82353 | 0.89514 | 0.88889 | 1.1765 | 1.9608 | 0.79167 | 0.98039 | 1.3369
| VB | 6500 | 7200 | 18000 | 8000 | 0.36111 | 0.90278 | NP | 0.31597 | 0.63194 | NP | 0.48148 | 0.90278 | 1.5046 | 0.42882 | 0.75231 | 1.0259
H-5 | IB | UL | 34400 | UL | 39900 | bar: Number of stories 1 to Number of stories 3
| IIA | 37500 | 22500 | 63000 | 18000 | 0.59524 | 0.59524 | 0.59524 | 0.52083 | 0.52083 | 0.52083 | 0.79365 | 0.89286 | 0.89286 | 0.70685 | 0.74405 | 0.74405
| IIB | 23000 | 14400 | 42000 | 12000 | 0.54762 | 0.54762 | 0.54762 | 0.47917 | 0.47917 | 0.47917 | 0.73016 | 0.82143 | 0.82143 | 0.6503 | 0.68452 | 0.68452
| IIIA | 28500 | 19800 | 45000 | 18000 | 0.63333 | 0.63333 | 0.63333 | 0.55417 | 0.55417 | 0.55417 | 0.84444 | 0.95 | 0.95 | 0.75208 | 0.79167 | 0.79167
| IIIB | 19000 | 14400 | 30000 | 12000 | 0.63333 | 0.63333 | 0.63333 | 0.55417 | 0.55417 | 0.55417 | 0.84444 | 0.95 | 0.95 | 0.75208 | 0.79167 | 0.79167
| IV | 36000 | 21600 | 63000 | 18000 | 0.57143 | 0.57143 | 0.57143 | 0.5 | 0.5 | 0.5 | 0.7619 | 0.85714 | 0.85714 | 0.67857 | 0.71429 | 0.71429
| VA | 18000 | 15300 | 45000 | 14000 | 0.4 | 1.1765 | 1.4706 | 0.35 | 0.82353 | 0.89514 | 0.53333 | 1.1765 | 1.9608 | 0.475 | 0.98039 | 1.3369
| VB | 9000 | 7200 | 45000 | 8000 | 0.2 | 1.25 | NP | 0.175 | 0.875 | NP | 0.26667 | 1.25 | NP | 0.2375 | 1.0417 | NP
I-1 | IB | 55000 | 19950 |  | 15100 | 2.7569 | 2.7569 | 2.902 | 1.9298 | 1.9298 | 1.9692 | 3.6759 | 2.7569 | 4.2414 | 2.8836 | 2.2974 | 2.9966
Ass't | IIA | 19000 | 13125 |  | 6800 | 1.4476 | 1.4476 | 1.8095 | 1.0133 | 1.0133 | 1.1014 | 1.9302 | 1.4476 | 2.4127 | 1.528 | 1.2063 | 1.645
| IIB | 10000 | 8400 |  | NP | 1.1905 | 1.1905 | 1.4881 | 0.83333 | 0.83333 | 0.9058 | 1.5873 | 1.1905 | 1.9841 | 1.2566 | 0.99206 | 1.3528
| IIIA | 16500 | 11550 |  | 6800 | 1.4286 | 1.4286 | 1.7857 | 1 | 1 | 1.087 | 1.9048 | 1.4286 | 2.381 | 1.5079 | 1.1905 | 1.6234
| IIIB | 10000 | 8400 |  | NP | 1.1905 | 1.1905 | 1.4881 | 0.83333 | 0.83333 | 0.9058 | 1.5873 | 1.1905 | 1.9841 | 1.2566 | 0.99206 | 1.3528
| IV | 18000 | 12600 |  | 6800 | 1.4286 | 1.4286 | 1.7857 | 1 | 1 | 1.087 | 1.9048 | 1.4286 | 2.381 | 1.5079 | 1.1905 | 1.6234
| VA | 10500 | 8925 |  | 5200 | 1.1765 | 1.1765 | 1.4706 | 0.82353 | 0.82353 | 0.89514 | 1.5686 | 1.1765 | 1.9608 | 1.2418 | 0.98039 | 1.3369
| VB | 4500 | 4200 |  | NP | 1.0714 | 1.0714 | NP | 0.75 | 0.75 | NP | 1.4286 | 1.0714 | 1.7857 | 1.131 | 0.89286 | 1.2175
I-2 | IB | UL | 17100 | UL | 15100 | bar: Number of stories 1 to Number of stories 3
Hos | IIA | 15000 | 11250 | 15000 | 6800 | 1 | 1 | NP | 0.875 | 0.875 | NP | 1.3333 | 1.3333 | 1.5 | 1.1875 | 1.1111 | 1.25
| IIB | 11000 | 7200 | 10000 | NP | 1.1 | NP | NP | 0.9625 | NP | NP | 1.4667 | NP | NP | 1.3062 | NP | NP
| IIIA | 12000 | 9900 | 10500 | 6800 | 1.1429 | NP | NP | 0.84848 | NP | NP | 1.5238 | NP | NP | 1.2795 | NP | NP
| IIIB | NP | NP | NP | NP | bar: Number of stories 1 to Number of stories 3
| IV | 12000 | 10800 | 12000 | 6800 | 1 | NP | NP | 0.77778 | NP | NP | 1.3333 | NP | NP | 1.1728 | NP | NP
| VA | 9500 | 7650 | 7500 | 5200 | 1.2418 | NP | NP | 0.86928 | NP | NP | 1.6558 | NP | NP | 1.3108 | NP | NP
| VB | NP | NP | NP | NP | bar: Number of stories 1 to Number of stories 3
I-3 | IB | UL | 14250 | UL | 15100 | bar: Number of stories 1 to Number of stories 3
| IIA | 15000 | 9375 | 15000 | NP | 1 | 1 | NP | 0.875 | 0.875 | NP | 1.3333 | 1.5 | 1.5 | 1.1875 | 1.25 | 1.25
| IIB | 10000 | 6000 | 10000 | NP | 1 | NP | NP | 0.875 | NP | NP | 1.3333 | 1.5 | NP | 1.1875 | 1.25 | NP
| IIIA | 10500 | 8250 | 10500 | NP | 1 | 1 | NP | 0.875 | 0.875 | NP | 1.3333 | 1.2727 | 1.5 | 1.1875 | 1.0606 | 1.25
| IIIB | 7500 | 6000 | 7000 | NP | 1.0714 | NP | NP | 0.875 | NP | NP | 1.4286 | 1.25 | NP | 1.2723 | 1.0417 | NP
| IV | 12000 | 9000 | 12000 | NP | 1 | 1 | NP | 0.875 | 0.875 | NP | 1.3333 | 1.3333 | 2.2222 | 1.1875 | 1.1111 | 1.5152
| VA | 7500 | 6375 | 7500 | NP | 1 | 1 | NP | 0.82353 | 0.875 | NP | 1.3333 | 1.1765 | 1.5 | 1.1875 | 0.98039 | 1.25
| VB | 5000 | NP | 5000 | NP | 1 | NP | NP | 0.875 | NP | NP | 1.3333 | 1.5 | NP | 1.1875 | 1.25 | NP
I-4 | IB | 60500 | 34200 |  | 45200 | 1.3385 | 1.3385 | 1.8621 | 1.1712 | 1.1712 | 1.2636 | 1.7847 | 1.769 | 2.7215 | 1.0596 | 1.2548 | 1.8823
| IIA | 26500 | 22500 |  | 20200 | 1.1778 | 1.1778 | 1.4722 | 0.82444 | 0.82444 | 0.89614 | 1.5704 | 1.1778 | 1.963 | 1.0386 | 0.98148 | 1.3384
| IIB | 13000 | 14400 |  | 13500 | 0.90278 | LNP | NP | 0.63194 | 0.63194 | NP | 1.2037 | 0.90278 | 1.5046 | 0.76235 | 0.75231 | 1.0259
| IIIA | 23500 | 19800 |  | 20200 | 1.1634 | 1.1634 | 1.4836 | 0.83081 | 0.83081 | 0.90305 | 1.5512 | 1.1869 | 1.9781 | 0.921 | 0.98906 | 1.3487
| IIIB | 13000 | 14400 |  | 13500 | 0.90278 | 0.90278 | NP | 0.63194 | 0.63194 | NP | 1.2037 | 0.90278 | 1.5046 | 0.76235 | 0.75231 | 1.0259
| IV | 25500 | 21600 |  | 20200 | 1.1806 | 1.1806 | 1.4757 | 0.82639 | 0.82639 | 0.89825 | 1.5741 | 1.1806 | 1.9676 | 0.99938 | 0.9838 | 1.3415
| VA | 18500 | 15300 |  | 15700 | 1.1783 | NP | NP | 0.84641 | NP | NP | 1.5711 | 1.2092 | NP | 0.93286 | 1.0076 | NP
| VB | 9000 | 7200 |  | 9100 | 0.98901 | NP | NP | 0.86538 | NP | NP | 1.3187 | 1.25 | NP | 0.78297 | 1.0417 | NP
M | IB | UL | 22800 | 15000 | 39900 | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF | INF
| IIA | 21500 | 15000 | 13500 | 18000 | 1.1944 | 1.1944 | 1.5926 | 1.0033 | 1.0033 | 1.0906 | 1.5926 | 1.4333 | 2.3889 | 0.9456 | 1.1198 | 1.6288
| IIB | 12500 | 9600 | 9000 | 12000 | 1.0417 | 1.0417 | LNP | 0.91146 | 0.91146 | LNP | 1.3889 | 1.3021 | 2.0833 | 0.82465 | 0.97656 | 1.4796
| IIIA | 18500 | 13200 | 13500 | 18000 | 1.0278 | 1.0278 | 1.3704 | 0.89931 | 0.89931 | 1.0664 | 1.3704 | 1.4015 | 2.0556 | 0.81366 | 0.96354 | 1.4453
| IIIB | 12500 | 9600 | 9000 | 12000 | 1.0417 | 1.0417 | LNP | 0.91146 | 0.91146 | LNP | 1.3889 | 1.3021 | 2.0833 | 0.82465 | 0.97656 | 1.4796
| IV | 20500 | 14400 | 13500 | 18000 | 1.1389 | 1.1389 | 1.5185 | 0.99653 | 0.99653 | 1.0832 | 1.5185 | 1.4236 | 2.2778 | 0.90162 | 1.0677 | 1.6016
| VA | 14000 | 10200 | 9000 | 14000 | 1 | 1 | 1.5 | 0.875 | 0.875 | 1.3125 | 1.3333 | 1.3725 | 2.25 | 0.79167 | 0.9375 | 1.4062
| VB | 9000 | 4800 | 6000 | 8000 | 1.125 | NP | NP | 0.98438 | NP | NP | 1.5 | 1.6875 | NP | 0.89062 | 1.0547 | NP
R-1 | IB | UL | 22800 | UL | 29900 | bar: Number of stories 1 to Number of stories 3
| IIA | 24000 | 15000 | 18000 | 13500 | 1.3333 | 1.3333 | 1.3333 | 1.12 | 1.12 | 1.1667 | 1.7778 | 1.6 | 2 | 1.4074 | 1.3333 | 1.6667
| IIB | 16000 | 9600 | 12000 | 9100 | 1.3333 | 1.3333 | 2.0833 | 1.1667 | 1.1667 | 1.2681 | 1.7778 | 1.6667 | 2 | 1.3919 | 1.3889 | 1.6667
| IIIA | 24000 | 13200 | 18000 | 13500 | 1.3333 | 1.3333 | 1.3333 | 1.1667 | 1.1667 | 1.1667 | 1.7778 | 1.8182 | 2 | 1.4074 | 1.5152 | 1.6667
| IIIB | 16000 | 9600 | 12000 | 9100 | 1.3333 | 1.3333 | 2.0833 | 1.1667 | 1.1667 | 1.2681 | 1.7778 | 1.6667 | 2 | 1.3919 | 1.3889 | 1.6667
| IV | 20500 | 14400 | 18000 | 13500 | 1.1389 | 1.1389 | 1.1389 | 0.99653 | 0.99653 | 0.99653 | 1.5185 | 1.4236 | 1.7083 | 1.2022 | 1.1863 | 1.4236
| VA | 12000 | 10200 | 10500 | 10500 | 1.1429 | 1.1429 | 1.1429 | 0.82353 | 0.82353 | 0.89514 | 1.5238 | 1.1765 | 1.7143 | 0.90476 | 0.98039 | 1.3369
| VB | 7000 | 4800 | 7000 | 6000 | 1 | 1 | NP | 0.875 | 0.875 | NP | 1.3333 | 1.4583 | 2.4306 | 0.92361 | 1.0938 | 1.6572
R-2 | IB | UL | 22800 | UL | 29900 | bar: Number of stories 1 to Number of stories 3
| IIA | 24000 | 15000 | 18000 | 13500 | 1.3333 | 1.3333 | 1.3333 | 1.12 | 1.12 | 1.1667 | 1.7778 | 1.6 | 2 | 1.4074 | 1.3333 | 1.6667
| IIB | 16000 | 9600 | 12000 | 9100 | 1.3333 | 1.3333 | 2.0833 | 1.1667 | 1.1667 | 1.2681 | 1.7778 | 1.6667 | 2 | 1.3919 | 1.3889 | 1.6667
| IIIA | 24000 | 13200 | 18000 | 13500 | 1.3333 | 1.3333 | 1.3333 | 1.1667 | 1.1667 | 1.1667 | 1.7778 | 1.8182 | 2 | 1.4074 | 1.5152 | 1.6667
| IIIB | 16000 | 9600 | 12000 | 9100 | 1.3333 | 1.3333 | 2.0833 | 1.1667 | 1.1667 | 1.2681 | 1.7778 | 1.6667 | 2 | 1.3919 | 1.3889 | 1.6667
| IV | 20500 | 14400 | 18000 | 13500 | 1.1389 | 1.1389 | 1.1389 | 0.99653 | 0.99653 | 0.99653 | 1.5185 | 1.4236 | 1.7083 | 1.2022 | 1.1863 | 1.4236
| VA | 12000 | 10200 | 10500 | 10500 | 1.1429 | 1.1429 | 1.1429 | 0.82353 | 0.82353 | 0.89514 | 1.5238 | 1.1765 | 1.7143 | 0.90476 | 0.98039 | 1.3369
| VB | 7000 | 4800 | 7000 | 6000 | 1 | 1 | NP | 0.875 | 0.875 | NP | 1.3333 | 1.4583 | 2.4306 | 0.92361 | 1.0938 | 1.6572
R-3 | IB | UL | 22800 | UL | UL | bar: Number of stories 1 to Number of stories 3
| IIA | UL | 15000 | 18000 | UL | bar: Number of stories 1 to Number of stories 3
| IIB | UL | 9600 | 12000 | UL | bar: Number of stories 1 to Number of stories 3
| IIIA | UL | 13200 | 18000 | UL | bar: Number of stories 1 to Number of stories 3
| IIIB | UL | 9600 | 12000 | UL | bar: Number of stories 1 to Number of stories 3
| IV | UL | 14400 | 18000 | UL | bar: Number of stories 1 to Number of stories 3
| VA | UL | 10200 | 10500 | UL | bar: Number of stories 1 to Number of stories 3
| VB | UL | 4800 | 7000 | UL | bar: Number of stories 1 to Number of stories 3
S-1 | IB | 48000 | 19950 | 30000 | 39900 | 1.203 | 1.203 | 1.6 | 1.0526 | 1.0526 | 1.4 | 1.604 | 1.8045 | 2.4 | 0.95238 | 1.1278 | 1.6917
| IIA | 26000 | 13125 | 24000 | 18000 | 1.0833 | 1.0833 | 2.1667 | 0.94792 | 0.94792 | 1.5072 | 1.4444 | 1.625 | 1.625 | 1.1435 | 1.3542 | 1.3542
| IIB | 17500 | 8400 | 16000 | 12000 | 1.0938 | 1.0938 | LNP | 0.95703 | 0.95703 | LNP | 1.4583 | 1.6406 | 1.6406 | 1.1545 | 1.3672 | 1.3672
| IIIA | 26000 | 11550 | 24000 | 18000 | 1.0833 | 1.0833 | 2.1667 | 0.94792 | 0.94792 | 1.7128 | 1.4444 | 1.625 | 1.625 | 1.1435 | 1.3542 | 1.3542
| IIIB | 17500 | 8400 | 16000 | 12000 | 1.0938 | 1.0938 | LNP | 0.95703 | 0.95703 | LNP | 1.4583 | 1.6406 | 1.6406 | 1.1545 | 1.3672 | 1.3672
| IV | 25500 | 12600 | 24000 | 18000 | 1.0625 | 1.0625 | 2.125 | 0.92969 | 0.92969 | 1.5399 | 1.4167 | 1.5938 | 1.5938 | 1.1215 | 1.3281 | 1.3281
| VA | 14000 | 8925 | 9000 | 14000 | 1 | 1 | 1.5 | 0.875 | 0.875 | 1.3125 | 1.3333 | 1.5 | 2.25 | 0.79167 | 0.9375 | 1.4062
| VB | 9000 | 4200 | 6000 | 8000 | 1.125 | NP | NP | 0.98438 | NP | NP | 1.5 | 1.6875 | NP | 0.89062 | 1.0547 | NP
S-2 | IB | 79000 | 34200 | 30000 | 59900 | 1.3189 | 1.3189 | 1.9783 | 1.154 | 1.154 | 1.65 | 1.7585 | 1.9783 | 2.9674 | 1.0441 | 1.2364 | 1.8547
| IIA | 39000 | 22500 | 24000 | 27000 | 1.4444 | 1.4444 | 1.625 | 1.2133 | 1.2133 | 1.3188 | 1.9259 | 1.7333 | 2.4375 | 1.1435 | 1.3542 | 1.9697
| IIB | 26000 | 14400 | 16000 | 18000 | 1.4444 | 1.4444 | 1.625 | 1.2639 | 1.2639 | 1.3738 | 1.9259 | 1.8056 | 2.4375 | 1.1435 | 1.3542 | 2.0312
| IIIA | 39000 | 19800 | 24000 | 27000 | 1.4444 | 1.4444 | 1.625 | 1.2639 | 1.2639 | 1.4219 | 1.9259 | 1.9697 | 2.4375 | 1.1435 | 1.3542 | 2.0312
| IIIB | 26000 | 14400 | 16000 | 18000 | 1.4444 | 1.4444 | 1.625 | 1.2639 | 1.2639 | 1.3738 | 1.9259 | 1.8056 | 2.4375 | 1.1435 | 1.3542 | 2.0312
| IV | 38500 | 21600 | 24000 | 27000 | 1.4259 | 1.4259 | 1.6042 | 1.2477 | 1.2477 | 1.3562 | 1.9012 | 1.7824 | 2.4062 | 1.1289 | 1.3368 | 2.0052
| VA | 21000 | 15300 | 9000 | 21000 | 1 | 1 | 1.5 | 0.875 | 0.875 | 1.0443 | 1.3333 | 1.3725 | 2.25 | 0.79167 | 0.9375 | 1.4062
| VB | 13500 | 7200 | 6000 | 12000 | 1.125 | 1.125 | NP | 0.98438 | 0.98438 | NP | 1.5 | 1.6875 | 3.125 | 0.89062 | 1.0547 | 2.1307