ICC CTC BALANCED FIRE PROTECTION

SMOKE AND HEAT VENT STUDY GROUP

2006 IFC REQUIREMENTS

FOR

DRAFT CURTAINSa

2/16/07

Revised 3/6/07

Max.

Use/		    Area		Commodity			Storage

Occupancy		   Limits		     Class			 Height

F-1			>50,000 sf		   any			  	    n/a

undivided area

S-1b			>50,000 sf		   anyc			   	   12 ft.

undivided area

High-Piled	           2,501 – 12,000 sf	   I – IV 			   30 ft.

Combustible

Storaged		501 – 2,500 sf	   High Hazarde		   20 ft.

Footnotes:

a – 	Not required in areas protected by ESFR sprinkler systems except 				to separate such systems from conventional sprinkler systems

b – 	Not required for aircraft repair hangars since smoke and heat vents 				are not required

c – 	Not required for frozen food warehouses storing only Class I/II 				commodities protected with an automatic sprinkler system since 				smoke and heat vents are not required

d – 	Only applicable to non-sprinklered buildings that are non-public 				accessible (Option 2)

e –    	Other than Group H-3 (See Section 2303.6)