ICC Code Technology Committee

Day Care/Adult Care/Assisted Living

Study Group Report - October 19, 2006

The study group took a clean sheet of paper approach to this area of study, without the constraints of the current code language. The parameters identified are noted below:

| CARE FACILITY PARAMETERS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | No. | Age | Duration | Self Evac. Ability | Issues/Needs/Class |
| Infant | 5 or less | <2.5 | Any | No | FP same as single family IRC or R-3 |
|  | 6 to ≤16 | <2.5 | Any | No | Need enhanced level of FP I-2 except: - Exit direct to outside at grade – Group E - Exit direct to outside at grade- R-3 with 13R |
|  | >16 | <2.5 | Any | No | I-2 except: <100 w/ exit direct to outside at grade– Group E |
| Child/Adult | 5 or less | ≥2.5 | Any | No | FP same as single family IRC or R-3 |
|  | 6 to ≤16 | ≥2.5 | Any | No | Need Enhanced level of FP I-2 except: - Exit direct to outside at grade– R-3 w/13R - Exit direct to outside at grade – Group E |
|  | >16 | ≥2.5 | Any | No | I-2 except: <100 w/ exit direct to outside at grade– Group E |
|  | 5 or less | ≥2.5 | Any | Yes | FP same as single family IRC or R-3 |
|  | 6 to ≤16 | ≥2.5 | Any | Yes | No special needs. Lives there: R-3 with 13R Not living there: Based on use, ie care given to employees kids in business – Group B |
|  | >16 | ≥2.5 | Any | Yes | No special needs. Lives there: R-2 with 13 or 13R depending on height Not living there: Based on use, ie care given to employees kids in business – Group B |

Assumptions:

- Terminology- call them “Care facilities”. Not day care, child care, adult care, assisted living

- Number- number of occupants receiving care, not incl. care-givers

- Duration – “any” - hazard not driven by amount of time the care is given or the period during the day or night when the care is given

- Self Evacuation Ability

  - No: Need assistance via personal or mechanical means.

  - Yes: Capable of self evacuation w/o assistance

- Supervision – Current code requirements for supervision are tied to the ability to provide evacuation assistance and/or direction. Criteria for supervision is not needed in the code as the issue is whether or not the occupants cared for are capable of self evacuation

- FP- fire protection includes active systems, passive systems (TOC), egress, etc.