## Sheet1
INTERNATIONAL BUILDING CODE - 2003 |  |  | INTERNATIONAL BUILDING CODE - 2000 |  | UNIFORM BUILDING CODE - 1997 |  | BOCA NATIONAL BUILDING CODE - 1996 |  | STANDARD BUILDING CODE - 1997
SECTION | TITLE | REQUIREMENT | SECTION | REQUIREMENT | SECTION | REQUIREMENT | SECTION | REQUIREMENT | SECTION | REQUIREMENT
302.1.1.1 | Separation | Separation. Where Table 302.1.1 requires a fire-resistance-rated separation, the incidental use area shall be separated from the remainder of the building with a fire barrier. Where Table 302.1.1 permits an automatic fire-extinguishing system without a fire barrier, the incidental use area shall be separated by construction capable of resisting the passage of smoke. The partitions shall extend from the floor to the underside of the fire-resistance-rated floor/ceiling assembly or fire-resistance- rated roof/ceiling assembly or to the underside of the floor or roof deck above. Doors shall be self-closing or automatic-closing upon | 302.1.1.1 | Automatic sprinklers. Evaluate the ability to suppress a fire based on the installation of an automatic sprinkler system in accordance with Section 903.3.1.1. “Required sprinklers” shall be based on the requirements of this code. Under the categories and occupancies in Table 3410.6.17, determine the appropriate value and enter that value into Table 3410.7 under Safety Parameter 3410.6.17, Automatic Sprinklers, for fire safety, means of egress divided by 2 and general safety. | 302.2 | Forms of Occupancy Separations. Occupancy separations shall be vertical or horizontal or both, or, when necessary, of such other form as may be required to afford a complete separation between the various occupancy divisions in the building. Where the occupancy separation is horizontal, structural members supporting the separation shall be protected by equivalent fire-resistive construction. | 302.1.1.1 | Separation. Where Table 3021.1.1 required a fire resistance rated separation, the specific occupancy area shall be separated from the remainder of the building with fire separation assemblies (See Section 709.0). Where Table 302.1.1 required smoke partitions, the smoke partitions shall be constructed of materials consistent with the type of construction and shall be capable of resisting the passage of smoke. The smoke partitions shall extend from the floor to the underside of the fire resistance rated floor/ceiling assembly or to the underside of the floor or roof deck above. All doors shall extend from the floor | 303.2 704.2.2.3 | 303.2 Height and area. A mixed occupancy building shall be governed by the height and area limitations applying to the principal intended use. However each portion of the building shall conform to all other requirements of this code for the occupancy contained therein. Accessory occupancies shall not exceed the area limitation not be located at a height greater than that permitted for such occupancy group in the type of construction being used. 704.2.2.3 Group R Residential. Nonfire rated partitions may be constructed within a small residential care/assisted living
|  | detection of smoke. Doors shall not have air transfer openings and shall not be undercut in excess of the clearance permitted in accordance with NFPA 80. | [5 empty] | or roof deck above. All doors shall be self-closing or automatic-closing upon detection of smoke. Doors shall not have air transfer openings and shall not be undercut in excess of the clearance permitted in accordance with NFPA 80 listed in Chapter 35. |  | facilities (Group R4 Small Facility), one and two family dwellings and within individual dwelling units unless required by Table 600. The tenant separation in a two family dwelling shall comply with 704.3. Exception: Shaft enclosures in Group R4 occupancies shall be enclosed and protected in accordance with the requirements of Table 705.1.2.
Table 302.1.1.a | Incidental Use Areas | One-hour separation or automatic extinguishing required for furnace, boiler, refrigerant machinery, and laboratory (not classified as Group H, in Group E, or 1-2) rooms. | Table 302.1.1.a |  | 302.5 310.2.2 | Heating Equipment Room Occupancy Separation. In Groups A; B; E;F;I;M;R, Division 1; and S Occupancies, rooms containing a boiler, central heating plant or hot-water supply boiler shall be separated from the rest of the building by not less than a one-hour occupancy separation. Exceptions: 1. In Groups A, B, E, F, M and S Occupancies, boilers, central heating plants or hot-water supply boilers where the largest piece of fuel equipment does not exceed 400,000Btu per hour (117.2kW) input. 2. In Group R, Division 1 Occupancies, a separation need not be provided for such rooms with | Table 302.1.1 | Similar; also applies to waste and soiled linen chute access rooms, kitchen, handicraft, employee lockers, and retail/gift shops. | 704.1.3.3.1 704.1.3.3.4 | 704.1.3.3.1 Every central heating boiler as defined in the Standard Mechanical Code, installed in any building other than a one or two family dwelling or Group F, shall be separated from the rest of the building by not less than 1-hour fire resistant construction. 704.1.3.3.4 Refrigerant system machinery rooms. Where required by the Standard Mechanical Code due to refrigerant type, amount, system classification and occupancy, a Level 2 machinery room shall be of noncombustible construction. A minimum of 1-hour construction shall separate the machinery room from
[6 empty] | equipment serving only one dwelling unit. In Group E Occupancies, when the opening for a heater or equipment room is protected by a pair of fire doors, the inactive leaf shall be normally secured in the closed position and shall be openable only by the use of a tool. An astragal shall be provided and the active leaf shall be self-closing. In Group H Occupancies, rooms containing a boiler, central heating plant or hot-water supply boiler shall be separated from the rest of the building but not less than a two-hour occupancy separation. In Divisions 1 and 2, there shall be no openings in such |  |  |  | other occupied spaces. A minimum of 3/4 hour C-labeled doors shall be used when separating from other occupancies.
occupancy separation except for necessary ducts and piping. For opening in exterior walls of equipment rooms in Group A, E or I Occupancies, see Sections 303.8, 305.8 and 308.8. 310.2.2 Special Provisions. Walls and floors separating dwelling units in the same building, or guest rooms in Group R, Division 1 hotel occupancies, shall not be of less than one-hour fire-resistive construction. Group R, Division 1 Occupancies more than two stories in height or having more than 3,000 square feet (279m2) of floor area above the first story shall not be of less than one-hour
fire-resistive construction throughout, except as provided in Section 601.5.2.2. Storage or laundry rooms that are within Group R, Division 1 Occupancies that are used in common by tenants shall be separated from the rest of the building by not less than one-hour fire-resistive occupancy separation. For Group R, Division 1 Occupancies with a Group S, Division 3 parking garage in the basement or first story, see Section 311.2.2. For attic space partitions and draft stops, see Section 708.
Table 302.1.1.d | Incidental Use Areas | Two-hour separation or one-hour and automatic extinguishing system required for paint shops (not classified Group H, located in other than Group F). | Table 302.1.1.d | Same | 304.8 305.8 306.8 308.8 | 304.8 Special Hazards. Chimneys and heating apparatus shall conform to the requirements of Chapter 31 of this code and the Mechanical Code. Storage and use of flammable and combustible liquids shall be in accordance with the Fire Code. Devices generating a glow, spark, or flame capable of igniting flammable vapors shall be installed such that sources of ignition are at least 18 inches (457mm) above the floor of any room in which Class I flammable liquids or flammable gases are used or stored. Stationary lead-acid battery systems used for facility standby, emergency power or uninterrupted power supplies shall be | Table 302.1.1 | Similar; also applies to maintenance and work shops. | 704.1.3.3.2 | A central heating boiler installed in a Group A or H occupancy shall be separated from the rest of the building by construction having fire resistance rating of not less than 2 hours.
installed and maintained in accordance with the Fire Code. 305.8 Special Hazards. Chimneys and heating apparatus shall conform to the requirements of Chapter 31 of this code and the Mechanical Code. Motion picture machine rooms shall conform to the requirements of Chapter 4. All exterior openings in a boiler room or rooms containing central heating equipment, if located below openings in another story or if less than 10 feet (3048mm) from other doors or windows of the same building, shall be protected by a fire assembly having
three-fourths-hour fire-protection rating, Such fire assemblies shall be fixed, automatic closing or self-closing. Class I, II, III-A liquids shall not be places, stored, or used in Group E Occupancies, except in approved quantities as necessary in laboratories and classrooms and for operation and maintenance as set forth in the Fire Code. 306.8 Special Hazards. For special hazards of Group F Occupancies, see Section 304.8. Storage and use of flammable and combustible liquids shall be in accordance with the Fire Code. Buildings erected or converted to house high-piled combustible stock
or aerosols shall comply with the Fire Code. Equipment, machinery or appliances that generate finely divided combustible waste or that use finely divided combustible material shall be equipped with an approved method of collection and removal. 308.8 Special Hazards. Chimneys and heating apparatus shall conform to the requirements of Chapter 31 of this code and the Mechanical Code. Motion picture projection rooms shall conform to the requirements of Section 406. Specific use areas shall be separated from Group I, Division 1.1 Occupancies used
for hospitals and nursing homes in accordance with Table 3-C. Doors shall be maintained self-closing or shall be automatic closing by actuation of a smoke detector. Storage and handling of flammable and combustible liquids shall be in accordance with the Fire Code. All exterior openings in a boiler room or room containing central heating equipment if located below openings in another story, or if less than 10 feet(3048mm) from the other doors or windows of the same building, shall be protected by a fire assembly having a three-fourths-hour fire-protection rating.
302.3.2 | Separated Uses | 302.3.2 Separated uses. Each portion of the building shall be individually classified as to use and shall be completely separated from adjacent areas by fire barrier walls or horizontal assemblies or both having a fire-resistance rating determined in accordance with Table 302.3.2 for uses being separated. Each fire area shall comply with this code based on the use of that space. Each fire area shall comply with the height limitations based on the use of that space and the type of construction classification. In each story, the building area shall be such that the sum of the ratios of the floor area of each use divided by the allowable area for | 302.3.3 | Automatic sprinklers. Evaluate the ability to suppress a fire based on the installation of an automatic sprinkler system in accordance with Section 903.3.1.1. “Required sprinklers” shall be based on the requirements of this code. Under the categories and occupancies in Table 3410.6.17, determine the appropriate value and enter that value into Table 3410.7 under Safety Parameter 3410.6.17, Automatic Sprinklers, for fire safety, means of egress divided by 2 and general safety. | 302.1 302.4 | 302.1 General. When a building is used for more than one occupancy purpose, each part of the building comprising a distinct "occupancy," as described in Section 301, shall be separated from any other occupancy as specified in Section 302.4. Exceptions: 1. When an approved spray booth constructed in accordance with the Fire Code is installed, such booth need not be separated from Group B, F, H, M or S Occupancies. 2. The following occupancies need not be separated from the uses to which they are accessory: 2.1. Assembly rooms having a floor area of not over 750 sq ft (69.7m2). 2.2. Administrative and | 313.1.2 | Separated use groups. Each portion of the building shall be individually classified in a use group and shall be completely separated from adjacent fire areas by fire separation assemblies (see Section 709.0) and floor/ceiling assemblies (see Section 713.0) having a fire resistance rating determined in accordance with Table 313.1.2, for the use groups being separated . Each fire area shall comply with the code based on the use group of that space. Each fire area shall comply with the height limitations of Section 503.0 based on the use of that space and the type of construction classification. In each | 303.2 | Height and area. A mixed occupancy building shall be governed by the height and area limitations applying to the principal intended use. However each portion of the building shall conform to all other requirements of this code for the occupancy contained therein. Accessory occupancies shall not exceed the area limitation not be located at a height greater than that permitted for such occupancy group in the type of construction being used.
|  | each use shall not exceed one. |  |  |  | clerical offices and similar rooms that do not exceed 25% of the floor area of the major use when not related to Group H, Division 2 and Group H, Division 3 Occupancies. 2.3 Gift shops, administrative offices and similar rooms in Group R, Division 1 Occupancies not exceeding 10% of the floor area of the major use. 2.4 The kitchen serving the dining area of which it is a part. 2.5 Customer waiting rooms not exceeding 450 sq ft (41.8m2) when not related to Group H Occupancies and when such waiting rooms have an exit directly to the exterior. 3. An occupancy separation need not be provided between a Group R, Division 3 Occupancy and a carport having no |  | story, the building area shall be such that the sum of ratios of the floor area of each use group divided by the allowable area from Section 503.0 for each use group shall not exceed one. Exception: Where the building is equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1, the required fire resistance rating of fire separation assemblies separating areas of other than Use Group H, shall be reduced from those indicated in Table 313.1.2 by 1-hour but not less than 1-hour and to not less than that required by Table 602 for floor construction.
enclosed uses above, provided the carport is entirely open on two or more sides. 4. A Group S, Division 3 Occupancy used exclusively for the parking or storage of private or pleasure-type motor vehicles need not be separated from a Group S, Division 4 Occupancy open parking garage as defined in Section 311.1 302.4 Fire Ratings for Occupancy Separations. Occupancy separations shall be provided between the various groups and divisions of occupancies as set forth in Table 3-B. For required separation of specific uses in Group 1, Division 1 hospitals and nursing homes, see Table 3-C. See also Section 504.6.1.
Exceptions: 1. A three-hour occupancy separation may be used between a Group A, Division 1 and a Group S, Division 3 Occupancy used exclusively for the parking or storage of private or pleasure-type motor vehicles provided no repair or fueling is done. A two-hour occupancy separation may be used between Group A, Division 2, 2.1, 3 or 4 E or I Occupancy and a Group S, Division 3 Occupancy used exclusively for the parking or storage of private or pleasure-type vehicles provided no repair or fueling is done. 2. Unless required by Section 311.2.2, the three-hour occupancy separation between a Group R, Division 1 Occupancy and a Group S,
Division 3 Occupancy used only for the parking or storage of private or pleasure-type motor vehicles with no repair or fueling may be reduced to two hours. Such occupancy separation may be further reduced to one hour where the area off such Group S, Division 3 Occupancy does not exceed 3,000 sq ft(279m2). 3. In the one-hour occupancy separation between Group R, Division 3 and Group U Occupancies, the separation may be limited to the installation of materials approved for one-hour fire-resistive construction on the garage side and a self-closing, tight-fitting door having a fire-protection rating of not less than 20
minutes when tested in accordance with Part II of UBC Standard 7-2, which is part of the this code, is permitted in lieu of a one-hour fire assembly. Fire dampers need not be installed in air ducts passing through the wall, floor or ceiling separating a Group R, Division 3 Occupancy from a Group U Occupancy, provided such ducts within the Group U Occupancy are constructed of steel having a thickness not less than 0.019 inch (0.48mm) (No.26 galvanized sheet gage) and have no openings into the Group U Occupancy. 4. Group H, Division 2 and Group H, Division 3 Occupancies need not be separated from Group H, Division 7
Occupancies when such occupancies also comply with the requirements for a Group H, Division 7 Occupancy.
403.2 | Automatic Sprinkler System | 403.2 Automatic sprinkler system. Buildings and structures shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 and a secondary water supply where required by Section 903.3.5.2. Exception: An automatic sprinkler system shall not be required in spaces or areas of: 1. Open parking garages in accordance with Section 406.3. 2. Telecommunications equipment buildings used exclusively for telecommunications equipment, associated electrical power distribution equipment, batteries and standby engines, provided that those spaces or areas are equipped | 403.2 | Automatic Sprinkler System. Buildings and structures shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 and a secondary water supply where required by Section 903.3.5.2. Exception: An automatic sprinkler system shall not be required in spaces or areas of 1. Open parking garages in accordance with Section 406.3. 2. Telecommunications equipment buildings used exclusively for telecommunications equipment, associated electrical power distribution equipment, batteries and standby engines, provided that those spaces or areas are equipped throughout with an | 403.1 403.2 | 403.1 Scope. This section applies to all Group B office buildings and Group R, Division 1 Occupancies, each having floors used for human occupancy located more than 75 ft (22860mm) above the lowest level of fire department vehicle access. Such buildings shall be of Type I or II-F.R. construction and shall be provided with an approved automatic sprinkler system in accordance with Section 403.2. 403.2 Automatic Sprinkler System. 403.2.1 System design. The automatic sprinkler system shall be provided throughout the building as specified by UBC Standard 9-1, and shall be designed in | 403.2 | Sprinkler system. All buildings and structures shall be equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1. Exception: An automatic sprinkler system shall not be required in spaces or areas of: 1. Open parking structures complying with Section 406.0. 2. Telecommunications equipment buildings used exclusively for telecommunications equipment, associated electrical power distribution equipment, batteries and standby engines, provided that those spaces or areas are equipped throughout with an automatic fire detection system in accordance with | 412.1.1 412.10 | 412.1.1 These requirements shall apply to all Group B and Group R buildings having floor surfaces used for human occupancy located more than 75ft (22.9m) above the lowest level of fire department vehicle access. Group B buildings shall be provided with either an approved automatic sprinkler system in accordance with 412.10 or areas of refuge (compartmentation) in accordance with 412.9. Group R buildings shall be provided with an approved automatic sprinkler system in accordance with 412.10. Group B buildings more than 12 stories or 150ft (45.7m) high shall be provided with an approved automatic sprinkler system
|  | throughout with an automatic fire detection system in accordance with Section 907.2 and are separated from the remainder of the building with fire barriers consisting of 1-hour fire-resistance- rated walls and 2-hour fire-resistance-rated floor/ceiling assemblies. |  | automatic fire detection system in accordance with Section 907.2 and are separated from the remainder of the building with fire barriers consisting of 1-hour fire-resistance-rated walls and 2-hour fire-resistance-rated floor/ceiling assemblies. |  | accordance with that standard and the following: 1. Shutoff valves and a water-flow device shall be provided for each floor. The sprinkler riser may be combined with the standpipe riser. 2. In Seismic Zones 2, 3 and 4, in addition to the main water supply, a secondary on-site supply of water equal to the hydraulically calculated sprinkler design demand plus 100 gallons per minute (378.5L/m) additional for the total standpipe system shall be provided. This supply shall be automatically available if the principal supply fails and shall have a duration of 30 minutes. 403.2.2 Modifications. The following |  | Section 919.0 and are separated from the remainder of the building with fore separation assemblies consisting of 1-hour fire resistance rated walls and 2-hour fire resistance rated floor/ceiling assemblies. |  | in accordance with 412.10. 412.10 Automatic sprinklers alternate. 412.10.1 An approved complete automatic sprinkler system shall be provided throughout the building. The sprinkler system shall be designed using the parameters set forth in NFPA 13 and 412.10.2 through 412.10.4. 412.10.2 Shutoff valves and water flow devices shall be provided at the riser connection ton each floor. The actuation of a water flow device shall activate the voice alarm system. The valves shall be supervised in accordance with 903.8. The sprinkler riser may be combined with the
[6 empty] | modifications of code requirements are permitted: 1. In buildings of Type I construction, the fire-resistive time periods set forth in Table 6-A may be reduced by one hour for interior-bearing walls, exterior-bearing and nonbearing walls, roofs and the beams supporting roofs, provided they do not frame into columns. In buildings of Type II-F.R. construction, the fire-resistive time period set forth in Table 6-A may be reduced by one hour for interior-bearing walls, exterior bearing and nonbearing walls, but no reduction is allowed for roofs. The fire-resistive time period reduction as specified herein shall not apply to |  |  |  | fire department standpipe riser. 412.10.3 In addition to the main water supply, for buildings located where the effective peak velocity related acceleration, Av, in accordance with 1607.1, is equal to or greater than 0.20, a secondary on-site supply of water equal to the hydraulically calculated sprinkler demand plus 100gpm (6.31L/s) for the standpipe system shall be provided. The supply shall have a duration of 30 minutes but not exceed 10000 gallons (37.9m3). 412.10.4 Automatic fire sprinklers may be omitted in the following rooms or areas when such rooms or areas are protected with an
[6 empty] | exterior-bearing and nonbearing walls whose fire resistive rating is less than four hours. Shafts other than stairway enclosures and elevator shafts may be reduced to one hour when sprinklers are installed within the shafts at alternate floors. Except for corridors in Group B offices and Group R, Division 1 Occupancies, and partitions separating dwelling units or guest rooms, all interior-bearing partitions required to be 1-hour fire-resistive construction by Table 6-A may be of noncombustible construction without a fire resistive time period. 3. Fire dampers, other than those needed to |  |  |  | approved automatic fire detection system which will respond to visible or invisible particles of combustion: 1. Generator and transformer rooms. 2. Any room where the application of water, or flame and water, may constitute a serious life or fire hazard. 3. Spaces or areas in telecommunications buildings used exclusively for telecommunications equipment, associated electrical power distribution equipment, batteries and standby engines, provided those spaces or areas are equipped throughout with an automatic fire alarm system and are separated from the remainder of the building by a wall with a
[6 empty] | protect floor/ceiling assemblies to maintain the fire resistance of the assembly, are not required. 4. Emergency windows required by Section 310.4 are not required. |  |  |  | fire resistance rating of not less than 2 hours. 4. When approved by the building official, any other area or room where sprinklers are considered undesirable because of the nature of the contents.
403.3 | Reductions in Fire-Resistance Rating | Reduction in fire-resistance rating. The fire-resistance-rating reductions listed in Sections 403.3.1 and 403.3.2 shall be allowed in buildings that have sprinkler control valves equipped with supervisory initiating devices and water-flow initiating devices for each floor. | 403.3 | Reduction in fire-resistance rating. The fire-resistance-rating reduction listed in Sections 403.3.1 and 403.3.2 shall be allowed in buildings that have sprinkler control valves equipped with supervisory initiating devices and water-flow initiating devices for each floor. | 403.2.2 | Modifications. The following modifications of code requirements are permitted: 1. In buildings of Type I construction, the fire-resistive time periods set forth in Table 6-A may be reduced by one hour for interior-bearing walls, exterior-bearing and nonbearing walls, roofs and the beams supporting roofs, provided they do not frame into columns. In buildings of Type II-F.R. construction, the fire-resistive time period set forth in Table 6-A may be reduced by one hour for interior-bearing walls, exterior-bearing and nonbearing walls, but no reduction is allowed for roofs. The fire-resistive time period reduction as | 403.3 | Alternative sprinkler system. Alternatively, to qualify for the fire resistance rating reduction for certain building elements listed in Section 403.3.3, the automatic sprinkler system shall comply with Section 906.2.1 and the optional fire protection features listed in Section 403.3.1 and 403.3.2. | 412.11 | Alternates permitted. When a complete approved automatic sprinkler system complying with 412.10 is provided, the following modifications of code requirements are acceptable: 1. Fixed tempered glass may be used in lieu of openable panels for smoke control purposes. 2. Manual fire alarm boxes are not required. 3. Spandrel walls, eyebrows and conpartmentation are not required; however, the fire resistance of the floors and juncture of exterior walls with each floor must be maintained. 4. Fire dampers, other than those needed to maintain the fire resistance of the floor/ceiling
[6 empty] | specified herein shall not apply to exterior-bearing and non-bearing walls whose fire-resistive rating is less than 4 hours. Shaft other than stairway enclosures and elevator shafts may be reduced to one hour when sprinklers are installed within the shafts at alternate floors. 2. Except for corridors in Group B offices and Group R, Division 1 Occupancies, and partitions separating dwelling units or guest rooms, all interior-nonbearing partitions required to be one-hour fire-resistive construction by Table 6-A may be of noncombustible construction with a fire-resistive time period. 3. Fire dampers, other than those needed to |  |  |  | assemblies, are not required except for those which may be necessary to bypass smoke to the outside, to convert from recirculated air to 100% outside air, and that which may be required to protect the fresh air supply intake against smoke which may be outside the building. 5. Smokeproof enclosures may be omitted provided all required stairways are equipped with a dampered relief opening or an exhaust fan at the top and supplied mechanically with sufficient air to discharge a minimum of 2500cfm (1.18m3/s) through the relief opening while maintaining a minimum positive pressure of 0.05inch of water column
[6 empty] | protect floor-ceiling assemblies to maintain the resistance of the assembly, are not required. 4. Emergency windows required by Section 310.4 are not required. |  |  |  | (12.4 Pa) relative to atmospheric pressure in addition to the maximum anticipated stack pressure relative to other parts of the building measured with all the enclosure doors closed. The combined positive pressure shall not exceed 0.35 inch of water column (87.1Pa). Activation of the mechanical equipment shall be in accordance with 1005.6.9.10. The stair pressurization system shall comply with 1005.6.9.1 and 1005.6.9.2. 6. The required fire resistance rating of vertical shafts other than stairway enclosures and elevator hoistways in buildings no higher than 250ft (76.2m) may be reduced to 1 hour when sprinklers are installed
within the shaft at alternate floors. 7. In Type I construction the fire resistance of partitions, columns, trusses, girders, beams and floors may be reduced by 1 hour.
404.2 | Use | Use. The floor of the atrium shall not be used for other than low fire hazard uses and only approved materials and decorations in accordance with the International Fire Code shall be used in the atrium space. Exception: The atrium floor area is permitted to be used for any approved use where the individual space is provided with an automatic sprinkler system in accordance with Section 903.3.1.1. | 404.2 | Use. The floor of the atrium shall not be used for other than low hazard uses and only approved materials and decorations in accordance with the IFC shall be used in the atrium space. Exception: The atrium floor area is permitted to be used for any approved use where the individual space in provided with an automatic sprinkler system in accordance with Section 903.3.1.1. | "402.10" | Combustible Furnishings in Atria. The quantity of combustible furnishings in atria shall not exceed that specified in the Fire Code. | 404.3 | Atrium occupancy. The floor of the atrium shall not be occupied for other than low fire-hazard occupancies and only approved materials and decorations shall be located in the atrium space. Exception: The occupancy of the atrium floor area for any approved purpose shall not be restricted where the hazard is protected with an automatic sprinkler system installed in accordance with Section 906.2.1. | 404.2 | Automotive service station. 404.2.1 An automotive service station of Group B occupancy is a place of retail business at which outdoor automotive refueling is carried on using fixed dispensing equipment connected to storage tanks by a closed system of piping and/or at which goods and services generally required in the operation and maintenance or motor vehicles and fulfilling motorist needs may also be available. The building consists of a sales office where automotive accessories and packaged automotive supplies may be kept or displayed. it may also include one or more service bays in
which vehicle washing, lubrication and minor replacement, adjustment and repair services are rendered. An automobile service station building shall not have a basement, but may have open pits if such pits are continually ventilated. it may be of any construction type. 404.2.2 Canopies and their supports over pumps shall be of noncombustible materials, wood of Type III sizes, or of construction providing 1-hour resistance. Combustible materials used in or on a canopy shall be: 1. Shielded from the pumps by a noncombustible element of the canopy, or wood of Type III sizes, or 2. Approved plastics covered by an aluminum facing
having a minimum thickness of 0.020 inch (0.51 mm) or corrosion resistant steel having a minimum base metal thickness of 0.016inch (0.41mm). the approved plastic shall have a flamespread rating of 25 or less when tested in the form intended for use in accordance with ASTM E 84. 404.2.3 Pumps or other dispensing devices shall be located a minimum of 10ft (3048mm) from a property line and from any building of Type IV construction. Pumps shall be located so the nozzle, with hose fully extended, shall not reach within 5ft (1524mm) of any building opening. 404.2.4. Pumps installed above grade
shall be counted on a concrete foundation and protected against vehicle damage by mounting on a concrete island or other approved collision protection. Subsurface pumps shall be installed in accordance with approved standards. 404.2.5 Storage and handling of flammable and combustible liquids shall be in accordance with the Standard Fire Prevention Code. 404.2.6 The pump motor shall be activated by a switch that cannot be energized until after the hose nozzle has been removed from its boot. The motor shall stop operating when the switch is de-energized upon replacement of the
hose nozzle in its boot. 404.2.7 A clearly labeled, manually operated pump master switch shall be provided in an approved location, readily accessible to the station attendant.
404.3 | Automatic Sprinkler Protection | 404.3 Automatic sprinkler protection. An approved automatic sprinkler system shall be installed throughout the entire building. Exceptions: 1. That area of a building adjacent to or above the atrium need not be sprinklered provided that portion of the building is separated from the atrium portion by a 2-hour fire barrier wall or horizontal assembly or both. 2. Where the ceiling of the atrium is more than 55 feet (16 764 mm) above the floor, sprinkler protection at the ceiling of the atrium is not required. | 404.3 | Automatic sprinkler protection. An approved automatic sprinkler system shall be installed throughout the entire building. Exceptions: 1. The area of a building adjacent to or above the atrium need not be sprinklered provided that portion of the building is separated from the atrium portion by a 2-hour fire barrier wall or horizontal assembly or both. 2. Where the ceiling of the atrium is more than 55ft (16764mm) above the floor, sprinkler protection at the ceiling of the atrium is not required. | 402.1 | General. Buildings, of other than Group H Occupancy, with automatic sprinkler protection throughout may have atria complying with the provisions of this section. Such atria shall have a minimum opening area and dimension as set forth in Table 4-A. | 404.2 | Automatic sprinkler system. The atrium and stories and floor areas connected to the atrium shall be equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1. The automatic sprinkler system shall be supervised in accordance with Section 924.1, method 1. Exception: an automatic sprinkler system shall not be required in areas separated from the atrium by fire separation assemblies in accordance with Section 709.0. | 414.3 | Automatic sprinkler protection. An approved automatic sprinkler system shall be installed throughout the entire building. Exceptions: 1. That area of a building adjacent to or above the atrium need not be sprinklered provided that portion of the building is separated from the atrium portion by fire separations corresponding to Table 600 but in no case less than a 2-hour fire resistant separation. 2. When the ceiling of the atrium is more than 55ft (16.8m) above the floor, sprinkler protection at the ceiling of the atrium may be omitted when approved by the building official.
404.5 | Enclosure | Enclosure of atriums. Atrium spaces shall be separated from adjacent spaces by a 1-hour fire barrier wall. Exceptions: 1. A glass wall forming a smoke partition where automatic sprinklers are spaced 6 feet (1829 mm) or less along both sides of the separation wall, or on the room side only if there is not a walkway on the atrium side, and between 4 inches and 12 inches (102mm and 305 mm) away from the glass and so designed that the entire surface of the glass is wet upon activation of the sprinkler system. The glass shall be installed in a gasketed frame so that the framing system deflects without breaking (loading) the glass | 404.5 | Enclosure of atriums. Atrium spaces shall be separated from adjacent spaces by a 1-hour fire barrier wall. Exceptions: 1. A glass wall forming a smoke partition where automatic sprinklers are spaced 6 ft (1829mm) or less along both sides of the separation wall, or on the room side only if there is not a walkway on the atrium side, and between 4 and 12 inches (102 and 305mm) away from the glass and so designed that the entire surface of the glass is wet upon activation of the sprinkler system. The glass shall be installed either: 1.1. In a gasketed frame so installed that the framing system deflects without breaking (loading) the glass before the | 402.3 | Enclosure of Atria. Atria shall be separated from adjacent spaces by not less than one-hour fire-resistive construction. Exceptions: 1. The separation between atria and tenant spaces that are not guest rooms, congregate residences or dwelling units may be omitted at three floor levels. 2. Open exit-access balconies are permitted within the atrium. Openings in the atrium enclosure other than fixed glazing shall be protected by smoke- and draft- control assemblies conforming to Section 1004.3.4.3.2. Exception: Other tightfitting doors that are maintained automatic closing, in accordance with | 404.5 | Enclosure of atriums. Atrium spaces shall be separated from adjacent spaces by a 1-hour fire partition as required for corridors. Exceptions: 1. In residential occupancies, protected openings are not required where the floor area of each guestroom or dwelling unit does not exceed 1000sq ft (93m2) and each room or unit has an approved means of egress not entering the atrium. 2. Adjacent spaces shall be separated from the atrium by fire windows or wall systems consisting of tempered, wired, laminated glass or nonfireresistance rated glass-block wall subject to the following criteria: 2.1. The glass shall be | 414.15 | Enclosure of atriums. Atrium spaces shall be separated from adjacent spaces by a 1-hour fire separation wall. A glass wall forming a smoke partition any be used in lieu of the required fire separation wall where automatic sprinklers are spaced 6 ft (1829mm) or less along both sides of the separation wall, or on the room side only if there is not a walkway on the atrium side, and not more than 1 ft (305mm) away from the glass and so designed that the entire surface of the glass is wet upon activation of the sprinkler system. The glass shall be installed either: 1. In a gasketed frame so installed that the framing system
|  | before the sprinkler system operates. 2. A glass-block wall assembly in accordance with Section 2110 and having a 3/4-hour fire protection rating. 3. The adjacent spaces of any three floors of the atrium shall not be required to be separated from the atrium where such spaces are included in computing the atrium volume for the design of the smoke control system. |  | sprinkler system operates, or 1.2. As a glass block wall assembly in accordance with Section 2110 and the listing for a 3/4-hour fire-resistance rating. 2. The adjacent spacing of any three floors of the atrium shall not be required to be separated from the atrium where such spaces are included in computing the atrium volume for the design of the smoke control system. |  | Section 713.2, by actuation of a smoke detector, or self-closing may be used when protected as required for glazed openings in Exception 2. Fixed glazed openings in the atrium enclosure shall be equipped with fire windows having a fire-resistive rating of not less than three-fourths hour, and the total area of such openings shall not exceed 25% of the area of the common wall between the atrium and the room into which the opening is provided. Exceptions: 1. In Group R, Division 1 Occupancies, openings may be unprotected when the floor area of each guest room , congregate residence or dwelling unit does |  | protected by a specially designed automatic sprinkler system. The sprinkler system shall completely wet the entire surface of the glass well when actuated. Where there are walking surfaces on both sides of the glass, both sides of the glass shall be so protected; 2.2 The tempered, wired (not meeting Section 719.1) or laminated glass shall be in a gasketed frame and installed in such a manner that the framing system will deflect without breaking (loading) the glass before the sprinkler system operates; 2.3. Obstructions, such as curtain rods, curtains, drapes, or similar materials shall not be installed between the |  | may deflect without breaking (loading) the glass before the sprinkler system operates, or 2. As a glass block wall assembly in accordance with 2112 and the listing for a 3/4 hour fire resistance rating. Exception: The adjacent spaces of any three floors of the atrium shall not be required to be separated from the atrium; however, such spaces shall be included when computing the volume of the atrium.
[6 empty] | not exceed 1,000 sq ft (92.9m2) and each room or unit has an approved means of egress not entering the atrium. 2. Guest rooms, dwelling units, congregate residence and tenant spaces may be separated from the atrium by approved fixed wired glass set in steel frames. In lieu thereof, tempered or laminated glass or listed glass block may be used, subject to the following: 2.1 The glass shall be protected by a sprinkler system equipped with listed quick response sprinklers. The sprinkler system shall completely wet the entire surface of the glass wall when actuated. Where there are walking surfaces on both sides of the |  | automatic sprinklers and the glass; and 2.4. Doors in such walls shall of glass or other approved material that will resist the passage of smoke. Glass utilized in doors shall be installed and protected in accordance with Item 2.1 and 2.3 of this exception. If installed in a frame, glass utilized in doors shall be protected in accordance with Item 2.2 of this exception. Doors shall be self-closing or automatic-closing upon smoke-detection and be positive latching. 3. The adjacent spaces of any three floors of the atrium shall not be required to be separated from the atrium; however, these spaces shall be included in the atrium
[6 empty] | glass, both sides of the glass shall be so protected. 2.2 The tempered or laminated glass shall be in a gasketed frame so installed that the glazing system may deflect without breaking (loading) the glass before the sprinkler system operates. 2.3 The glass block wall assembly shall be installed in accordance with its listing for a three-fourths-hour fire-resistive rating and Section 2110. 2.4 Obstructions such a curtain rods, drapery traverse rods, curtains, drapes or similar materials shall not be installed between the sprinkler and the glass. |  | volume for the design of the smoke control system (see Section 922.0). 4. The area limitations specified for fire resistance rated glass block and approved fire windows shall be unlimited where protected by an automatic sprinkler system that shall completely wet the entire surface of the glass when actuated. Where there are walking surfaces on both sides of the glass, both sides of the glass shall be protected.
405.1 | General | General. The provisions of this section apply to building spaces having a floor level used for human occupancy more than 30 feet (9144 mm) below the lowest level of exit discharge. Exceptions: 1. One- and two-family dwellings, sprinklered in accordance with Section 903.3.1.3. 2. Parking garages with automatic fire suppression systems in compliance with Section 405.3. 3. Fixed guideway transit systems. 4. Grandstands, bleachers, stadiums, arenas and similar facilities. 5. Where the lowest story is the only story that would qualify the building as an underground building and has an area not exceeding 1,500 square | 405.1 | General. The provisions of this section apply to building spaces having a floor level used for human occupancy more than 30ft (9144mm) below the lowest level of exit discharge. Exceptions: 1. One- and two family dwellings, sprinklered in accordance with Section 903.3.1.3. 2. Parking garages with automatic fire suppression systems in compliance with Section 405.3. 3. Fixed guideway transit systems. 4. Grandstands, bleachers, stadiums, arenas and similar facilities. 5. Where the lowest story is the only story that would qualify the building as an underground building and has an area not exceeding 1500sq ft |  | No related section. | 405.1 | Applicability. The provisions of this section apply to all structures having a floor level used for human occupancy more than 30ft (9144mm) below, or more than one story below, the lowest level of exit discharge serving that floor level. Exception: The provisions of this section shall not apply to the following structures: 1. Occupancies in Use Group R-3 equipped throughout with an automatic sprinkler system in accordance with Section 906.0. 2. Public garages equipped with an automatic sprinkler system in accordance with Section 906.0. 3. Fixed guideway transit systems. 4. Occupancies in Group | 415.1 | General. The provisions of this section apply to all building spaces having a floor level used for human occupancy more than 30ft (9144mm) or more than one story below the lowest level of exit discharge. Exceptions: 1. One- and two-family dwellings, sprinklered in accordance with NFPA 13D. 2. Parking garages with automatic fire suppression systems in compliance with 415.3. 3. Fixed guideway transit systems. 4. Grandstands. 5. When the lowest story is the only story which would qualify the building as an underground building and has an area not exceeding 1500 sq ft (139.4m2) and has an
|  | feet (139 m2) and has an occupant load less than 10. |  | (139m2) and has an occupant load not less than 10. |  |  |  | A-5. 5. Structures wherein the lowest story is the only story that qualifies the structure as an area not exceeding 1500sq ft (140m2) and an occupant load less than 10. |  | occupant load less than 10.
407.2.4 | Gift Shops | Gift shops. Gift shops less than 500 square feet (46.5m2) in area shall be permitted to be open to the corridor provided the gift shop and storage areas are fully sprinklered and storage areas are protected in accordance with Section 302.1.1. | 407.2.4 | Gift shops. Gift shops shall not be open to the corridor except where such spaces are less than 500sq ft (46.5m2) in area and both the gift shop and any storage rooms are protected in accordance with Section 302.1.1. | Table 3-C | No separation required. | 409.2.5 | Gift shops. Gift shops shall not be open to the corridor except where such spaces are less than 500sq ft (46.5m2) in area and protected in accordance with Section 302.1.1. | 409.1.5 Table 409.1.5 | Required to be separated by non-fire-rated separations with smoke resistant doors. 409.1.5 Protection from hazardous areas. Hazardous areas listed in Table 409.1.5 shall be separated/protected as shown. All doors shall be self-closing or automatic closing by smoke detection. Where nonfire-rated separation is permitted, the hazardous area shall be separated from the remainder of the building by partitions constructed of materials consistent with the building type of construction and capable of resisting the passage of smoke. The partitions shall extend from the floor to the underside
of a fire-resistance rated floor/ceiling or roof/ceiling assembly or to the floor/roof deck above.
408.6.1 | Smoke Compart-ments | Smoke compartments. The maximum number of residents in any smoke compartment shall be 200. The travel distance to a door in a smoke barrier from any room door required as exit access shall not exceed 150 feet (45 720 mm). The travel distance to a door in a smoke barrier from any point in a room shall not exceed 200 feet (60 960 mm). | 408.6.1 | Smoke compartments. The maximum number of residents in any smoke compartment shall be 200. The travel distance to a door in a smoke barrier from any room door required as exit access shall not exceed 150ft (45720mm). The travel distance to a door in a smoke barrier from any point in a room shall not exceed 200ft (60960mm). | 317 |  | 410.6.1 | Smoke compartments. The maximum number of residents in any smoke compartment shall be 200. The travel distance to a door in a smoke barrier from any room door required as exit access shall not exceed 150ft (45720mm). The travel distance to a door in a smoke barrier from any point in a room shall not exceed 200ft (60960mm). | 409.2.14.2 | Where required, smoke barriers shall: 1. Limit the housing to a maximum of 200 residents in any smoke compartment, and 2. Limit the travel distance to a door in a smoke barrier from any room door required as exit access to 100ft (30.5m) and from any point in a room to 150ft (45.7m). Exception: The travel distance may be increased by 50ft (15.2m) in buildings protected by an approved automatic sprinkler system.
408.7.1 | Conditions Three and Four Occupancy | Occupancy Conditions 3 and 4. Each sleeping area in Occupancy Conditions 3 and 4 shall be separated from the adjacent common spaces by a smoke-tight partition where the travel distance from the sleeping area through the common space to the exit access corridor exceeds 50 feet (15 240 mm). | 408.7.1 | Occupancy Conditions 3 and 4. Each sleeping area in Occupancy Conditions 3 and 4 shall be separated from the adjacent common spaces by a smoke-tight partition where the travel distance from the sleeping area through the common space to the exit access corridor exceeds 50ft (15240mm). | 316.2 |  | 410.7.1 | Occupancy Conditions III and IV. Each sleeping area in Occupancy Conditions III and IV shall be separated from the adjacent common spaces by a smoke-tight partition where the travel distance from the sleeping area through the common space to the exit access corridor exceeds 50ft (15240mm). | Table 409.2.15 | Similar; smoke-tight partitions required regardless of travel distance in Use Condition 4 if non-sprinklered.
408.7.2 | Condition Five Occupancy | Occupancy Condition 5. Each sleeping area in Occupancy Condition 5 shall be separated from adjacent sleeping areas, corridors and common spaces by a smoke-tight partition. Additionally, common spaces shall be separated from the exit access corridor by a smoke-tight partition. | 408.7.2 | Occupancy Condition 5. Each sleeping area in Occupancy Condition 5 shall be separated from adjacent areas, corridors and common spaces by a smoke-tight partition. Additionally, common spaces shall be separated from the exit access corridor by a smoke-tight partition. | 316.2 |  | 410.7.2 | Occupancy Condition V. Each sleeping area in Occupancy Condition V shall be separated from adjacent sleeping areas, corridors and common spaces by a smoke-tight partition. Additionally, common spaces shall be separated from the exit access corridor by a smoke-tight partition. | Table 409.2.15 | Partitions may be fire resistive if non-sprinklered, and smoke-tight if sprinklered.
411.5 | Alarm | Alarm. Actuation of a single smoke detector, the automatic sprinkler system or other automatic fire detection device shall immediately sound an alarm at the building at a constantly attended location from which emergency action can be initiated including the capability of manual initiation of requirements in Section 907.2.11.2. | 411.5 | Alarm. Actuation of a single smoke detector, the automatic sprinkler system to other automatic fire detection device shall immediately sound an alarm at the building at a constantly attended location from which emergency action can be initiated including the capability of manual initiation of requirements in Section 907.2.11.2. | 408.5.2 408.5.3 | 408.5.2 Alarm System. Activation of any single smoke detector, the automatic sprinkler system or other automatic fire-detection device shall immediately sound an alarm in the building at a constantly supervised location from which the manual operation of system noted in Section 408.5.3, Items 1, 2 and 3 may be initiated. 408.5.3 System Response. The activation of two or more smoke detectors, a single smoke detector monitored by an alarm verification zone, the automatic sprinkler system or other approved automatic fire-detection device shall automatically: 1. Stop confusing | 413.5 413.5.1 | System response. The activation of the automatic fire detection system within a single protected area do the automatic sprinkler system shall automatically: 1. Cause illumination of the means of egress with light of not less than 1 footcandle (10.76lux) at the walking surface level; 2. Stop any conflicting or confusing sounds and visual distractions; and 3. Activate an approved diagonal exit marking that will become apparent in an emergency. 413.5.1. Alarm. Activation of any single smoke detector, the automatic sprinkler system or any other automatic fire detection device shall immediately sound an | 403.5.5 | System response. 403.5.5.1 The activation of the automatic fire detection system within a single protected area or the automatic sprinkler system shall automatically: 1. Cause illumination of the means of egress with light of not less than 1 foot-candle (10.81x) at the walking surface level, and 2. Stop any conflicting or confusing sounds and visual effects, and 3. Activate an approved directional exit marking that will become apparent in an emergency. 403.5.5.2 Activation of ay single smoke detector, the automatic sprinkler system or any other automatic fire detection device shall
[6 empty] | sounds and visual effects, 2. Activate an approved directional exit marking, and 3. Cause illumination of the means of egress with light of not less than 1 footcandle (10.76 1x) at the walking surface. |  | alarm at the building at a constantly attended location from which emergency action can be initiated including the capability of manual initiation of requirements in Section 413.5. |  | immediately sound an alarm at the building at a constantly attended location from which emergency action can be initiated including the capability of manual initiation of 403.5.5.1(1) through 4.3.5.5.1(3). 403.5.5.3 A public address system shall be installed in accordance with NFPA 72 shall be provided and shall be audible throughout the entire amusement building.
413.2 | Attic, Underfloor, and Concealed Spaces | Attic, under-floor and concealed spaces. Attic, under- floor and concealed spaces used for storage of combustible materials shall be protected on the storage side as required for 1-hour fire-resistant construction. Openings shall be protected by assemblies that are self-closing and are of noncombustible construction or solid wood core not less than 13/4 inch (45 mm) in thickness. Exceptions: 1. Areas protected by approved automatic sprinkler systems. 2. Group R-3 and U occupancies. | 413.2 | Attic, under-floor and concealed spaces. Attic, under-floor and concealed spaces used for storage of combustible materials shall be protected on the storage side as required by for 1-hour fire-resistant construction. Openings shall be protected by assemblies that are self-closing and are of noncombustible construction or solid wood core not less than 1 3/4 inch(45mm) in thickness. Exception: 1. Areas protected by approved automatic sprinkler systems. 2. group R-3 and Group U occupancies. | 712 | Usable Space under Floors. Usable space under the first story shall be enclosed , and such enclosure, when constructed of metal or wood, shall be protected on the side of the usable space as required for one-hour fire-resistive construction. Doors shall be self-closing, tightfitting of solid wood construction 1 3/8 inches (35mm) in thickness or self-closing , tightfitting doors acceptable as a part of an assembly having a fire-protection rating of not less than 20 minutes when tested in accordance with Part II of UBC Standard 7-2. Exceptions: 1. Group R, Division 3 and Group U Occupancies. 2. Basements in |  | No related section. |  | No related section.
single-story Group S, Division 3 repair garages where 10% or more of the area of floor-ceiling is open to the first floor. 3. Underfloor spaces protected by an automatic sprinkler system.
414.5.3 | Automatic Fire Detection | Automatic fire detection systems. Group H occupancies shall be provided with an automatic fire detection system in accordance with Section 907.2. | 414.5.3 | Automatic fire detection systems. Group H occupancies shall be provided with an automatic sire detection system in accordance with Section 907.2. | 307.9 | Fire Alarm Systems. An approved manual fire alarm system shall be provided in Group H Occupancies used for the manufacturing of organic coatings. Approved automatic smoke detection shall be provided for rooms used for storage, dispensing, use and handling of hazardous materials when required by the Fire Code. For Group H, Division 6 Occupancies See Section 307.11. For installation requirements, see the Fire Code. For aerosol storage warehouses, see the Fire Code. | 417.5.3 | Detection systems. All occupancies in Group H shall be provided with an automatic fire detection system in accordance with NFPA 72 listed in Chapter 35 where required by the fire prevention code listed in Chapter 35. The detection system shall be provided in areas where the hazardous materials are utilized and stored. | 407.2.5.2 | Smoke detection. Activation of the detection system shall sound a local alarm. An approved smoke detection system installed in accordance with 905 shall be provided in: 1. Rooms or areas where highly toxic compressed gases, liquid or solid oxidizers, or unclassified detonable, Class I or Class II organic peroxides are stored. 2. Where Class III or Class IV organic peroxides are stored in quantities exceeding the exempt amounts specified in Table 407.2.5. Exception: A smoke detection system shall not be required in detached storage buildings, storing those oxidizers and organic peroxides
listed above, if such buildings are provided with an automatic fire extinguishing system.
504.2 | Automatic Sprinkler Increase | Automatic sprinkler system increase. Where a building is equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1, the value specified in Table 503 for maximum height is increased by 20 feet (6096 mm) and the maximum number of stories is increased by one story. These increases are permitted in addition to the area increase in accordance with Sections 506.2 and 506.3. For Group R buildings equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.2, the value specified in Table 503 for maximum height is | 504.2 | Automatic Sprinkler increase. For buildings protected throughout with an approved automatic sprinkler system installed in accordance with Section 903.3.1.1, the value specified in Table 503 for maximum height is increased by 20ft (6096mm) and the maximum number of stories is increased by 1 story. For Group R buildings protected throughout with an approved automatic sprinkler system installed in accordance with Section 903.3.1.2, the value is specified in Table 503 for maximum height is increased by 20ft (6096mm) and the maximum number of stories is increased by one story, but shall not | 506 | Maximum Height of Buildings and Increases. The maximum height and number of stories of buildings shall be dependent on the character of the occupancy and the type of construction and shall not exceed the limits set forth in Table 5-B, except as provided in this section and as specified in Section 302.1 for mixed occupancy buildings. Exceptions: 1. Towers, spires and steeples erected as a part of a building and not used for habitation or storage are limited as to height only by structural design if completely of noncombustible materials, or may extend not to exceed 20 feet (6096mm) | 504.2 | Automatic sprinkler systems. Where a building is equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1, the building height limitation specified in Table 503 shall be increased one story and 20ft (6096mm). The building height limitations for buildings with occupancy in Use Group R specified in Table 503 shall be increased one story and 20ft (6096mm) but not to exceed a height of four stories and 60ft (18288mm) where the building is equipped throughout with an automatic sprinkler system installed in accordance with Section 906.2.2 and the system is | Table 500 | Increases reflected in table values.
|  | increased by 20 feet (6096 mm) and the maximum number of stories is increased by one story, but shall not exceed four stories or 60 feet (18 288 mm), respectively. Exceptions: 1. Group I-2 of Type IIB, III, IV or V construction. 2. Group H-1, H-2, H-3 or H-5. 3. Fire-resistance rating substitution in accordance with Table 601, Note d. |  | exceed four stories or 60ft (18288mm), respectively. These increases are permitted in addition to the area increase. Exceptions: 1. Group I-2 of Type IIB, III, IV, or V construction. 2. Group H-1, H-2, H-3 or H-5. |  | above the height limit in Table 5-B of combustible materials. 2. The height of one-story aircraft hangars and buildings used for manufacture of aircraft shall not be limited if the building is provided with automatic sprinkler systems throughout as specified in Chapter 9 and is entirely surrounded by public ways or yards not less in width than one- and one-half times the height of the building. The story limits set forth in Table 5-B may be increased by one story if the building is provided with an approved automatic sprinkler system throughout. The increase in the number of stories for automatic sprinkler systems shall not |  | supervised is accordance with Section 924.1, method 1. Exception: The automatic sprinkler system height increase shall not apply to any of the following conditions: 1. Buildings with an occupancy in Use Group H-1. 2. A fire area with an occupancy in Use Groups H-2 or H-3. 3. Buildings of Types 2C, 3A, 4 and 5A construction with an occupancy in Use Group I-2.
apply when the automatic sprinkler systems throughout are installed under the following provisions: 1. Section 904.2.6 for Group H, Divisions 1,2,3,6 and 7 Occupancies. 2. Section 505 for an increase in allowable area. 3. Substitution for one-hour fire-resistive construction pursuant to Section 508. 4. Section 402, Atria. 5. Section 904.2.7 for Group I, Division 1.1 and 1.2 Occupancies used as hospitals, nursing homes or health-care centers in Type II One-hour, Type III One-hour, Type IV or Type V One-hour construction. See Chapters 3 and 4 for special occupancy provisions.
506.1 | General | General. The areas limited by Table 503 shall be permitted to be increased due to frontage (If) and automatic sprinkler system protection (Is) in accordance with the following: Formula Omitted. | 506.1 | General. The areas limited by Table 503 shall be permitted to be increased due to frontage and automatic sprinkler system protection in accordance with the following: Formula omitted. | 505.1 505.2 505.3 | 505.1 General. The floor areas specified in Section 504 may be increased by employing one of the provisions of this section. 505.2 Unlimited Area. The area of any one- or two-story building of Groups B;F, Division 1 or 2; M;S, Division 1,2,3,4 or 5; and H, Division 5 Occupancies shall not be limited if the building is provided with an approved automatic sprinkler system throughout as specified in Chapter 9, and entirely surrounded and adjoined by public ways or yards not less than 60 ft (18288mm) in width. The area of Group S, Division 2 or Group F, Division 2 Occupancy in a one-story Type II, Type III | 506.2 506.3 | Street frontage increase. Where a building or structure has more than 25% of the building perimeter fronting on a street or other unoccupied space, the area limitations specified in Table 503 shall be increased 2% for each 1% of such excess frontage. The unoccupied space shall be on the same lot or dedicated for public use, shall not be less than 30ft (9144mm) in width and shall have access from a street by a posted fire lane not less than 18ft (5486mm) in width. 506.3 Automatic sprinkler system. Where a building is equipped throughout with an automatic sprinkler system installed in | 503.3.1 | The exceptions and requirements of 503.3 and 503.4 shall modify unsprinklered areas permitted by Table 500 and the specific use provisions of this chapter.
[6 empty] | One-hour or Type IV building shall not be limited if the building is entirely surrounded and adjoined by public ways or yards not less than 60 ft (18288mm) in width. 505.3 Automatic Sprinkler Systems. The areas specified in Table 5-B and Section 504.2 may be tripled in one-story buildings and doubled in buildings of more than one story if the building is provided with an approved automatic sprinkler system throughout. The area increases permitted in this section may be compounded with that specified in Section 505.1.1, 505.1.2 or 505.1.3. The increases permitted in this section shall not apply when automatic |  | accordance with Section 906.2.1, the area limitation specified in Table 503 shall be increased 200% for one- and two-story buildings and 100% for buildings more than two stories in height. Exceptions: 1. The automatic sprinkler system increase shall not apply to buildings with an occupancy in Use Group H-1. 2. The automatic sprinkler system increase shall not apply to any fire area with an occupancy in Use Group H-2 or H-3.
sprinkler systems are installed under the following provisions: 1. Section 506 for an increase in allowable number of stories. Section 904.2.6.1 for Group H, Divisions 1 and 2 Occupancies. 3. Substitution for one-hour fire-resistive construction pursuant to Section 508. 4. Section 402, Atria.
506.3 | Automatic Sprinkler Increase | Automatic sprinkler system increase. Where a building is protected throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1, the area limitation in Table 503 is permitted to be increased by an additional 200 percent (Is = 200 percent) for multistory buildings and an additional 300 percent (Is = 300 percent) for single-story buildings. These increases are permitted in addition to the height and story increases in accordance with Section 504.2. Exceptions: 1. Buildings with an occupancy in Group H-1, H-2 or H-3. 2. Fire-resistance rating substitution in accordance with Table | 506.3 | Automatic sprinkler system increase. Where a building is protected throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1, where the area limitation in Table 503 is permitted to be increased by 200% for multi-story buildings and 300% for single-story buildings. Exception: Group H-1, H-2 and H-3. | 505.3 | 505.3 Automatic Sprinkler Systems. The areas specified in Table 5-B and Section 504.2 may be tripled in one-story buildings and doubled in buildings of more than one story if the building is provided with an approved automatic sprinkler system throughout. The area increases permitted in this section may be compounded with that specified in Section 505.1.1, 505.1.2 or 505.1.3. The increases permitted in this section shall not apply when automatic sprinkler systems are installed under the following provisions: 1. Section 506 for an increase in allowable number of stories. Section 904.2.6.1 for Group H, Divisions 1 | 506.3 | 506.3 Automatic sprinkler system. Where a building is equipped throughout with an automatic sprinkler system installed in accordance with Section 906.2.1, the area limitation specified in Table 503 shall be increased 200% for one- and two-story buildings and 100% for buildings more than two stories in height. Exceptions: 1. The automatic sprinkler system increase shall not apply to buildings with an occupancy in Use Group H-1. 2. The automatic sprinkler system increase shall not apply to any fire area with an occupancy in Use Group H-2 or H-3. | Table 500 | Separate columns for sprinklered and unsprinklered.
|  | 601, Note d. |  |  |  | and 2 Occupancies. 3. Substitution for one-hour fire-resistive construction pursuant to Section 508. 4. Section 402, Atria.
507.2 | Sprinklered One-Story | Sprinklered, one story. The area of a one-story, Group B, F,M or S building or a one-story Group A-4 building of other than Type V construction shall not be limited when the building is provided with an automatic sprinkler system throughout in accordance with Section 903.3.1.1, and is surrounded and adjoined by public ways or yards not less than 60 feet (18 288 mm) in width. Exceptions: 1. Buildings and structures of Type I and II construction for rack storage facilities which do not have access by the public shall not be limited in height provided that such buildings conform to the requirements of | 507.2 | Sprinklered, one-story. The area of a one-story, Group A-4, B, F, M or S building shall not be limited when the building is provided with an automatic sprinkler system throughout in accordance with Section 903.3.1.1, and is surrounded and adjoined by public ways or yards not less than 60ft (18288mm) in width. Exceptions: 1. Buildings and structures of Types I and II construction for rack storage facilities which do not have access by public shall not be limited in height provided that such buildings conform to the requirements of Section 507.1 and NFPA 231C. 2. The automatic sprinkler system shall not be | 505.2 | 505.2 Unlimited Area. The area of any one- or two-story building of Groups B;F, Division 1 or 2; M;S, Division 1,2,3,4 or 5; and H, Division 5 Occupancies shall not be limited if the building is provided with an approved automatic sprinkler system throughout as specified in Chapter 9, and entirely surrounded and adjoined by public ways or yards not less than 60 ft (18288mm) in width. The area of Group S, Division 2 or Group F, Division 2 Occupancy in a one-story Type II, Type III One-hour or Type IV building shall not be limited if the building is entirely surrounded and adjoined by public ways or yards not less than 60 ft (18288mm) in width. | 507.1 | One-story buildings. For Use Groups A-3, B, F-1, F-2, I-2, M, S-1, and S-2 and for motion picture theaters, the area of the buildings that do not exceed one story and 85ft (25908mm) in height, other than buildings of Type 5 construction, shall not be limited, provided that the building is equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1; and the building is isolated as specified in Section 507.2. Buildings with an occupancy in Use Group I-2 shall not be constructed of Type 3B construction. Fire areas of Use Group E are permitted in unlimited area buildings in accordance with | 503.4 | Occupancy area modifications. 503.4.1 The area of a one story building of Group B, Group F, Group M, or Group S occupancy shall not be limited provided the building is equipped with an approved automatic sprinkler system throughout, in accordance with 903, or other automatic extinguishing systems as approved by the building official, and is surrounded on all sides by a permanent open space of not less than 60ft (18m). High-piled combustible storage shall be protected in accordance with Chapter 36 of the Standard Fire Prevention Code. Exceptions: 1. Where water may cause or increase a fire, other
|  | Section 507.1 and NFPA 231C. 2. The automatic sprinkler system shall not be required in areas occupied for indoor participant sports, such as tennis, skating, swimming and equestrian activities, in occupancies in Group A-4, provided that: 2.1. Exit doors directly to the outside are provided for occupants of the participant sports areas, and 2.2. The building is equipped with a fire alarm system with manual fire alarm boxes installed in accordance with Section 907. |  | required in areas occupied for indoor participant sports, such as tennis, skating, swimming and equestrian activities, in occupancies in Group A-4, provided that: 2.1 Exit doors directly to the outside are provided for occupants of the participant sport areas, and 2.2 The building is equipped with a fire alarm system with manual fire alarm boxes installed in accordance with Section 907. |  |  |  | Section 507.1.1. Fire areas of Use Groups H-2, H-3 and H-4 are permitted in unlimited areas buildings in accordance with Section 507.1.2. Exceptions: 1. Buildings and structures of special industrial occupancies in accordance with Section 503.1.1 shall be exempt from the above height limitations and fire separation distance requirements, and the automatic suppression system shall not be provided where such installations will be detrimental or dangerous to the specific occupancy as approved by the code official. Where located with a fire separation distance of less than 30ft (9144mm), the |  | fire extinguishing systems shall be required in rooms or buildings used for the manufacture or storage of hazardous materials including but not limited to, aluminum powder, calcium carbide, metallic sodium and potassium, quicklime, magnesium powder and sodium peroxide. 2. In Group F and Group S occupancies where noncombustible products are manufactured or stored, such as metal processing and manufacturing plants, and metal products are not stored in combustible wrappings, containers or palletized, the sprinkler system may be omitted upon approval of the building official.
[8 empty] | exterior walls of such buildings shall be protected or constructed to provide a fire resistance rating of not less than 2 hours. 2. The automatic fire suppression system shall not be required for buildings of Type 2 or Type 4 construction which are occupied exclusively for the storage of noncombustible materials that are not packed or crated in combustible materials. 3. Buildings and structures of Types 1 and 2 construction for rack storage facilities which do not have access by the public shall not be limited in height provided that such buildings conform to the requirements of Section 507.1 and |  | 503.4.2 The area of a one-story building of Type IV construction used for Group E occupancy shall not be limited provided the building is equipped throughout with an approved automatic sprinkler system in accordance with 903, is surrounded on all sides by a permanent open space of not less than 60ft (18.3m), and is provided with 1-hour fire resistant smokestop partitions dividing the building into areas not to exceed 30000sq ft (2787m2) in floor area. 503.4.3 One-story Group A buildings without a stage requiring proscenium opening protection of Type V 1-hour, IV or III construction which are surrounded on all sides by a permanent
[8 empty] | NFPA 231C listed in Chapter 35. 4. The automatic sprinkler system shall not be required in areas occupied for indoor participant sports, such as tennis, skating, and swimming and equestrian activities, in occupancies in Use Group A-3 provided that: 4.1 Exit doors directly to the outside are provided for all occupants of the participant sport areas; and 4.2. The building is equipped with a fire alarm system with manual fire alarm boxes installed in accordance with Section 918.0. 5. The automatic fire suppression system shall not be required for buildings of Type 2 or Type 4 construction classified as agricultural buildings. |  | open space not less than 60ft (18.2m), are provided with an approved automatic sprinkler system, and the assembly floor is located at, or within 21inches (533mm) of street or grade level and all exits meet the street or grade level by ramps having a slope not exceeding 1:10 shall not be limited in area. 503.4.4 Where there are no balconies or galleries in Group A - Large Assemblies without a stage requiring proscenium opening protection or in Group A - Small Assembly with or without a stage requiring proscenium opening protection, and the assembly floor is located at or within 21inches (533mm) of street or grade level and all exits meet the
street or grade level by ramps having a slope not exceeding 1:10, the maximum allowable areas of Type III, IV and V construction may be increased 50% over the unsprinklered areas specified in Table 500. This increase may be added to the area increase permitted by 503.3.2. 503.4.5 One-story buildings used for participation sports such as tennis, skating and similar activities, limited in occupant content to those participating in the sports activity, with no spectator seating permitted, may be unlimited in area when of Types III, IV and V construction and are surrounded on all sides by not less than 30ft (9144mm) of permanent open
space. 503.4.6 When used as a place of worship, the allowable areas for Group A - Small Assembly without a stage requiring proscenium opening protection may be increased 33 1/3% over the unsprinklered areas specified in Table 500. The increase may be added to the area increase permitted by 503.3.2. 503.4.7 The area of a one story Group E, Type III, IV or V building may be increased 100% over the unsprinklered areas specified in Table 500 if the building is surrounded on all sides by a permanent open space of not less than 60ft (18.3m), and there are not less than two exits provided from each classroom, one
of which opens directly to the exterior of the building. This increase may be added to the area increase permitted by 503.3.2. 503.4.8 The permanent open space of 60ft (18.3m) required in 503.4.1, 503.4.2, 503.4.3 and 503.4.7 shall be permitted to be reduced to not less than 40ft (12.2m) provided all the following requirements are met: 1. The reduced open space shall not be allowed for more than 75% of the perimeter of the building. 2. The exterior wall facing the reduced open space shall have a minimum fire resistance rating of 3 hours. 3. All openings in the exterior wall, facing the reduced open space, shall have opening protectives
with a fire resistance rating of 3 hours. 503.4.9 Group A area modification: Open air grandstands and bleachers, see 403.6.2.1. 503.4.10 Group M area modifications: covered mall buildings see 413.6. 503.4.11 Group S area modifications: 1. Aircraft hangars see 411.7.2. 2. Automobile parking garages see 411.3.
507.3 | Two-Story | Two story. The area of a two-story, Group B, F, M or S building shall not be limited when the building is provided with an automatic sprinkler system in accordance with Section 903.3.1.1 throughout, and is surrounded and adjoined by public ways or yards not less than 60 feet (18 288 mm) in width. | 507.3 | Two-story. The area of a two-story, Group B, F, M or S building shall not be limited when the building is provided with an automatic sprinkler system in accordance with Section 903.3.1.1 throughout, and is surrounded and adjoined by public ways or yards not less than 60ft (18288mm) in width. | 505.2 | 505.2 Unlimited Area. The area of any one- or two-story building of Groups B;F, Division 1 or 2; M;S, Division 1,2,3,4 or 5; and H, Division 5 Occupancies shall not be limited if the building is provided with an approved automatic sprinkler system throughout as specified in Chapter 9, and entirely surrounded and adjoined by public ways or yards not less than 60 ft (18288mm) in width. The area of Group S, Division 2 or Group F, Division 2 Occupancy in a one-story Type II, Type III One-hour or Type IV building shall not be limited if the building is entirely surrounded and adjoined by public ways or yards not less than 60 ft (18288mm) in width. |  | No related section. |  | No related section.
507.8 | Group E Buildings | Group E buildings. The area of a one-story Group E building of Type II, IIIA or IV construction shall not be limited when the following criteria are met: 1. Each classroom shall have not less than two means of egress, with one of the means of egress being a direct exit to the outside of the building complying with Section 1017. 2. The building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 3. The building is surrounded and adjoined by public ways or yards not less than 60 feet (18 288 mm) in width. | 507.7 | Group E buildings. The area of a one-story Group E building of Type II, IIIA or IV construction shall not be limited when the following criteria are met: 1. Each classroom shall have not less than two means of egress, with one of the means of egress being a direct exit to the outside of the building complying with Section 1005. 2. The building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 3. The building is surrounded and adjoined by public ways or yards not less than 60ft (18288mm) in width. |  | No related section. | 507.1.1 | School buildings. For occupancies in Use Group E, one-story buildings of Type 2, 3A or 4 construction shall not be limited in area where a direct exit to the outside of the building is provided from each classroom and the building is equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1. Exterior walls on all sides of such buildings shall comply with Section 507.2. | 503.4.2 503.4.7 | 503.4.2 The area of a one-story building of Type IV construction used for Group E occupancy shall not be limited provided the building is equipped throughout with an approved automatic sprinkler system in accordance with 903, is surrounded on all sides by a permanent open space of not less than 60ft (18.3m), and is provided with 1-hour fire resistant smokestop partitions dividing the building into areas not to exceed 30000 sq ft (2787m2) in floor area. 503.4.7 The area of one story Group E Type III, IV or V building may be increased 100% over the unsprinklered areas specified in Table 500 if the building is surrounded on all sides by a
permanent open space not less than two exits provided from each classroom, one of which opens directly to the exterior of the building. This increase may be added to the area increase permitted by 503.3.2.
507.9 | Motion Picture Theater | Motion picture theaters. In buildings of Type I or II construction, the area of one-story motion picture theaters shall not be limited when the building is provided with an automatic sprinkler system throughout in accordance with Section 903.3.1.1 and is surrounded and adjoined by public ways or yards not less than 60 feet (18 288 mm) in width. | 507.8 | Motion picture theaters. In buildings of Type I or II construction, the area of one-story motion picture theaters shall not be limited when the building is provided with an automatic sprinkler system throughout in accordance with Section 903.3.1.1 and is surrounded and adjoined by public ways or yards not less than 60ft (18288mm) in width. |  | No related section. | 507.1 | One-story buildings. For Use Groups A-3, B, F-1, F-2, I-2, M, S-1, and S-2 and for motion picture theaters, the area of the buildings that do not exceed one story and 85ft (25908mm) in height, other than buildings of Type 5 construction, shall not be limited, provided that the building is equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1; and the building is isolated as specified in Section 507.2. Buildings with an occupancy in Use Group I-2 shall not be constructed of Type 3B construction. Fire areas of Use Group E are permitted in unlimited area buildings in accordance with |  | No related section.
Section 507.1.1. Fire areas of Use Groups H-2, H-3 and H-4 are permitted in unlimited areas buildings in accordance with Section 507.1.2. Exceptions: 1. Buildings and structures of special industrial occupancies in accordance with Section 503.1.1 shall be exempt from the above height limitations and fire separation distance requirements, and the automatic suppression system shall not be provided where such installations will be detrimental or dangerous to the specific occupancy as approved by the code official. Where located with a fire separation distance of less than 30ft (9144mm), the
exterior walls of such buildings shall be protected or constructed to provide a fire resistance rating of not less than 2 hours. 2. The automatic fire suppression system shall not be required for buildings of Type 2 or Type 4 construction which are occupied exclusively for the storage of noncombustible materials that are not packed or crated in combustible materials. 3. Buildings and structures of Types 1 and 2 construction for rack storage facilities which do not have access by the public shall not be limited in height provided that such buildings conform to the requirements of Section 507.1 and
NFPA 231C listed in Chapter 35. 4. The automatic sprinkler system shall not be required in areas occupied for indoor participant sports, such as tennis, skating, and swimming and equestrian activities, in occupancies in Use Group A-3 provided that: 4.1 Exit doors directly to the outside are provided for all occupants of the participant sport areas; and 4.2. The building is equipped with a fire alarm system with manual fire alarm boxes installed in accordance with Section 918.0. 5. The automatic fire suppression system shall not be required for buildings of Type 2 or Type 4 construction classified as agricultural buildings.
Table 601 | Fire-Resistance Rating Requirements for Building Elements | Table lists the hourly fire-resistance requirements for building elements as a function of building construction types. The construction types are sub-categorized as Types IA, IB, IIA, IIB, IIIA, IIIB, IV, VA, and VB. Footnotes include a definition of structural frame, reduction in roof frame fire-resistance, the use of sprinklers in lieu of 1-hour fire resistive construction, and the priority of fire-resistance of exterior walls due to separation. | Table 601 | Same | Table 6-A | The construction types and rating of building elements have some differences. See table for specifics. | Table 602 | The construction types and rating of building elements have some differences. See table for specifics. | Table 600 | The construction types and rating of building elements have some differences. See table for specifics.
602.4.3 | Roof Framing | Roof framing. Wood-frame or glued-laminated arches for roof construction, which spring from the floor line or from grade and do not support floor loads, shall have members not less than 6 inches (152 mm) nominal in width and have less than 8 inches (203 mm) nominal in depth for the lower half of the height and not less than 6 inches (152mm) nominal in depth for the upper half. Framed or glued laminated arches for roof construction that spring from the top of walls or wall abutments, framed timber trusses and other roof framing, which do not support floor loads, shall have members not less than 4 inches (102 mm) | 602.4.3 | Roof framing. Wood-framed or glued laminated-arches for roof construction, which spring from the floor line or from grade and do not support floor loads shall have members not less than 6 inches (152mm) nominal in width and have less than 8 inches (203mm) nominal in depth for the lower half of the height and not less than 6 inches (152mm) nominal in depth for the upper half. Framed or glued laminated arches for roof construction that spring from the top of walls or wall abutments, framed timber trusses, and other roof framing, which do not support floor loads, shall have members not less than 4 inches (102mm) | 605.6.4 | Roof framing. Framed sawn timber arches or structural glued-laminated timber arches for roof construction, which spring from the floor line and do not support floor loads, shall have members not less than 6 inches (152mm) in width and not less than 8 inches (203mm) in depth for the lower half of the height and not less than 6 inches (152mm) in depth for the upper half. Framed sawn timber or structural glued timber arches for roof construction, which spring from the top of walls or wall abutments, framed lumber or structural glued-laminated timber trusses, and other roof framing that does not support floor loads, shall have | 2304.5.1 | Arches. Framed or glued laminated arches for roof construction which spring from the floor line or from grade and do not support floor loads shall have members not less than 6 inches nominal in width, not less than 8 inches nominal in depth for the lower half of the height and not less that 6 inches nominal in depth for the upper half. Framed or glued laminated arches for roof construction which spring from the top of walls or wall abutments, framed timber trusses and other roof framing which does not support floor loads shall have members not less than 4 inches nominal in width and not less than 6 inches nominal in depth. | 605.4 | Roof framing. 605.4.1 Framed or glued laminated arches for roof construction which spring from the floor line and do not support floor loads shall have members not less than 6 inches nominal wide and 8 inches nominal deep for the lower of the height and not less than 6 inches nominal in any dimension for the upper half of the height. 605.4.2 Framed or glued laminated arches for roof construction which spring from the top of walls or wall abutments, framed timber trusses and other roof framing which do not support floor loads, shall have members not less than 6 inches nominal deep. Spaced
|  | nominal in width and not less than 6 inches (152 mm) nominal in depth. Spaced members shall be permitted to be composed of two or more pieces not less than 3 inches (76 mm) nominal in thickness where blocked solidly throughout their intervening spaces or where spaces are tightly closed by a continuous wood cover plate of not less than 2 inches (51 mm) nominal in thickness secured to the underside of the members. Splice plates shall be not less than 3 inches (76 mm) nominal in thickness. Where protected by approved automatic sprinklers under the roof deck, framing members shall be not less than 3 inches (76 mm) nominal in width. |  | nominal in width and not less than 6 inches (152mm) nominal in depth. Spaced members may be composed of two or more pieces not less than 3 inches (76mm) nominal in thickness where blocked solidly throughout their intervening spaces or where spaces are tightly closed by a continuous wood cover plate of not less than 2 inches (51mm) nominal in thickness secured to the underside of the members. Splice plates shall be not less than 3 inches (76mm) nominal in thickness. Where protected by approved automatic sprinklers under the roof deck, framing members shall not be less than 3 inches (76mm) nominal width. |  | members not less than 4 inches (102mm) in width and not less than 6 inches (152mm) in depth. Spaced members may be composed of two or more pieces not less than 3 inches (76mm) in thickness, when blocked solidly throughout their intervening spaces, or when such spaces are tightly closed by a continuous wood cover plate of not less than 2 inches (51mm) in thickness, secured to the underside of the members. Splice plates shall not be less than 3 inches(76mm) in thickness. When protected by an approved automatic sprinkler system under the roof deck, framing members shall not be less than 3 inches (76mm) in thickness. |  | Spaced members shall be composed of two or more pieces not less than 3 inches nominal in thickness where blocked solidly throughout their intervening spaces or where such spaces are tightly closed by a continuous wood cover plate of not less than 2 inches nominal in thickness, secured to the underside of the members. Splice plates shall not be less than 3 inches nominal in thickness. Where equipped with an automatic sprinkler system installed in accordance with Section 906.2.1, and 906.2.2 or 907.0 under the roof deck, framing members shall not be less than 3 inches nominal in width. |  | members may be composed of two or more pieces not less than 3 inches nominal thick when blocked solidly throughout their intervening spaces or when such spaces are tightly closed by a continuous wood cover plate or not less than 2 inches nominal thick, secured to the underside of the members. Splice plated shall be of no less than 3 inches nominal thick. When protected by approved automatic sprinklers under the roof deck, such framing members shall be not less than 3 inches nominal wide.
704.9 | Vertical Separation of Openings | Vertical separation of openings. Openings in exterior walls in adjacent stories shall be separated vertically to protect against fire spread on the exterior of the buildings where the openings are within 5 feet (1524 mm) of each other horizontally and the opening in the lower story is not a protected opening in accordance with Section 715.4.8. Such openings shall be separated vertically at least 3 feet (914 mm) by spandrel girders, exterior walls or other similar assemblies that have a fire-resistance rating of at least 1 hour or by flame barriers that extend horizontally at least 30 inches (762 mm) beyond the exterior wall. Flame barriers shall also | 704.9 | Vertical separation of openings. Openings in exterior walls in adjacent stories shall be separated vertically to protect against fire spread on the exterior of the buildings where the openings are within 5ft (1524mm) of each other horizontally and the opening in the lower story is not a protected opening in accordance with Section 714.3.7. Such openings shall be separated vertically at least 3ft (914mm) by spandrel girders, exterior walls or other similar assemblies that have a fire-resistance rating of at least 1 hour or by flame barriers that extend horizontally at least 30inches (762mm) beyond the exterior wall. Flame barriers shall also have a fire- | 709.3.2.3 | Exterior. When openings in an exterior wall are above and within 5 feet (1524mm) laterally of an opening in the story below, such openings shall be separated by an approved flame barrier extending 30 inches (762mm) beyond the exterior wall in the plane of the floor or by approved vertical flame barriers not less than 3 feet (914mm) high measured vertically above the top of the lower opening. Flame barriers shall have a resistance of not less than three-fourths hour. Exceptions: 1. Flame barriers are not required in buildings equipped with an approved automatic sprinkler system throughout. 2. This section shall not apply | 705.4 | Vertical separation of openings. Openings in exterior walls in adjacent stories shall be separated vertically to protect fire against fire spread on the exterior of the buildings where the openings are within 5ft (1524mm) of each other horizontally and the opening in the lower story is not a protected opening in accordance with Section 706.0. Such openings shall be separated vertically at least 3ft (914mm) by spandrel girders, exterior walls or other similar assemblies which have a fire resistance rating of at least 30inches (762mm) beyond the exterior wall. Flame barriers shall also have a fire resistance rating of at least 1 | 705.1.1.3 | Where openings in an exterior wall are above and within 5 ft (1524mm) laterally of an opening of the story below, such openings shall be separated by an approved noncombustible flame barrier extending 30 inches (762mm) beyond the exterior wall in the plane of the floor or by approved vertical flame barriers, not less than 3ft (914mm) high measured vertically above the top of the lower opening. Such flame barriers are not required when a complete approved automatic sprinkler system. is installed.
|  | have a fire-resistance rating of at least 1 hour. The unexposed surface temperature limitations specified in ASTM E 119 shall not apply to the flame barriers or vertical separation unless otherwise required by the provisions of this code. Exceptions: 1. This section shall not apply to buildings that are three stories or less in height. 2. This section shall not apply to buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. 3. Open parking garages. |  | resistance rating of at least one hour. The unexposed surface temperature limitations specified in ASTM E 119 shall not apply to the flame barriers or vertical separation unless otherwise required by the provisions of this code. Exceptions: 1. This section shall not apply to buildings that are three stories or less in height. 2. This section shall not apply to buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 3. Open parking garages. |  | to buildings of three stories or less in height. 3. Flame barriers are not required on Group S, Division 4 Occupancies. |  | hour. The unexposed surface temperature limitations specified in ASTM E 119 listed in Chapter 35 shall not apply to the flame barriers or vertical separation unless otherwise required by the provisions of this code. Exceptions: 1. This section shall not apply to buildings that are three stories or less in height. 2. This section shall not apply to buildings equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1.
704.12 | Opening Protection | Opening protection. Windows required to be protected in accordance with Section 704.8, 704.9, or 704.10 shall comply with Section 715.4.8. Other openings required to be protected with fire doors or shutters in accordance with Sections 704.8, 704.9 and 704.10 shall comply with Section 715.3. Exception: Fire protective assemblies are not required where the building is protected throughout by an automatic sprinkler system and the exterior openings are protected by an approved water curtain using automatic sprinklers approved for that use. The sprinklers and the water curtain shall be installed in | 704.12 | Opening protection. Windows required to be protected in accordance with Section 704.8, 704.9, or 704.10 shall comply with Section 714.3.7. Other openings required to be protected with the fire doors or shutters in accordance with Sections 704.8, 704.9 and 704.10 shall comply with Section 714.2. Exception: Fire protective assemblies are not required where the building is protected throughout by an automatic sprinkler system and the exterior openings are protected by an approved water curtain using automatic sprinklers approved for that use. The sprinklers and the water curtain shall be installed in | Table 5-A | Addresses locations requiring opening protection. | 706.1 706.3 | Where required. Exterior opening protectives shall be provided in all exterior wall openings that are required to be protected by Section 705.0. 706.2. Automatic protection. Approved fire protective assemblies shall be fixed, self-closing or equipped with approved automatic-closing devices and shall conform to the requirements of this section and Sections 702.0, 717.0, 718.0, 719.0 and 720.0. Fire protective assemblies are required where outside automatic sprinklers are installed for the protection of the exterior openings. The sprinklers shall be installed in accordance with NFPA 13 listed in | 705.1.3 | Approved types of fire windows, doors and shutters. 705.1.3.1 Wall openings required to be protected shall be protected by approved listed and labeled fire doors, windows and shutters and their accompanying hardware, including all frames, closing devices , anchorage and sills, in accordance with the requirements of NFPA 80, except as otherwise specified in this code. 705.1.3.2 Openings are classified in accordance with the character and location of the wall in which they are situated. Fire protection ratings for products intended to comply with this section shall be as
|  | accordance with NFPA 13. |  | accordance with NFPA 13. |  |  |  | Chapter 35, and shall have an automatic water supply and be provided with a fire department connection. |  | determined and reported by a nationally recognized testing agency in accordance with NFPA 252 or NFPA 257. All such products shall bear an approved label. In each of the following classes, the minimum fire protection ratings are shown. 705.1.3.2.1 Fire doors are classified as 3-hour, 1 1/2hour, 1 hour, 3/4 hour or 20 minutes. 705.1.3.2.2 Unless otherwise specified, door assembles in walls required to have a fire resistance rating of 1-hour or less shall have a fire resistance rating of 20 minutes when tested in accordance with NFPA 252 without the hose stream. Exception: For Group I Unrestrained, corridor doors shall be
in accordance with 409.1.4. 705.1.3.2.3 All doors in smoke barriers, horizontal exits, stairway enclosures and other doors opening between rooms and fire-rated exit access corridors shall be self-closing and so maintained or shall be provided with approved door holding devices of the fail-safe type which will release the door causing it to close when activated by approved listed smoke detectors. When doors are automatic-closing by smoke detection, there shall be not more than a 10-second delay before the door starts to close after the smoke detector is actuated. Exception: Doors from classrooms in Group
E occupancies, opening directly into a 1-hour rated corridor, may be installed without self-closing devices. 705.1.3.3 The maximum size of fire doors shall not exceed that specified in Appendix E, NFPA 80. 705.1.3.4 For 1 1/2 hour and 1-hour doors used in stairway enclosures the average temperature rise developed on the unexposed side shall not exceed 450 degrees F (232 degrees C) at the end of 30 minutes of standard fire test exposure. 705.1.3.5 Fire doors shall be equipped with an approved closer. See 1009.2.2 for doors in horizontal exits. Exception: Doors located in common walls separating guest
rooms in Group R1 hotels and motels may be installed without automatic or self-closing devices. 705.1.3.6 View panels. 705.1.3.6.1 1/4-inch (6.4mm) thick wired glass labeled for fire protection purposes may be used in approved opening protectives with the maximum sizes shown in Table 705.1.3.6. Other glazing materials which have been tested and labeled to indicate the type of opening to be protected for fire protection purposes may be used in approved opening protectives in accordance with their listing with the maximum sizes tested. For requirements for safety glazing, see 2405. Table omitted.
705.1.3.6.2 View panels in 1-hour fire resistant partitions shall consist of one of the following: 1. 1/4 inch (6.4mm) thick labeled wire glass assemblies installed in steel frames. The wired glass shall be limited to 1296 sq in (0.84m2) with no dimension greater than 54 inches (1372mm). 2. Labeled glass block panels installed in steel channels. The glass block shall be limited to 120 sq ft (11.1m2) with no dimension greater than 12ft (3658mm). 3. Other glazing materials which have been tested and labeled to indicate the type of opening to be protected for fire protection purposes may be used in approved opening protectives in
accordance with their listing with the maximum sizes tested. None of the assemblies shall exceed 25% of the wall area separating each tenant space from corridor. 705.1.3.6.3 View panels shall achieve a minimum fire protection rating of 45 minutes, including fire endurance and hose stream tests in accordance with NFPA 257 under positive pressure. Within the first ten minutes of a test, the pressure in the furnace shall be adjusted so at least 2/3 of the test specimen is above the neutral pressure plane, and the neutral pressure plane shall be maintained at that height for the balance of the test.
705.8 | Openings | Openings. Each opening through a firewall shall be protected in accordance with Section 715.3 and shall not exceed 120 square feet (11m2). The aggregate width of openings at any floor level shall not exceed 25 percent of the length of the wall. Exceptions: 1. Openings are not permitted in party walls constructed in accordance with Section 503.2. 2. Openings shall not be limited to 120 square feet (11 m2) where both buildings are equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1. | 705.8 | Openings. Each opening through a fire wall shall be protected in accordance with Section 714.2 and shall not exceed 120sq ft (11m2). The aggregate width of openings at any floor level shall not exceed 25% of the length of the wall. Exceptions: 1. Openings are not permitted in party walls constructed in accordance with Section 503.2. 2. Openings shall not be limited to 120sq ft (11m2) where both buildings are equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1. | 504.6.2 | Fire resistance and openings. Area separation walls shall not be less than four-hour fire-resistive construction in Types I, II-F.R., III, and IV buildings and two-hour fire-resistive construction in Type II One-hour, Type II-N or Type V buildings. The total width of all openings in such walls shall not exceed 25% of the length of the wall in each story. All openings shall be protected by a fire assembly having three-hour fire-protection rating in four-hour fire-resistive walls and one- and one-half-hour fire-protection rating in two-hour fire-resistive walls. | 708.2 708.2.1 708.3 | 708.2. Size of opening. Each opening through a fire wall shall not exceed 120sq ft (11m2). The aggregate width of all openings at any floor level shall not exceed 25% of the length of the wall. Exception: Openings shall not be limited to 120sq ft (11m2) where both buildings are equipped throughout with an automatic sprinkler system installed in accordance with Chapter 9. 708.2.1 First Story. Where the entire first-story floor areas on both sides of a fire wall are equipped throughout with an approved automatic sprinkler system installed in accordance with Section 906.2.1, the maximum allowable size of openings on the first story of the |  | No related section.
building shall not exceed 240sq ft (22m2) with a minimum distance of 3ft (914mm) between adjacent openings. 708.3 Opening protectives. All opening protectives in fire walls shall comply with the provisions of Section 704.0 and shall have the minimum fire protection rating as set forth in Section 717.0.
707.2 | Shaft Enclosure 2)Escalator or stairway not part of means of egress in sprinklered building; 5)Floor openings of malls and atriums | Shaft enclosure required. Openings through a floor/ceiling assembly shall be protected by a shaft enclosure complying with this section. Exceptions: 1. A shaft enclosure is not required for openings totally within an individual residential dwelling unit and connecting four stories or less. 2. A shaft enclosure is not required in a building equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 for an escalator opening or stairway which is not a portion of the means of egress protected according to Item 2.1 or 2.2: 2.1. Where the area of the floor opening between stories does not | 707.2 | Shaft enclosure required. Openings through a floor/ceiling assembly shall be protected by a shaft enclosure complying with this section. Exceptions: 1. A shaft enclosure is not required for openings totally within an individual residential dwelling unit and connecting four stories or less. 2. A shaft enclosure is not required in a building equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. for an escalator opening or stairway which is not a portion of the means of egress protected according to Items 2.1 or 2.2: 2.1. Where the area of the floor opening between stories does not | 711.1 711.3 | 711.1 General. Openings through floors shall be enclosed in a shaft enclosure of fire-resistive construction having the time period set forth in Table 6-A for "shaft enclosures" except as permitted in Sections 711.3, 711.5 and 711.6. See also Section 304.6 for shafts in Group B Occupancies, Section 306.6 for shafts in Group F Occupancies, Sections 307.6 and 307.11.2.3 for shafts in Group H Occupancies, Section 309.6 for shafts in Group M Occupancies and Section 311.6 for shaft in Group S Occupancies. 711.3 Special Provision. In other than Group I Occupancies, openings that | 713.3 | Floor opening enclosure. All floor openings connecting two or more stories shall be protected by a shaft enclosure that complies with Section 710.0. Exception: A shaft enclosure in not required for any of the following floor openings: 1. A floor opening serving and contained within a single dwelling unit and connecting four stories or less. 2. A floor opening which: 2.1. Is not part of the required means of egress. 2.2. is not concealed within the building construction; 2.3. Does not connect more than two stories; 2.4. Is separated from other floor openings serving other floors by construction conforming to Section 710.3; and 2.5. Is not | 705.2.2 | Shaft enclosures. All openings through a floor and penetrations through a floor shall be protected by a shaft enclosure in accordance with 705.2.3. Exceptions: 1. A shaft enclosure is not required for openings totally within a dwelling unit and connecting four stories or less. 2. A shaft enclosure is not required for a floor opening which: 1. is not part of the required means of egress, and 2. is nor concealed within the building construction, and 3. does not connect more than two stories, and 4. does not connect with a stairway or escalator serving other floors, and 5. is not open to any corridors in Group I and R Occupancies
|  | exceed twice the horizontal projected area of the escalator or stairway and the opening is protected by a draft curtain and closely spaced sprinklers in accordance with NFPA 13. In other than Groups B and M, this application is limited to openings that do not connect more than four stories. 2.2. Where the opening is protected by approved power-operated automatic shutters at every floor penetrated. The shutters shall be of noncombustible construction and have a fire-resistance rating of not less than 1.5 hours. The shutter shall be so constructed as to close immediately upon the actuation of a smoke detector |  | exceed twice the horizontal projected area of the escalator or stairway and the opening is protected by a draft curtain and closely spaced sprinklers in accordance with NFPA 13. In other than Groups B and M, this application is limited to openings that do not connect more than four stories. 2.2. Where the opening is protected by approved power-operated automatic shutters at every floor penetrated. The shutters shall be noncombustible construction and have a fire-resistance rating of not less than 1.5 hours. The shutter shall be so constructed as to close immediately upon the actuation of |  | penetrate only one floor and are not connected with openings communicating with other stories or basements and that are not concealed within building construction assemblies need not be enclosed. Exit enclosures shall conform to the applicable provisions of Section 1005.3.3. In one- and two-story buildings other than Group I Occupancies, gas vents, ducts, piping and factory-built chimneys that extend through not more than two floors need not be enclosed, provided the openings around the penetrations are firestopped at each floor. |  | open to a corridor in occupancies in Use Groups I and R, or is not open to a corridor on a floor not equipped throughout with an approved automatic fire suppression system in the use groups. 3. A floor opening in a mall that complies with section 402.0. 4. A floor opening between a mezzanine that complies with Section 505.0. and the floor below. 5. An atrium that complies with Section 404.0. 6. A floor opening in an open parking structure that complies with Section 406.0. 7. An approved concrete or masonry chimney where annular space protection is provided for in accordance with Section 721.6.4. 8. A floor opening |  | or to corridors on nonsprinklered floors in other occupancies, and 6. is separated from floor openings serving other floors by construction conforming with required shaft enclosures. 3. A shaft enclosure is not required for penetrations by pipe, tube, conduit, wire, cable, duct and vents protected in accordance with 705.4. 4. A shaft enclosure is not required for floor openings complying with the special provisions for covered malls or atriums. 5. A shaft enclosure is not required for approved masonry chimneys where annular space protection is provided at each floor level in
|  | installed in accordance with Section 907.11 and shall completely shut off the well opening. Escalators shall cease operation when the shutter begins to close. The shutter shall operate at a speed of not more than 30 feet per minute (152.4 mm/s) and shall be equipped with a sensitive leading edge to arrest its progress where in contact with any obstacle, and to continue its progress on release therefrom. 3. A shaft enclosure is not required for penetrations by pipe, tube, conduit, wire, cable, and vents protected in accordance with Section 712.4. 4. A shaft enclosure is not required for penetrations by ducts |  | a smoke detector installed in accordance with Section 907.10 and shall completely shut off the well opening. Escalators shall cease operation when the shutter begins to close. The shutter shall operate at a speed of not more than 30ft per minute (152.4mm/s) and shall be equipped with a sensitive leading edge to arrest its progress where in contact with any obstacle, and to continue its progress on release therefrom. 3. A shaft enclosure is not required for penetrations by pipe, tube, conduit, wire, cable, and vents protected in accordance with 711.4. 4. A shaft enclosure is not required for penetrations by ducts |  |  |  | containing an escalator and complying with Section 3011.2. 9. A floor opening that complies with Section 410.5 in an occupancy in Use Group I-3. 10. Noncombustible shafts connecting communicating floor levels in an occupancy in Use Group I-3 where the area complies with Section 410.5. Where additional stories are located above or below, the shaft shall be permitted to continue with fire and smoke damper protection provided at the fire resistance rated floor/ceiling assembly between the noncommunicating stories. 11. A single floor opening containing a stairway which is not a required means of egress in an |  | accordance with 705.4. 6. A shaft enclosure is not required for floor openings in an open parking garage. 7. A shaft enclosure is not required for floor openings between a mezzanine and the floor below. 8. A shaft enclosure is not required in fully sprinklered buildings for an escalator opening protected in accordance with one of the following alternatives: Alternative A - (1) the area of the floor opening between stories shall not exceed twice the horizontal projected area of the escalator, and (2) Draft curtains and special sprinkler head locations shall meet the requirements of NFPA 13, and (3) In other than Group B
|  | protected in accordance with Section 712.4. Grease ducts shall be protected in accordance with the International Mechanical Code. 5. A shaft enclosure is not required for floor openings complying with the provisions for covered malls or atriums. 6. A shaft enclosure is not required for approved masonry chimneys, where annular space protection is provided at each floor level in accordance with Section 717.2.5. 7. In other than Groups I-2 and I-3, a shaft enclosure is not required for a floor opening that complies with the following: 7.1. Does not connect more than two stories. 7.2. Is not part of the |  | protected in accordance with Section 711.4.4. Grease ducts shall be protected in accordance with the IMC. 5. A shaft enclosure is not required for floor openings complying with the provisions for covered malls or atriums. 6. A shaft enclosure is not required for approved masonry chimneys, where annular space protection is provided at each floor level in accordance with Section 716.2.5. 7. In other than Groups I-2 and I-3, a shaft enclosure is not required for a floor opening that complies with the following: 7.1. Does not connect more than two stories. 7.2. Is not part of the required means of |  |  |  | occupancy in Use Group B and complying with the following parameters: 11.1 The stairway does not connect more than six floor levels. 11.2. The stairway does not connect with an exit access corridor. 11.3. The stairway floor opening shall not exceed 160sq ft (15m2). 11.4. The stairway floor opening shall be protected in the same manner as an escalator floor opening complying with Section 3011.2. 11.5. the building is equipped throughout with an approved automatic sprinkler system in accordance with Section 906.2.1. |  | and M occupancies the escalator openings shall not connect more than four stories, or Alternative B - The opening is protected by approved power operated automatic shutters at every floor opening. The shutters shall be of noncombustible construction and have a fire resistance rating of not less than 1 1/2 hours. The shutter shall close immediately upon the automatic detection of smoke by an approved device and shall completely shut off the floor opening. The escalator shall stop when the shutter begins to close. The shutter shall operate at a speed of not more than 30ft per minute (0.152 m/s) and shall
|  | required means of egress system except as permitted in Section 1019.1. 7.3. Is not concealed within the building construction. 7.4. Is not open to a corridor in Group I and R occupancies. 7.5. Is not open to a corridor on nonsprinklered floors in any occupancy. 7.6. Is separated from floor openings serving other floors by construction conforming to required shaft enclosures. 8. A shaft enclosure is not required for automobile ramps in open parking garages and enclosed parking garages constructed in accordance with Sections 406.3 and 406.4, respectively. 9. A shaft enclosure is |  | egress system except as permitted in Section 1005.3.2. 7.3. Is not concealed within the building construction. 7.4. Is not open to a corridor in Group I and R occupancies. 7.5. Is not open to a corridor or nonsprinklered floors in any occupancy. 7.6. Is separated from floor openings serving other floors by construction conforming to required shaft enclosures. 8. A shaft enclosure is not required for automobile ramps in open parking garages and enclosed parking garages constructed in accordance with Sections 406.3 and 406.4, respectively. 9. A shaft enclosure is not required for joints | [5 empty] | be equipped with a sensitive leading edge to arrest its progress when in contact with any obstacle, and to continue its progress after release.
|  | not required for floor openings between a mezzanine and the floor below. 10. A shaft enclosure is not required for joints protected by a fire-resistant joint system in accordance with Section 713. 11. Where permitted by other sections of this code. |  | protected by a fire-resistant joint system in accordance with Section 712. 11. Where permitted by other sections of this code.
707.11 | Enclosure at the Bottom | Enclosure at the bottom. Shafts that do not extend to the bottom of the building or structure shall: 1. Be enclosed at the lowest level with construction of the same fire-resistance rating as the lowest floor through which the shaft passes, but not less than the rating required for the shaft enclosure; 2. Terminate in a room having a use related to the purpose of the shaft. The room shall be separated from the remainder of the building by construction having a fire-resistance rating and opening protectives at least equal to the protection required for the shaft enclosure; or 3. Be protected by approved fire dampers installed | 707.11 | Enclosure at the bottom. Shafts that do not extend to the bottom of the building or structure shall: 1. Be enclosed at the lowest level with construction of the same fire-resistance rating as the lowest floor through which the shaft passes, but not less than the rating required for the shaft enclosure. 2. Terminate in a room having a use related to the purpose of the shaft. The room shall be separated from the remainder of the building by construction having a fire-resistance rating and opening protectives at least equal to the protection required to the shaft enclosure; or 3. be protected by approved fire dampers installed | 711.2 | Extent of Enclosures. Shaft enclosures shall extend from the lowest floor opening through successive floor openings and shall be enclosed at the top and bottom. Exceptions: 1. Shaft extending through or to the underside of the roof sheathing, deck or slab need not be enclosed at the top. 2. Shafts need not be enclosed at the bottom when protected by fire dampers conforming to approved recognized standards, installed at the lowest floor level within the shaft enclosure. Shaft enclosures shall be constructed to continuously maintain the required fire-resistive integrity. | 710.5 | Bottom enclosure. Shafts which do not extend to the bottom of the building shall be enclosed at the lowest level with a fire separation assembly having a fire resistance rating of not less than that required for the shaft enclosure walls, or shall terminate in a room having an occupancy related to the purpose of the shaft. The room shall be separated from the remainder of the building by fire separation assemblies having a fire resistance rating with opening protectives of not less than that required for the shaft enclosure. Exceptions: 1. The fire resistance rated room separation is not required, provided that there are | 705.2.3.3 | Enclosure at bottom. Shafts which do not extend to the bottom of the building or structure shall be enclosed at the lowest level with construction of the same fire resistance as the lowest floor through which the shaft passes, but not less than the rating required for the shaft enclosure, or shall terminate in a room having a use related to the purpose of the shaft. The room shall be separated from the remainder of the building by construction having a fire resistance rating and opening protectives at least equal to the protection required for the shaft enclosure. For shafts containing refuse or laundry chutes, see
|  | in accordance with their listing at the lowest floor level within the shaft enclosure. Exceptions: 1. The fire-resistance-rated room separation is not required provided there are no openings in or penetrations |  | in accordance with their listing at the lowest floor level within the shaft enclosure. Exceptions: 1. The fire-resistance-rated room separation is not required provided there are no openings in or penetrations of the shaft enclosure to the interior of the building except at the bottom. The bottom of the shaft shall be closed off around the penetrating items with materials permitted by Section 716.3.1 for draftstopping, or the room shall be provided with an approved automatic fire-suppression system. 2. A shaft enclosure containing a refuse chute or laundry chute shall not be used for any other purpose and shall |  |  |  | not any openings in or penetrations through the shaft enclosure to the remainder of the building except at the bottom. The bottom of the shaft shall be closed off around the penetrating items with materials permitted by Section 721.3 for draftstopping, or the room shall be equipped throughout with an automatic sprinkler system installed in accordance with Chapter 9. 2. The fire resistance rated room separation and protection at the bottom of the shaft are not required where there are not any combustible materials in the shaft and where there are no any openings in or other penetrations through the shaft enclosure |  | 705.2.4. Exceptions: 1. Fire resistant separation of the room is not required provided there are no openings in or penetrations through the shaft enclosure to the interior of the building except at the bottom of the shaft. The bottom of the shaft shall be closed off around the penetrating items with materials permitted by the code for draft stops, or the room shall be provided with an approved automatic sprinkler system. 2. Fire resistance separation of the room is not required and the bottom of the shaft may be open provided there are no combustibles in the shaft and there are no other openings or
|  |  |  | terminate in a room protected in accordance with Section 707.13.4. 3. The fire-resistance-rated room separation and the protection at the bottom of the shaft are not required provided there are no combustibles in the shaft and there are no openings or other penetrations through the shaft enclosure to the interior of the building. |  |  |  | to the remainder of the building. |  | penetrations through the shaft enclosure to the interior of the building.
707.14.1 | Elevator Lobby | Elevator lobby. Elevators opening into a fire-resistance-rated corridor as required by Section 1016.1 shall be provided with an elevator lobby at each floor containing such a corridor. The lobby shall separate the elevators from the corridor by fire partitions and the required opening protection. Elevator lobbies shall have at least one means of egress complying with Chapter 10 and other provisions within this code. Exceptions: 1. In office buildings, separations are not required from a street-floor elevator lobby provided the entire street floor is equipped with an automatic sprinkler system in accordance with Section 903.3.1.1. | 707.14.1 | Elevator lobby. Elevators opening into a fire-resistance-rated corridor as required by Section 1004.3.2.1 shall be provided with an elevator lobby at each floor containing such a corridor. The lobby shall completely separate the elevators from the corridor by fire barriers and the required opening protection. Elevator lobbies shall have at least one means of egress complying with Chapter 10 and other provision of this code. Exceptions: 1. In office buildings, separations are not required from a street floor elevator lobby provided the entire street floor is equipped with an automatic sprinkler system in accordance with Section 903.3.1.1. 2. Elevators not | 1004.3.4.5 | Elevators. Elevators opening into a corridor shall be provided with an elevator lobby at each floor containing such a corridor. The lobby shall completely separate the elevators from the corridor by construction conforming to Section 1004.3.4.3.1 and all openings into the wall contiguous with the corridor shall be protected as required by Section 1004.3.4.3.2. Exceptions: 1. In office buildings, separations need not be provided from a street floor elevator lobby, provided the entire street floor is protected with an automatic sprinkler system. 2. Elevators not required to meet the shaft enclosure requirements of |  | No related section. | 412.6 | Elevators and elevator lobbies. 412.6.1 All elevators on all floors shall open into elevator lobbies which are separated from the remainder of the building by 1-hour fire resistant construction with 20-minute opening protectives. Exception: 1. Elevator lobbies within an atrium. 2. Where there are open exterior corridors the entire width of the building with stairs located at each end and the elevators are located on the exterior of the building. 3. The main entrance level of the building. 412.6.2 Openings in the elevator lobby shall be limited to those required for access to the elevators and for egress from the
|  | 2. Elevators not required to be located in a shaft in accordance with Section 707.2. 3. Where additional doors are provided in accordance with Section 3002.6. Such doors shall be tested in accordance with UL 1784 without an artificial bottom seal. 4. In other than Group I-3, and buildings more than four stories above the lowest level of fire department vehicle access, lobby separation is not required where the building, including the lobby and corridors leading to the lobby, is protected by an automatic sprinkler system installed throughout in accordance with Section 903.3.1.1 or 903.3.1.2. |  | required to be located in a shaft in accordance with Section 707.2. 3. Where the additional doors are provided in accordance with Section 3002.6. 4. In other than Groups I-2 and I-3, and buildings more than four stories above the lowest level of fire department vehicle access, lobby separation is not required where the building, including the lobby and corridors leading to the lobby, is protected by an automatic sprinkler system installed throughout in accordance with Section 903.3.1.1 or 903.3.1.2. |  | Section 711. 3. Where additional doors are provided in accordance with Section 3007. Elevator lobbies shall comply with the requirements of Section 3002. |  |  |  | building. All rooms and enclosures shall have at least one required exit accessible without travel through the elevator lobby. Openings may be provided with horizontal sliding doors conforming with 1012.4. Exit stairways, chutes, janitor closets, guest rooms, service rooms, etc., shall not open into the elevator lobby. 412.6.3 Each elevator lobby shall be provided with an approved smoke detector located on the lobby ceiling. When the detector is activated, elevator doors shall not open and all cars serving that lobby are to return to the main floor and under manual control only. If the main floor detector or a transfer floor detector is
activated, all cars serving the main floor or transfer floor shall return to a location approved by a fire department and building official and be under manual control only. The detector may serve to close the lobby doors. 412.6.4 Refer to Chapter 30 for general elevator requirements.
715.3.4 | Doors in Vertical Exit Enclosures and Exit Passageways | Doors in vertical exit enclosures and exit passageways. Fire door assemblies in vertical exit enclosures and exit passageways shall have a maximum transmitted temperature end point of not more than 450°F (232°C) above ambient at the end of 30 minutes of standard fire test exposure. Exception: The maximum transmitted temperature end point is not required in buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2. | 714.2.4 | Doors in exit enclosures. Fire door assemblies in exit enclosures shall have a maximum transmitted temperature end point of not more than 450 degrees F (232degreesC) above ambient at the end of 30 minutes of standard fire test exposure. Exception: The maximum transmitted temperature end point is not required in buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2. | 713.3 | Identification of Fire Doors, Fire Windows and Fire Dampers. Fire doors, fire windows and fire dampers shall have an approved label or listing mark, indicating the fire-protection rating, which is permanently affixed at the factory where fabrication and assembly are done. Periodic inspections shall be made by an approved inspection agency during fabrication and assembly. Labels for fire doors used to protect openings into exit enclosures shall indicate that the temperature rise on the unexposed surface does not exceed 450 degrees F (232 degreesC) above ambient at the end of 30 minutes of the fire | 717.1.2 | Doors in exit enclosures. All doorway opening protectives for exit enclosures shall be labeled means of egress fore doors and shall have a maximum transmitted temperature end point of not more than 450 degrees F (232 degrees C) above ambient at the end of 30 minutes of standard fire test exposure. Exception: The maximum transmitted temperature end point is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1 or 906.2.2. | 705.1.3.4 | For 1 1/2 hour and 1 hour doors used in stairway enclosures the average temperature rise developed on the unexposed side shall not exceed 450 degree F (232 degrees C) at the end of 30 minutes of standard fire test exposure.
exposure specified in UBC Standard 7-2 to show compliance with Section 1005.3 Oversized fire doors may be installed when approved by the building official. the doors shall be labeled or be furnished with a certificate of inspection from an approved agency.
715.3.4.1 | Glazing in Doors | Glazing in doors. Fire-protection-rated glazing in excess of 100 square inches (0.065 m2) shall be permitted in fire door assemblies when tested in accordance with NFPA 252 as components of the door assemblies and not as glass lights, and shall have a maximum transmitted temperature end point of 450°F (232°C) in accordance with Section 715.3.4. Exception: The maximum transmitted temperature end point is not required in buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2. | 714.2.4.1 | Glazing in doors. Fire-protection-rated glazing in excess of 100 sq inches (0.065m2) shall be permitted in fire door assemblies when tested in accordance with NFPA 252 as components of the door assemblies and not as glass lights, and shall have a maximum transmitted temperature end point of 450degreesF (232degreesC) in accordance with Section 714.2.4. Exception: The maximum transmitted end point is not required in buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2. | 713.7 | Glazed Openings in Fire Doors. Glazed openings in fire doors shall not be permitted in a fire assembly required to have a three-hour fire-resistive rating. The area of glazed openings in a fire door required to have one- and one-half-hour or one-hour fire-resistive rating shall be limited to 100 sq inches (64500mm2) with a minimum dimension of 4 inches (102mm). When both leaves of a pair of doors have observation panels, the total area of the glazed openings shall not exceed 100 sq inches (64500mm2) for each leaf. Glazed openings shall be limited to 1296 sq inches (0.84m2) in wood and plastic-faced composite or | 717.4 | Glass panels. Fire protection rated glazing shall be permitted in fire door assemblies in accordance with Section 717.0 unless otherwise specifically provided for in this code, and as herein specifically prescribed. | 705.1.3.6 | View panels. View panels. 705.1.3.6.1 1/4-inch (6.4mm) thick wired glass labeled for fire protection purposes may be used in approved opening protectives with the maximum sizes shown in Table 705.1.3.6. Other glazing materials which have been tested and labeled to indicate the type of opening to be protected for fire protection purposes may be used in approved opening protectives in accordance with their listing with the maximum sizes tested. For requirements for safety glazing, see 2405. Table omitted.
[6 empty] | hollow metal doors, per light, when fire-resistive assemblies are required to have a three-fourths-hour fire-resistive rating. |  |  |  | 705.1.3.6.2 View panels in 1-hour fire resistant partitions shall consist of one of the following: 1. 1/4 inch (6.4mm) thick labeled wire glass assemblies installed in steel frames. The wired glass shall be limited to 1296 sq in (0.84m2) with no dimension greater than 54 inches (1372mm). 2. Labeled glass block panels installed in steel channels. The glass block shall be limited to 120 sq ft (11.1m2) with no dimension greater than 12ft (3658mm). 3. Other glazing materials which have been tested and labeled to indicate the type of opening to be protected for fire protection purposes may be used in approved opening protectives in
accordance with their listing with the maximum sizes tested. None of the assemblies shall exceed 25% of the wall area separating each tenant space from corridor. 705.1.3.6.3 View panels shall achieve a minimum fire protection rating of 45 minutes, including fire endurance and hose stream tests in accordance with NFPA 257 under positive pressure. Within the first ten minutes of a test, the pressure in the furnace shall be adjusted so at least 2/3 of the test specimen is above the neutral pressure plane, and the neutral pressure plane shall be maintained at that height for the balance of the test.
716.5.4 | Fire Partitions | Fire partitions. Duct penetrations in fire partitions shall be protected with approved fire dampers installed in accordance with their listing. Exceptions: In occupancies other than Group H, fire dampers are not required where any of the following apply: 1. The partitions are tenant separation and corridor walls in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2 and the duct is protected as a through penetration in accordance with Section 712. 2. The duct system is constructed of approved materials in accordance with the International | 715.5.4 | Fire partitions. Duct penetrations in fire partitions shall be protected with approved fire dampers installed In accordance with their listing. Exceptions: In occupancies other then Group H, fire dampers are not required where any of the following apply: 1. The partitions are tenant separation and corridor walls in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. The duct system is constructed of approved materials in accordance with the IMC and the duct penetrating the wall meets all of the following minimum requirements: 2.1 The duct shall not exceed | 713.11(3) | Penetrations of shaft enclosures. Exceptions: 1. Duct penetrations by steel exhaust air subducts extending vertically upward at least 22inches (559mm) above the top of the opening in a vented shaft where the airflow is upward. 2. Penetrations of a fire-resistive floor forming the base of a shaft enclosure may be protected by fire dampers listed for installation in the horizontal position. | 714.1.5 | Ducts. Ducts that penetrate a wall assembly shall be provided with approved fire dampers that comply with Section 718.0. Exceptions: 1. Fire dampers are not required at penetrations of fire separation assembly walls or fire partitions where: 1.1 Steel exhaust air subducts extend at least 22 inches (559mm) vertically in an exhaust shaft in which there is a continuous air flow upward to the outside. 1.2. Penetrations are tested in accordance with ASTM E 119 listed in Chapter 35 as part of the fire resistance rated assembly. 1.3. Such walls are penetrated by ducted HVAC systems, have a required fire | 705.1.2.2.1 | Fire dampers, installed in accordance with manufacturers installation instructions, shall be provided in ducts penetrating walls or partitions having a fire resistance rating off one hour or more. Exceptions: 1. When the branch ducts connect to return risers in which the air flow is upward and subducts at least 22 inches (559mm) long are carried up inside the riser at each inlet. 2. In duct systems of any duct materials or combinations thereof allowed by Chapter 6 of the Standard Mechanical Code penetrating 1-hour walls or partitions, where the duct penetrating the rated wall or partition meets all of the following
|  | Mechanical Code and the duct penetrating the wall meets all of the following minimum requirements: 2.1. The duct shall not exceed 100 square inches (0.06 m2). 2.2. The duct shall be constructed of steel a minimum of 0.0217 inch (0.55 mm) in thickness. 2.3. The duct shall not have openings that communicate the corridor with adjacent spaces or rooms. 2.4. The duct shall be installed above a ceiling. 2.5. The duct shall not terminate at a wall register in the fire-resistance-rated wall. 2.6. A minimum 12-inch-long (0.30 m) by 0.060-inch-thick (1.52 mm) steel sleeve shall be centered in each duct opening. The sleeve shall be secured to |  | 100 sq inches (0.06m2). 2.2 The duct shall be constructed of steel a minimum of 0.0217inch (0.55mm) in thickness. 2.3 The duct shall not have openings that communicate the corridor with adjacent spaces or rooms. 2.4. The duct shall be installed above a ceiling. 2.5. The duct shall not terminate at a wall register in the fire-resistance-rated wall. |  |  |  | resistance rating of 1 hour or less, are in areas of other than Use Group H and are in buildings equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1. 1.4. The penetrations are in garage exhaust or supply shafts which are separated from all other building shafts by not less than a 2-hour fire resistance rated fire separation assembly. 2. In occupancies in other than Use Group H, fire dampers are not required at the penetration of fire partitions where: 2.1. The partitions are tenant separation and corridor walls in buildings equipped throughout with an automatic sprinkler system in accordance |  | minimum requirements: 1. the duct shall not exceed 100sq in (0.06m2), 2. the duct shall be of 0.0217in (0.55mm) minimum steel, 3. the duct shall continue with no duct openings for not less than 5ft (1.5m) from the rated wall, 4. the duct shall be installed above a ceiling, and 5. the duct does not terminate at a wall register in the rated wall.
|  | both sides of the wall and all four sides of the sleeve with minimum 11/2-inch by 11/2-inch by 0.060-inch (0.038 m by 0.038 m by 1.52mm) steel retaining angles. The retaining angles shall be secured to the sleeve and the wall with No. 10 (M5) screws. The annular space between the steel sleeve and wall opening shall be filled with rock (mineral) wool batting on all sides. | [5 empty] | with Section 906.2.1. 2.2. The partitions are corridor walls and the ducts are constructed of steel and do not have openings which communicate the corridor with adjacent spaces or rooms.
717.3.2 | Groups R-1, R-2, R-3, and R-4 | Groups R-1, R-2, R-3 and R-4. Draftstopping shall be provided in floor/ceiling spaces in Group R-1 buildings, in Group R-2 buildings as applicable in Section 101.2 with three or more dwelling units, in Group R-3 buildings as applicable in Section 101.2 with two dwelling units and in Group R-4 buildings. Draftstopping shall be located above and in line with the dwelling unit and sleeping unit separations. Exceptions: 1. Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 2. Draftstopping is not required in buildings equipped throughout with an automatic | 716.3.2 | Groups R-1, R-2, R-3 and R-4. Draftstopping shall be provided in floor/ceiling spaces in Group R-1 buildings, in Group R-2 buildings as applicable in Section 101.2 with three or more dwelling units, in Group R-3 buildings as applicable in Section 101.2 with two dwelling units and in Group R-4 buildings. Draftstopping shall be located above and in line with the dwelling unit and tenant separations. Exceptions: 1. Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 2. Draftstopping is not required in buildings equipped throughout with an automatic | 708.3.1.1.1 708.3.1.1.2 | 708.3.1.1.1 Single-family dwellings. When there is usable space above and below the concealed space of a floor-ceiling assembly in a single-family dwelling, draft stops shall be installed so that the area of the concealed space does not exceed 1000 sq ft (93m2). Draftstopping shall divide the concealed space into approximately equal areas. 708.3.1.1.2 Two or more dwelling units and hotels. Draft stops shall be installed in floor-ceiling assemblies of buildings having more than one dwelling unit and in hotels. Such draft stops shall be in line with wall separating individual dwelling units and | 721.7.1.1 | Use Groups R-1 and R-2. In occupancies I Use Groups R-1 and R-2, draftstopping shall be installed in line with tenant and dwelling unit separation walls where the walls of not extend to the underside of the floor sheathing above. Exception: Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 906.2.1 or 906.2.1, provided that automatic sprinklers are also installed in the combustible concealed space. | 2305.2.2.2 | Multifamily (two or more) dwellings, motels, hotels. In the floor/ceiling assemblies above and in line with the tenant separation, when tenant separation walls do not extend to the floor sheathing above.????????
|  | sprinkler system in accordance with Section 903.3.1.2, provided that automatic sprinklers are also installed in the combustible concealed spaces. |  | sprinkler system in accordance with Section 903.3.1.2, provided that automatic sprinklers are also installed in the combustible concealed spaces. |  | guest rooms from each other and from other areas.
717.3.3 | Other Groups | Other groups. In other groups, draftstopping shall be installed so that horizontal floor areas do not exceed 1,000 square feet (93 m2). Exception: Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. | 716.3.3 | Other groups. In other groups, draftstopping shall be installed so the horizontal floor areas do not exceed 1000sq ft (93m2). Exception: Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. | 708.3.1.1.3 | Other uses. Draft stops shall be installed in floor-ceiling assemblies of buildings or portions of buildings used for other than dwelling or hotel occupancies so that the area of the concealed space does not exceed 1000 sq ft (93m2) and so that the horizontal dimension between stops does not exceed 60 ft(18288mm). Exception: Where approved automatic sprinklers are installed within the concealed space, the area between draft stops may be 3000 sq ft (279m2) and the horizontal dimension my be 100 ft (30480mm). | 721.7.1.3 | Other use groups. In all other use groups, draftstopping shall be installed so that horizontal areas do not exceed 1000 sq ft (93m2). Exception: Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 906.2.1 or 906.2.2, provided that automatic sprinklers are also installed in the combustible concealed space above the ceiling. | 2305.2.2.3 | Other buildings. In floor/ceiling assemblies so that horizontal areas do not exceed 1000sq ft (92.9m2).??????????
717.4.2 | Groups R-1 and R-2 | Groups R-1 and R-2. Draftstopping shall be provided in attics, mansards, overhangs or other concealed roof spaces of Group R-2 buildings with three or more dwelling units and in all Group R-1 buildings. Draftstopping shall be installed above, and in line with, sleeping unit and dwelling unit separation walls that do not extend to the underside of the roof sheathing above. Exceptions: 1. Where corridor walls provide a sleeping unit or dwelling unit separation, draftstopping shall only be required above one of the corridor walls. 2. Draftstopping is not required in buildings equipped throughout with an automatic sprinkler | 716.4.2 | Groups R-1 and R-2. Draftstopping shall be provided in attics, mansards, overhangs or other concealed roof spaces of Group R-2 buildings with three or more dwelling units and in all Group R-1 buildings. Draftstopping shall be installed above, and in line with, tenant and dwelling unit separation walls that do not extend to the underside of the roof sheathing above. Exceptions: 1. Where corridor walls provide a tenant or dwelling unit separation, draftstopping hall only be required above one of the corridor walls. 2. Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system in accordance with | 708.3.1.2.1 | Two or more dwelling units and hotels. Draft stops shall be installed in the attics, mansards, overhangs, false fronts set out from walls and similar concealed spaces of buildings containing more than one dwelling unit and in hotels. Such draft stops shall be above and in line with the walls separating individual dwelling units and guest rooms from each other and from other uses. Exceptions: Draft stops may be omitted along one of the corridor walls, provided draft stops at walls separating individual dwelling units and guest rooms from each other and from other uses, extend to the | 721.7.2.1 | Use Group R. In occupancies in Use Group R, in attics, mansards, overhangs or other concealed roof spaces, draftstopping shall be installed above, and in line with, tenant and dwelling unit separation walls that do not extend to the underside of the roof sheathing above. Exceptions: 1. Where corridor walls provide a tenant or dwelling unit separation, draftstopping shall only be required above one of the corridor walls. 2. Flat roofs with solid joist construction are not required to be provided with draftstopping over tenant and dwelling unit separation walls if joists form a draftstop. 3. | 2305.2.3 | Attics. 1. Single family dwellings. None required. 2. Multifamily (two or more) dwellings, motels, hotels. In the attic, mansard, overhang, or other concealed roof space above and in line with the tenant separation when tenant separation walls do not extend to the roof sheathing above. Exceptions: Where corridor walls provide a tenant separation, draftstopping shall only be required above on e of the corridor walls. 2. Where flat roofs with solid joist construction are used, draftstopping over tenant separation walls is not required. 3. Where approved sprinklers are provided, draftstopping shall be
|  | system in accordance with Section 903.3.1.1. 3. In occupancies in Group R-2 that do not exceed four stories in height, the attic space shall be subdivided by draftstops into areas not exceeding 3,000 square feet (279 m2) or above every two dwelling units, whichever is smaller. 4. Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.2, provided that automatic sprinklers are also installed in the combustible concealed spaces. |  | 903.3.1.1. 3. In occupancies in Group R-2 that do not exceed four stories in height, the attic space shall be subdivided by draftstops into areas not exceeding 3000sq ft (279m2) or above every two dwelling units, whichever is smaller. 4. Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.2, provided that automatic sprinklers are also installed in the combustible concealed spaced. |  | remaining corridor draft stop. 2. Where approved sprinklers are installed, draftstopping may be as specified in the exception to Section 708.3.1.2.2. |  | Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 906.2.1 or 906.2.2, provided that automatic sprinklers are also installed in attics, mansards, overhangs and other concealed roof spaces of combustible concealed space. 4. Draftstopping is not required in a detached one and two-family dwellings. 5. In occupancies in Use Group R-2 which do not exceed four stories in height, the attic space shall be subdivided by |  | required for areas over 9000sq ft (836m2). 3. Other buildings. In attic spaces so that horizontal areas do not exceed 3000sq ft (279m2). Exceptions: 1. Where flat roofs with solid joist construction are used, draftstopping over tenant separation walls is not required. 2. Where approved sprinklers are provided, the area may be tripled.
draftstops into areas not exceeding 3000sq ft (279m2) or above every two dwelling units, whichever is smaller.
717.4.3 | Other Groups | Other groups. Draftstopping shall be installed in attics and concealed roof spaces, such that any horizontal area does not exceed 3,000 square feet (279 m2). Exception: Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. | 716.4.3 | Other groups. Draftstopping shall be installed in attics and concealed roof spaces, such that any horizontal area does not exceed 3000sq ft (279m2). Exception: Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. | 708.3.1.2.2 | Other uses. Draft stops shall be installed in attics, mansards, overhangs false fronts set out from walls and similar concealed spaces of buildings having uses other than dwellings or hotels, so that the area between draft stops does not exceed 3000 sq ft (279m2) and the greatest horizontal dimension does not exceed 60feet (18288mm). Exception: Where approved automatic sprinklers are installed, the area between draft stops may be 9000 sq ft (836m2) and greatest horizontal dimension may be 100ft (30480mm), | 721.7.2.2 | Other use groups. Draftstopping shall be installed in attics and concealed roof spaces, such that any horizontal area does not exceed 3000sq ft (279m2). Exceptions: 1. Flat roofs with solid joist construction are not required to be provided with draftstopping over tenant separation walls if the joists form a draftstop. 2. Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 906.2.1 or 906.2.2, provided that automatic sprinklers are also installed in attics and other concealed roof spaces of combustible construction. | 2305.2.3.3 | Other buildings. In attic spaces so that horizontal areas do not exceed 3000sq ft (279m2).????????
Table 803.5 | Interior Wall and Ceiling Finish Requirements by Occupancy | Presents finish requirements for sprinklered and non-sprinklered areas based on occupancy group. | Table 803.4 | Same | Table 8-B | Similar; less restrictive for enclosed vertical exitways in I-3 and S. Different for other exitways in A, B, F, H, and I. | Table 803.4 803.4.3 | Similar; BNBC Table 803.4 less restrictive for enclosed exitways for I-3 and different for corridors for A, H, and I-3; 803.4.3 similar to Table 803.4 note c. 803.4.3 Rooms and enclosed spaces. Requirements for rooms or enclosed spaces are based upon spaces enclosed in partitions of the building or structure, and where a fire resistance rating is required for the structural elements, the enclosing partitions shall extend from the floor to the ceiling. Partitions which do not comply with this shall be considered as enclosing spaces and the rooms or spaces on both sides shall be counted as one. In determining the | Table 803.3 | Numerous differences. Separate columns for sprinklered and non-sprinklered facilities.
applicable requirements for rooms or enclosed spaces, the specific occupancy thereof shall be the governing factor, regardless of the use group classification of the building or structure. Where an automatic sprinkler system installed in accordance with Section 906.2.1 or 906.2.2 is installed throughout a building. Class II or III interior finish shall be permitted where Class I or II materials, respectively are required in Table 803.4.
803.6.1 | Textile Wall Coverings | Textile wall coverings. Textile wall coverings shall have a Class A flame spread index in accordance with ASTM E 84 and be protected by automatic sprinklers installed in accordance with Section 903.3.1.1 or 903.3.1.2 or the covering shall meet the criteria of Section 803.6.1.1 or 803.6.1.2 when tested in the manner intended for use in accordance with NFPA 265 using the product mounting system, including adhesive. | 803.5.1 | Textile wall coverings. Textile wall coverings shall have a Class A flame spread index in accordance with ASTM E 84 and be protected by automatic sprinklers installed in accordance with Section 903.3.1.1 or Section 903.3.1.2 or the covering shall meet the criteria of Section 803.5.1.1 or Section 803.5.1.2 when tested in the manner intended for use un accordance with NFPA 265 using the product mounting system, including adhesive. | 805 | When used as interior wall finish, textile wall coverings, including materials such as those having a napped, tufted, looped, non-woven, woven or similar surface shall comply with the following: 1. Textile wall coverings shall have a Class I flame spread and shall be protected by automatic sprinklers complying with UBC Standard 9-1 or 9-3, or 2. The textile wall covering shall meet the acceptance criteria of UBC Standard 8-2 when tested using a product mounting system, including adhesive representative of actual use. | 803.6 | Carpet and carpet-like wall coverings. Textile wall coverings having a napped, tufted, looped, woven, nonwoven or similar surface, shall comply with the following: 1. Such materials shall have a Class I flame spread classification and be installed only in rooms or areas protected by an automatic sprinkler system installed in accordance with Chapter 9; or 2. Such material shall be tested in accordance with an 8-foot by 12-foot by 8-foot high (2438mm by 3658mm by 2438mm) room/corner fire test procedure utilizing a product-mounting system, including adhesive, representative of actual installation. | 803.5.2 | Textile wall coverings, including materials such as those having a napped, tufted, looped nonwoven , woven or similar surface shall comply with one of the following: 1. Textile wall coverings shall have a flamespread index of 25 or less in accordance with ASTM E 84 and shall be protected b automatic sprinklers, or Textile wall coverings shall meet the acceptance criteria specified in 803.5.3 when tested in accordance with NFPA 265 using the product mounting system, including adhesive, of actual use.
Prior to testing, the sample shall be conditioned at 70 degrees F (21 degrees C) +_ 5% and at a relative humidity of 50% +_ 5% until the sample reaches a rate of weight change of less than 0.1% per day. The product shall be exposed to a flame from a gas diffusion burner for 15 minutes. The fire exposure shall be 40kW for the first 5 minutes, followed by an exposure of 150kW for an additional 10 minutes. Such tests shall demonstrate that a product will not spread fire to the edge of the specimen or cause flashover in the test room.
804.5.1 | Minimum Critical Radiant Flux | Minimum critical radiant flux. Interior floor finish in vertical exits, exit passageways and exit access corridors shall not be less than Class I in Groups I-2 and I-3 and not less than Class II in Groups A, B, E, H, I- 4, M, R-1, R-2 and S. In all other areas, the interior floor finish shall comply with the DOC FF-1 “pill test” (CPSC 16 CFR, Part 1630). Exception: Where a building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, Class II materials are permitted in any area where Class I materials are required and materials complying with DOC FF-1 “pill test” (CPSC 16 CFR, Part 1630) are | 804.5.1 | Minimum critical radiant flux. Interior floor finish in vertical units, exit passageways and exit access corridors shall not be less than Class II in Groups A, B, E, H, I-4, M, R-1, R-2 and s. In all other areas, the interior floor finish shall comply with the DOC FF-1 "pill test" (CPSC 16 CFR 1630). Exception: Where a building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, Class II materials are permitted in any area where Class I materials are required and materials complying with DOC FF-1 "pill test" (CPSC 16 CFR 1630) are permitted in any area where Class II materials are required. |  | No related section. | 805.3 | Required classification. Interior floor finish in vertical exits, exit passageways and exit access corridors shall not be less than Class I in Use Group I-2 and not less than Class II in Use Groups A, B, E, I-1, I-3, M, R-1 and R-2. In all other areas, the interior floor finish shall comply with the DOC FF-1 "pill test" (CPSC 16 CFR; 1630) listed in Chapter 35. Exception: Where a building is equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1 or 906.2.2, Class II materials are permitted in any area where Class I materials are required and materials complying with the DOC FF-1 "pill test" | 803.8.2 803.3 | 803.8.2 Carpet materials used on floors of exit access corridors and enclosed exits in other that Group I occupancies shall satisfactorily withstand a minimum critical radiant flux of 0.22watts/cm2 when tested in accordance with the NFPA 253. Exception: Buildings equipped with an approved automatic sprinkler system. 803.3 Interior finish requirements based on
|  | permitted in any area where Class II materials are required. | [5 empty] | (CPSC 16 CFR; 1630) listed in Chapter 35 are permitted in any area where Class II materials are required. |  | occupancy 803.3.1 The minimum flamespread classification of interior finish and floor coverings shall be based on the use or occupancy as set forth in Table 803.3. Exceptions: 1. Except in Group I occupancies and in enclosed vertical exits, Class C interior finish material may be used in access to exits and other spaces as wainscoting extending not more than 48 inches (1219mm) above the floor and for tack and bulletin
boards covering not more than 5% of the gross wall area of the room. In Group I occupancies, Class B interior finish material may be used in access to exits as wainscoting extending not more than 48 inches (1219mm) above the floor. 2. The exposed faces of Type III structural members, including decking and planking, where otherwise permitted by this code, are excluded from flamespread requirements. 3. For churches or places of worship, nothing in this section shall prevent the use of wood for ornamental purposes, trusses, paneling, or chancel furnishing. Table Omitted. 803.3.2 Imitation leather or other material, consisting of, or
coated with a pyroxylin or similarly hazardous base, shall not be used in Group A occupancies.
|  | Section deleted. | 903.1.2 | Residential systems. Unless specifically allowed by this code, residential sprinkler systems installed in accordance with NFPA 13D or NFPA 13R shall not be recognized for the purposes of exceptions or reductions permitted by other requirements of this code. | 904.1.3 | Modifications. When residential sprinkler systems as set forth in UBC Standard 9-3 are provided, exceptions to, or reductions in, code requirements based on the installation of an automatic fire-extinguishing system are not allowed. | 906.2.2 906.2.3 | NFPA 13R systems. In buildings four stories or less in height, systems designed and installed in accordance with NFPA 13R listed in Chapter 35 shall be permitted in Use Group I-1 fire areas in buildings with not more than 16 occupants and Use Group R fire areas. Sprinklers shall not be required in bathrooms that do not exceed 55sq ft (5.12m2) in area and are located within individual dwelling units or guestrooms. 906.2.3 NFPA 13D systems. In Use Group R-3 fire areas with at least 1-hour fire resistance rated fire separation assemblies between dwelling units, or in Use Group I-1 fire areas in buildings with not more than eight | 903.7.6 | Group R2 - Residential occupancy. An approved automatic sprinkler system shall be provided throughout Group R2occupancies three or more stories in height. Exceptions: Three-story buildings which are not required to have an automatic sprinkler system by other provisions of the code and provided with exterior exitway stair complying with 1006.2. 2. An automatic sprinkler system complying with NFPA 13R shall be permitted for buildings not exceeding four stories in height provided the automatic sprinkler system shall not be considered as an alternate to other requirements of the code. See 903.2.
occupants, systems designed and installed in accordance with NFPA 13D listed in Chapter 35 shall be permitted. Exceptions: 1. Sprinklers shall not be required in bathrooms that do not exceed 55ft (5.12m2) in area. 2. A single fire protection water supply shall be permitted to serve not more than eight dwelling units provided that the water supply is increased by 5 gallons per minute (gpm) (18.9L/min) for each dwelling unit served where a common supply serves both the domestic and sprinkler systems in more than one dwelling unit.
903.2 Exception |  | Exception: Spaces or areas in telecommunications buildings used exclusively for telecommunications equipment, associated electrical power distribution equipment, batteries and standby engines, provided those spaces or areas are equipped throughout with an automatic fire alarm system and are separated from the remainder of the building by a wall with a fire-resistance rating of not less than 1 hour and a floor/ceiling assembly with a fire-resistance rating of not less than 2 hours. |  | No related section. |  | No related section. |  | No related section. |  | No related section.
903.2.10.1 | Stories and Basements without Openings | 903.2.10.1 Stories and basements without openings. An automatic sprinkler system shall be installed throughout every story or basement of all buildings where the floor area exceeds 1,500 square feet (139.4m2) and where there is not provided at least one of the following types of exterior wall openings: 1. Openings below grade that lead directly to ground level by an exterior stairway complying with Section 1009 or an outside ramp complying with Section 1010. Openings shall be located in each 50 linear feet (15 240 mm), or fraction thereof, of exterior wall in the story on at least one side. 2. Openings | 903.2.12.1 | Stories and basements without openings. An automatic sprinkler system shall be installed throughout every story or basements of all buildings where the floor area exceeds 1500sq ft (139.4m2) and where there is not provided at least one of the following types of exterior wall openings: 1. Openings below grade that lead directly to ground level by an exterior stairway complying with Section 1003.3.3 or an outside ramp complying with Section 1003.3.4. Openings shall be located in each 50linear feet (15240mm), or fraction thereof, of exterior wall in the story on at least one side. 2. Openings | 904.2.2 | All occupancies except Group R, Division 3 and Group U Occupancies. Except for Group R, Division 3 and Group U Occupancies, an automatic sprinkler system shall be installed: 1. In every story or basement of all buildings when the floor area exceeds 1500 sq ft (139.4m2) and there is not provided at least 20 sq ft (1.86m2) of opening entirely above the adjoining ground level in each 50 lineal ft (15240mm) or fraction thereof of exterior wall in the story or basement on at least one side of the building. Openings shall have a minimum dimension of not less than 30 inches (762mm). Such | 904.11 |  | 903.5.1 | 903.5 General. Approved automatic sprinkler equipment meeting the requirements of 903 shall be installed in buildings as follows: 1. Basements having floor areas exceeding 2500 sq ft (232m2) when used as workshops or for manufacture, repair, sale or storage of combustible materials or when used as lounges or nightclubs regardless of the size. See 503.4.1, Exception 2.
|  | entirely above the adjoining ground level totaling at least 20 square feet (1.86 m2) in each 50 linear feet (15 240 mm), or fraction thereof, of exterior wall in the story on at least one side. |  | entirely above the adjoining ground level totaling at least 20 sq ft (1.86m2) in each 50 linear feet (15240mm), or fraction thereof, of exterior wall in the story on at least one side. |  | openings shall be accessible to the fire department from the exterior and shall not be obstructed in a manner that firefighting or rescue cannot be accomplished from the exterior. When openings in a story are provided on only one side and the opposite wall of such story is more than 75ft(22860mm) from such openings, the story shall be provided with an approved automatic sprinkler system, or openings as specifies above shall be provided on at least two sides of an exterior wall of the story. If any portion of a basement is located more than 75ft(22860mm) from openings required in this section, the
basement shall be provided with an approved automatic sprinkler system. 2. At the top of the rubbish and linen chutes and in their terminal rooms. Chutes extending through three or more floors shall have additional sprinkler heads installed within such chutes at alternate floors. Sprinkler heads shall be accessible for servicing. 3. In rooms where nitrate film is stored or handled. 4. In protected combustible fiber storage vaults as defined in the Fire Code. 5. Throughout all buildings with a floor level with an occupant load of 30 or more that is located 55 feet (16764mm) or more above the lowest level of fire department vehicle
access. Exceptions: 1. Airport control towers. 2. Open parking structures. 3. Group F, Division 2 Occupancies.
903.2.10.1.1 | Opening Dimensions and Access | 903.2.10.1.1 Opening dimensions and access. Openings shall have a minimum dimension of not less than 30 inches (762 mm). Such openings shall be accessible to the fire department from the exterior and shall not be obstructed in a manner that fire fighting or rescue cannot be accomplished from the exterior. | 903.2.12.1.1 | Opening dimensions and access. Openings shall have a minimum dimension of not less than 30 inches (762mm). Such openings shall be accessible to the fire department from the exterior and shall not be obstructed in a manner that fire-fighting or rescue cannot be accomplished from the exterior. | 904.2.2 | All occupancies except Group R, Division 3 and Group U Occupancies. Except for Group R, Division 3 and Group U Occupancies, an automatic sprinkler system shall be installed: 1. In every story or basement of all buildings when the floor area exceeds 1500 sq ft (139.4m2) and there is not provided at least 20 sq ft (1.86m2) of opening entirely above the adjoining ground level in each 50 lineal ft (15240mm) or fraction thereof of exterior wall in the story or basement on at least one side of the building. Openings shall have a minimum dimension of not less than 30 inches (762mm). Such | 904.11 | Other required suppression systems. In addition to the requirements of this section, the sections of this code indicated in Table 904.11 also require the installation of an automatic fore suppression system for certain buildings and areas. | 903.5.2 | In buildings which do not have suitable access, as set forth in 1405, to each story above grade on at least one accessible side of side of the building. Openings which are glazed with security glazing designed to withstand breakage shall not be considered as access openings.
openings shall be accessible to the fire department from the exterior and shall not be obstructed in a manner that firefighting or rescue cannot be accomplished from the exterior. When openings in a story are provided on only one side and the opposite wall of such story is more than 75ft(22860mm) from such openings, the story shall be provided with an approved automatic sprinkler system, or openings as specifies above shall be provided on at least two sides of an exterior wall of the story. If any portion of a basement is located more than 75ft(22860mm) from openings required in this section, the
basement shall be provided with an approved automatic sprinkler system. 2. At the top of the rubbish and linen chutes and in their terminal rooms. Chutes extending through three or more floors shall have additional sprinkler heads installed within such chutes at alternate floors. Sprinkler heads shall be accessible for servicing. 3. In rooms where nitrate film is stored or handled. 4. In protected combustible fiber storage vaults as defined in the Fire Code. 5. Throughout all buildings with a floor level with an occupant load of 30 or more that is located 55 feet (16764mm) or more above the lowest level of fire department vehicle
access. Exceptions: 1. Airport control towers. 2. Open parking structures. 3. Group F, Division 2 Occupancies.
903.2.10.1.2 | Openings on One Side Only | Openings on one side only. Where openings in a story are provided on only one side and the opposite wall of such story is more than 75 feet (22860 mm) from such openings, the story shall be equipped throughout with an approved automatic sprinkler system, or openings as specified above shall be provided on at least two sides of the story. | 903.2.12.1.2 | Openings on one side only. Where openings in a story are provided on only one side and the opposite wall of such story is more than 75ft (22860mm) from such openings, the story shall be equipped throughout with an approved automatic sprinkler system, or openings as specified above shall be provided on at least two sides of the story. | 904.2.2 | All occupancies except Group R, Division 3 and Group U Occupancies. Except for Group R, Division 3 and Group U Occupancies, an automatic sprinkler system shall be installed: 1. In every story or basement of all buildings when the floor area exceeds 1500 sq ft (139.4m2) and there is not provided at least 20 sq ft (1.86m2) of opening entirely above the adjoining ground level in each 50 lineal ft (15240mm) or fraction thereof of exterior wall in the story or basement on at least one side of the building. Openings shall have a minimum dimension of not less than 30 inches (762mm). Such | 904.11 | Other required suppression systems. In addition to the requirements of this section, the sections of this code indicated in Table 904.11 also require the installation of an automatic fore suppression system for certain buildings and areas. | 1405 | Fire Department Access in Exterior Walls 1405.1 General. Exterior walls shall have access openings for fire department use serving each story above grade on an accessible side of the building up to a height of 75ft (22.9 m). Such access openings shall be a minimum of 32 inches (813mm)wide and 48 inches (1219mm) high and with the bottom of the opening not more than 32 inches (813mm) above the floor. Exception: Fire department access to high-piled combustible storage and high-rack storage systems shall be in accordance with Chapter 36 of the Standard Fire Prevention Code.
openings shall be accessible to the fire department from the exterior and shall not be obstructed in a manner that firefighting or rescue cannot be accomplished from the exterior. When openings in a story are provided on only one side and the opposite wall of such story is more than 75ft(22860mm) from such openings, the story shall be provided with an approved automatic sprinkler system, or openings as specifies above shall be provided on at least two sides of an exterior wall of the story. If any portion of a basement is located more than 75ft(22860mm) from openings required in this section, the
basement shall be provided with an approved automatic sprinkler system. 2. At the top of the rubbish and linen chutes and in their terminal rooms. Chutes extending through three or more floors shall have additional sprinkler heads installed within such chutes at alternate floors. Sprinkler heads shall be accessible for servicing. 3. In rooms where nitrate film is stored or handled. 4. In protected combustible fiber storage vaults as defined in the Fire Code. 5. Throughout all buildings with a floor level with an occupant load of 30 or more that is located 55 feet (16764mm) or more above the lowest level of fire department vehicle
access. Exceptions: 1. Airport control towers. 2. Open parking structures. 3. Group F, Division 2 Occupancies.
903.2.10.1.3 | Basements | Basements. Where any portion of a basement is located more than 75 feet (22 860 mm) from openings required by Section 903.2.10.1, the basement shall be equipped throughout with an approved automatic sprinkler system. | 903.2.12.1.3 | Basements. Where any portion of a basement is located more than 75ft (22860mm) from openings required by Section 903.2.12.1, the basement shall be equipped throughout with an approved automatic sprinkler system. | 904.2.2 | All occupancies except Group R, Division 3 and Group U Occupancies. Except for Group R, Division 3 and Group U Occupancies, an automatic sprinkler system shall be installed: 1. In every story or basement of all buildings when the floor area exceeds 1500 sq ft (139.4m2) and there is not provided at least 20 sq ft (1.86m2) of opening entirely above the adjoining ground level in each 50 lineal ft (15240mm) or fraction thereof of exterior wall in the story or basement on at least one side of the building. Openings shall have a minimum dimension of not less than 30 inches (762mm). Such | 904.11 | Other required suppression systems. In addition to the requirements of this section, the sections of this code indicated in Table 904.11 also require the installation of an automatic fore suppression system for certain buildings and areas. | 903.5 | General. Approved automatic sprinkler equipment meeting the requirements of 903 shall be installed in buildings as follows: 1. Basements having floor areas exceeding 2500sq ft (232m2) when used as workshops or for manufacture, repair, sale or storage of combustible materials or when used as lounges or nightclubs regardless of size. See 503.4.1, Exception 2. 2. In buildings which do not have suitable access, as set forth in 1405, to each story above grade on at least one accessible side of the building. Openings which are glazed with security glazing designed to withstand breakage shall not be considered as access
[6 empty] | openings shall be accessible to the fire department from the exterior and shall not be obstructed in a manner that firefighting or rescue cannot be accomplished from the exterior. When openings in a story are provided on only one side and the opposite wall of such story is more than 75ft(22860mm) from such openings, the story shall be provided with an approved automatic sprinkler system, or openings as specifies above shall be provided on at least two sides of an exterior wall of the story. If any portion of a basement is located more than 75ft(22860mm) from openings required in this section, the |  |  |  | openings. 3. See Chapter 36, Standard Fire Prevention Code. 4. See 407.1.3, 411.7.6 and 411.7.7. 5. Spray finishing booth, area or room shall comply with Chapter 10 of the Standard Fire Prevention Code.
basement shall be provided with an approved automatic sprinkler system. 2. At the top of the rubbish and linen chutes and in their terminal rooms. Chutes extending through three or more floors shall have additional sprinkler heads installed within such chutes at alternate floors. Sprinkler heads shall be accessible for servicing. 3. In rooms where nitrate film is stored or handled. 4. In protected combustible fiber storage vaults as defined in the Fire Code. 5. Throughout all buildings with a floor level with an occupant load of 30 or more that is located 55 feet (16764mm) or more above the lowest level of fire department vehicle
access. Exceptions: 1. Airport control towers. 2. Open parking structures. 3. Group F, Division 2 Occupancies.
905.3.1 | Building Height | 905.3.1 Building height. Class III standpipe systems shall be installed throughout buildings where the floor level of the highest story is located more than 30 feet (9144 mm) above the lowest level of fire department vehicle access, or where the floor level of the lowest story is located more than 30 feet (9144mm) below the highest level of fire department vehicle access. Exceptions: 1. Class I standpipes are allowed in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. 2. Class I manual standpipes are allowed in open parking garages where the highest floor is | 905.3.1 | Building Height. Class III standpipe systems shall be installed throughout buildings where the floor level of the highest story is located more than 30ft (9144mm) above the lowest level of the fire department vehicle access, or where the floor level of the lowest story is located more than 30ft (9144mm) below the highest level of fire department vehicle access. Exceptions: 1. Class I standpipes are allowed in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. 2. Class I manual standpipes are allowed in open parking garages where the highest floor is located not more than | 904.5.2 | Where required. Standpipe systems shall be provided as set forth in Table 9-A. | 915.2.1 | Building height. Standpipe systems shall be installed throughout all buildings in which the floor level of the highest story is located more than 30ft (9144mm) above the lowest level of the fire department vehicle access or in which the floor level of the lowest story is located more than 30ft (9144mm) below the highest level of fire department vehicle access. | 904.2.1 | Standpipes shall be provided in all buildings in which the highest floor is greater than 30ft (9144mm) above the lowest level of fire department vehicle access. Exception: Standpipes are not required in Group R3 buildings.
|  | located not more than 150 feet (45 720 mm) above the lowest level of fire department vehicle access. 3. Class I manual dry standpipes are allowed in open parking garages that are subject to freezing temperatures, provided that the hose connections are located as required for Class II standpipes in accordance with Section 905.5. 4. Class I standpipes are allowed in basements equipped throughout with an automatic sprinkler system. |  | 150ft (45720mm) above the lowest level of fire department vehicle access. 3. Class I manual dry standpipes are allowed in open parking garages that are subject to freezing temperatures, provided that the hose connections are located as required for Class II standpipes in accordance with Section 905.5. 4. Class I standpipes are allowed in basements equipped throughout with an automatic sprinkler system.
|  | Section deleted. | 905.3.2 | Building area. In buildings exceeding 10000sq ft (929m2) in area per story, Class I automatic wet or manual wet standpipes shall be provided where any portion of the building's interior area is more than 200ft (60960mm) of travel, vertically and horizontally, from the nearest point of fire department vehicle access. Exceptions: Buildings equipped throughout with automatic sprinkler systems installed in accordance with Section 903.3.1.1. 2. Group A-4, A-5, F-2, R-2, S-2 or U occupancies. 3. Automatic dry and semiautomatic dry standpipe are allowed as provided for in NFPA 14. |  | No related section. | 915.2.2 | Building area. Standpipe systems shall be installed in all buildings where any portion of the building floor area is more than 400ft (122m) of travel from the nearest point of fire department vehicle access. Exceptions: 1. Buildings equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1 or 906.2.2. 2. Occupancies in Use Group A-4, A-5, F-2, R-2, S-2 or U. 3. Buildings less than 10000sq ft (930m2). | 904.2.2 | Standpipes shall be provided in buildings in which the highest floor is 30ft (9144mm) or less above the lowest level of fire department vehicle access and exceeding 10000sq ft (929m2) in area per story when any portion of the building's interior area is more than 200ft (61m) of travel from the nearest point of fire department vehicle access. Exceptions: 1. Standpipes are not required in Group R2 with 8 units are less, R3 and S2 occupancies. 2. Standpipes are not required in buildings protected throughout with automatic sprinklers installed in accordance with NFPA 13.
905.5.2 | Protection | Protection. Fire-resistance-rated protection of risers and laterals of Class II standpipe systems is not required. | 905.5.2 | Protection. Fire-resistance-rated protection of risers and laterals of Class II standpipe systems is not required. | 904.5.4 | Location of Class II standpipes. Class II standpipe outlets shall be accessible and shall be located so that all portions of the building are within 30ft(9144mm) of a nozzle attached to 100ft(30480mm) of hose. In Group A, Divisions 1 and 2.1 Occupancies, with occupant loads of more than 1000, outlets shall be located on each side of any stage, on each side of the rear of the auditorium and on each side of the balcony. Fire-resistant protection of risers and laterals of Class II standpipe systems is not required. | 915.7.4 | Protection of risers. Risers and laterals of standpipe systems of the types complying with Section 915.3, item 2 or 3, and not located within a fire resistance rated exit enclosure shall be enclosed by construction having a minimum fire resistance rating equal to that required for shaft enclosures in the building. Exception: Buildings equipped throughout with an automatic sprinkler system in accordance with Sections 906.2.1 or 906.2.2. |  | No related section.
905.6.1 | Protection | Protection. Risers and laterals of Class III standpipe systems shall be protected as required for Class I systems in accordance with Section 905.4.1. | 905.6.1 | Protection. Risers and laterals of Class III standpipe systems shall be protected as required for Class I systems in accordance with Section 905.4.1. | 904.5.5 | Location of Class III standpipes. Class III standpipe systems shall have outlets located as required for Class I standpipes in Section 904.5.3 and shall have Class II outlets as required in Section 904.5.4. Risers and laterals of Class III standpipe systems shall be protected as required for Class I systems. Exceptions: 1. In buildings equipped with an approved automatic sprinkler system, risers and laterals that are not located within an enclosed stairway or pressurized enclosure need not be enclosed within fire-resistive construction. 2. Laterals for Class II outlets on Class III systems need not be protected. In buildings | 915.7.4 | Protection of risers. Risers and laterals of standpipe systems of the types complying with Section 915.3, item 2 or 3, and not located within a fire resistance rated exit enclosure shall be enclosed by construction having a minimum fire resistance rating equal to that required for shaft enclosures in the building. Exception: Buildings equipped throughout with an automatic sprinkler system in accordance with Sections 906.2.1 or 906.2.2. |  | No related section.
where more than one Class III standpipe is provided, the standpipes shall be interconnected at the bottom.
905.8 | Dry Standpipe | Dry standpipes. Dry standpipes shall not be installed. Exception: Where subject to freezing and in accordance with NFPA 14. | 905.8 | Dry standpipe. In buildings requiring standpipes, dry standpipes complying with NFPA 14 are permitted when, in the opinion of the building official, an approved water supply is not available or when the standpipe is subject to freezing. |  | No related section. | 915.3.1 | Type of system required. Buildings required by Section 915.2 to be equipped with standpipe systems shall be provided with a wet standpipe system that complies with Section 915.3, item 1. Exceptions: 1. Buildings in which the highest floor is located not more than 75ft (22860mm) above the lowest level of fire department vehicle access, shall be permitted to use a standpipe system that complies with Section 915.3, item 2 or 3. 2. Buildings which are equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1 and in which the highest floor is located not more than 150ft (45720mm) | 904.3.5 | In buildings requiring standpipes in accordance with 904.2, dry standpipes having no permanent water supply may be installed when in the opinion of the building official and the fire official, a constant and automatic water supply is not necessary.
above the lowest level of fire department vehicle access, shall be permitted to use a standpipe system complying with Section 915.3, item 2 or 3. 3. Open parking structures in which the highest floor is located not more than 150ft (45720mm) above the lowest level of fire department vehicle access, shall be permitted to use a standpipe system complying with Section 915.3, item 2, 3, or 4.
907.2.1 | Group A | Group A. A manual fire alarm system shall be installed in accordance with NFPA 72 in Group A occupancies having an occupant load of 300 or more. Portions of Group E occupancies occupied for assembly purposes shall be provided with a fire alarm system as required for the Group E occupancy. Exception: Manual fire alarm boxes are not required where the building is equipped throughout with an automatic sprinkler system and the notification appliances will activate upon sprinkler water flow. | 907.2.1 | Group A. A manual fire alarm system shall be installed in accordance with NFPA 72 in Group A occupancies having an occupant load of 300 or more. Portions of Group E occupancies occupied for assembly purposes shall be provided with a fire alarm as required for Group E occupancy. Exception: Manual fire alarm boxes are not required where the building is equipped throughout with an automatic sprinkler system and the notification appliances will activate upon sprinkler water flow. | 303.9 | Fire Alarm Systems. An approved fire alarm system shall be installed as set forth in the Fire Code in Group A, Division 1, 2 and 2.1 Occupancies. For amusement building alarm systems, see Section 408.5.1. | 918.4.1 | Use Group A-4 or E. A fire alarm system shall be installed and maintained in all occupancies in group A-4 or E. A fire alarm system shall not be required for sanctuary or nave areas of churches and similar religious buildings. | 905.1.1 | General. A fire alarm system in accordance with NFPA 72 shall be installed in all the following occupancies: Group A having an occupant load of 1000 persons or more. Group B having an occupant load of 500 or more persons or more than 100 persons above or below the street floor. Group E. Group F two stories or more in height, and having an occupant load of 500 or more persons above or below the street floor level. Group H. Group I. Group M having an occupant load of 500 or more persons or more than 100 persons above or below the street floor level. group R. R1 Occupancies having
accommodations for more than 15 guests. R2 Apartment houses four or more stories in height, and dormitories or rooming houses (not transient) having more than 15 sleeping accommodations. R4 occupancies. Exceptions: 1. Group R1 and R2. Where each guest room in R1 occupancies, dormitories and rooming houses has a direct exit to the outside of the building and the building is three stories or less in height. 2. Groups A, B, E, F, H, M, and R1, R2, R3, and R4 Small Facilities. The manual fire alarm boxes required in 905.1 may be omitted in buildings meeting all of the following requirements: 1. The
building is equipped with automatic fire detection or automatic sprinkler system covering all areas. 2. Actuation of the automatic sprinkler system will activate the fire alarm system. 3. Provisions are made to manually activate the fire alarm system at a minimum of one centrally located station.
907.2.1.1 | System Initiation in Group A Occupancies with an Occupant Load of 1,000 or More | 907.2.1.1 System initiation in Group A occupancies with an occupant load of 1,000 or more. Activation of the fire alarm in Group A occupancies with an occupant load of 1,000 or more shall initiate a signal using an emergency voice/alarm communications system in accordance with NFPA 72. Exception: Where approved, the prerecorded announcement is allowed to be manually deactivated for a period of time, not to exceed 3 minutes, for the sole purpose of allowing a live voice announcement from an approved, constantly attended location. | 907.2.1.1 | System initiation in Group A occupancies with an occupant load of 1000 or more. Activation of the fire alarm in group A occupancies with an occupant load of 1000 or more shall initiate a signal using an emergency voice/alarm communications system in accordance with NFPA 72. Exception: Where approved, the prerecorded announcement is allowed to be manually deactivated for a period of time, not to exceed 3 minutes, for the sole purpose of allowing a live voice announcement from an approved, constantly attended location. | 303.9 | Fire Alarm Systems. An approved fire alarm system shall be installed as set forth in the Fire Code in Group A, Division 1, 2 and 2.1 Occupancies. For amusement building alarm systems, see Section 408.5.1. |  | No related section. | 905.1.1 | General. A fire alarm system in accordance with NFPA 72 shall be installed in all the following occupancies: Group A having an occupant load of 1000 persons or more. Group B having an occupant load of 500 or more persons or more than 100 persons above or below the street floor. Group E. Group F two stories or more in height, and having an occupant load of 500 or more persons above or below the street floor level. Group H. Group I. Group M having an occupant load of 500 or more persons or more than 100 persons above or below the street floor level. group R. R1 Occupancies having
accommodations for more than 15 guests. R2 Apartment houses four or more stories in height, and dormitories or rooming houses (not transient) having more than 15 sleeping accommodations. R4 occupancies. Exceptions: 1. Group R1 and R2. Where each guest room in R1 occupancies, dormitories and rooming houses has a direct exit to the outside of the building and the building is three stories or less in height. 2. Groups A, B, E, F, H, M, and R1, R2, R3, and R4 Small Facilities. The manual fire alarm boxes required in 905.1 may be omitted in buildings meeting all of the following requirements: 1. The
building is equipped with automatic fire detection or automatic sprinkler system covering all areas. 2. Actuation of the automatic sprinkler system will activate the fire alarm system. 3. Provisions are made to manually activate the fire alarm system at a minimum of one centrally located station.
907.2.2 | Group B | Group B. A manual fire alarm system shall be installed in Group B occupancies having an occupant load of 500 or more persons or more than 100 persons above or below the lowest level of exit discharge. Exception: Manual fire alarm boxes are not required where the building is equipped throughout with an automatic sprinkler system and the alarm notification appliances will activate upon sprinkler water flow. | 907.2.2 | Group B. A manual fire alarm system shall be installed in Group B occupancies having an occupant load of 500 or more persons or more than 100 persons above or below the lowest level of exit discharge. Exception: Manual fire alarm boxes are not required where the building is equipped throughout with an automatic sprinkler system and the alarm notification appliances will activate upon sprinkler water flow. |  | No related section. | 918.4.2 | Use Group B. A fire alarm system shall be installed and maintained in all occupancies in Use Group B where such buildings have occupied floors which are two or more stories above the lowest level of exit discharge or which floors two or more stories below the highest level of exit discharge. | 905.1.1 | General. A fire alarm system in accordance with NFPA 72 shall be installed in all the following occupancies: Group A having an occupant load of 1000 persons or more. Group B having an occupant load of 500 or more persons or more than 100 persons above or below the street floor. Group E. Group F two stories or more in height, and having an occupant load of 500 or more persons above or below the street floor level. Group H. Group I. Group M having an occupant load of 500 or more persons or more than 100 persons above or below the street floor level. group R. R1 Occupancies having
accommodations for more than 15 guests. R2 Apartment houses four or more stories in height, and dormitories or rooming houses (not transient) having more than 15 sleeping accommodations. R4 occupancies. Exceptions: 1. Group R1 and R2. Where each guest room in R1 occupancies, dormitories and rooming houses has a direct exit to the outside of the building and the building is three stories or less in height. 2. Groups A, B, E, F, H, M, and R1, R2, R3, and R4 Small Facilities. The manual fire alarm boxes required in 905.1 may be omitted in buildings meeting all of the following requirements: 1. The
building is equipped with automatic fire detection or automatic sprinkler system covering all areas. 2. Actuation of the automatic sprinkler system will activate the fire alarm system. 3. Provisions are made to manually activate the fire alarm system at a minimum of one centrally located station.
907.2.3 | Group E | Group E. A manual fire alarm system shall be installed in Group E occupancies. When automatic sprinkler systems or smoke detectors are installed, such systems or detectors shall be connected to the building fire alarm system. Exceptions: 1. Group E occupancies with an occupant load of less than 50. 2. Manual fire alarm boxes are not required in Group E occupancies where all the following apply: 2.1. Interior corridors are protected by smoke detectors with alarm verification. 2.2. Auditoriums, cafeterias, gymnasiums and the like are protected by heat detectors or other approved detection devices. 2.3. | 907.2.3 | Group E. A manual fire alarm system shall be installed in group E occupancies. When automatic sprinkler systems or smoke detectors are installed, such systems or detectors shall be connected to the building alarm system. Exceptions: 1. Group E occupancies with an occupant load of less than 50. 2. Manual fire alarm boxes are not required in Group E occupancies where all of the following apply: 2.1. Interior corridors are protected by smoke detectors with alarm verification. 2.2. Auditoriums, cafeterias, gymnasiums and the like are protected by heat detectors or other approved detection devices. 2.3. Shops and | 305.9 | Fire Alarm Systems. An approved fire alarm system shall be provided for Group E Occupancies with an occupant load of 50 or more persons. In Group E Occupancies provided with an automatic sprinkler or detection system, the operation of such system shall automatically activate the school fire alarm system, which shall include an alarm mounted on the exterior of the building. See Chapter 10 for smoke-detection requirements. For installation requirements, see the Fire Code. | 918.4.1 | Use Group A-4 or E. A fire alarm system shall be installed and maintained in all occupancies in group A-4 or E. A fire alarm system shall not be required for sanctuary or nave areas of churches and similar religious buildings. | 905.1 | Manual fire alarm systems 905.1.1 General A fire alarm system in accordance with NFPA 72 shall be installed in all of the following occupancies: Group A having an occupant load of 1000 persons or more. Group B having an occupant load of 500 or more persons or more than 100 persons above or below the street floor. Group E. Group F two stories or more in height, and having an occupant load of 500 or more persons above or below the street floor level. Group H. Group I. Group M having an occupant load of 500 or more persons or more than 100 persons above or below the street floor level. Group R. R1
|  | Shops and laboratories involving dusts or vapors are protected by heat detectors or other approved detection devices. 2.4. Off-premises monitoring is provided. 2.5. The capability to activate the evacuation signal from a central point is provided. 2.6. In buildings where normally occupied spaces are provided with a two-way communication system between such spaces and a constantly attended receiving station from where a general evacuation alarm can be sounded, except in locations specifically designated by the building official. |  | laboratories involving dusts or vapors are protected by heat detectors or other approved detection devices. 2.4. Off-premises monitoring is provided. 2.5. The capability to activate the evacuation signal from a central point is provided. 2.6. IN buildings where normally occupied spaces are provided with a two-way communication system between such spaces and constantly attended receiving station from where a general evacuation alarm can be sounded, except in locations specifically designated by the building official. | [5 empty] | occupancies having accommodations for more than 15 guests. R2 Apartment houses four or more stories in height, and dormitories or rooming houses (not transient) having more than 15 sleeping accommodations. R4 occupancies. Exceptions: Group R1 and R2. Where each guest room in R1 occupancies, dormitories and rooming houses has a direct exit to the outside of the building and the building is three stories or less in height. 2. Groups A, B, E, F, H, M and R1, R2, R3, and R4 Small Facilities. The manual fire alarm boxes required in 905.1 may be omitted in buildings meeting all of the following
requirements: 1. The building is equipped with an automatic fire detection or automatic sprinkler system covering all areas. 2. Actuation of the automatic fire detection or automatic sprinkler system will activate the fire alarm. 3. Provisions are made to manually activate the fire alarm system at a minimum of one centrally located station. 905.1.2 Manual fire alarm boxes shall be located
not more than 5ft (1524mm) from the entrance to each exit. 905.1.3 Each floor shall be zoned separately. No one zone may exceed 15000sq ft (1394m2). A zone indicator panel shall be located at grade level at the normal point of fire department access or at a constantly attended building security control center. Exception: Automatic sprinkler system zones shall not exceed the area permitted by NFPA 13. 905.1.4 Upon completion of the fire alarm system, all alarm initiating devices and circuits, alarm indicating appliances and circuits, supervisory signal initiating devices and circuits, signaling line circuits,
and primary and secondary power supplies shall be subjected to a 100% acceptance test in accordance with NFPA 72. 905.1.5 Alarm indicating appliances 905.1.5.1 Required. Alarm indicating appliances listed for purpose shall be provided. 905.1.5.2 Visible and audible alarm indicating appliances shall be provided in occupancies housing the hearing impaired, Every required fire alarm system shall include visible alarm indicating appliances in public and common areas. 905.1.5.3 Activation The alarm indicating appliances shall be automatically activated by all of the following where provided: 1. Smoke
detectors, other than single-station or multiple-station smoke detectors, as required by 905.2. Activation of the alarm system by smoke detectors shall be by either two cross-zoned smoke detectors within a single protected area or a single smoke detector monitored by an alarm verification zone or an approved equivalent method. 2. Sprinkler water-flow devices; 3. Manual fire alarm boxes; and 4. Other approved types of automatic fire detection device suppression systems. 905.1.5.4 Audible Alarms. Audible alarm indicating appliances shall provide a distinctive sound which shall not be
used for any purpose other than that of a fire alarm. Such devices shall provide a sound pressure level of 15dBA above the average ambient sound level in every occupied space within the building. The minimum sound pressure levels shall be: 70dBA in buildings of Group R occupancy, 90dBA in mechanical equipment rooms; and 60dBA in all other occupancy classifications. The maximum sound pressure level for audible alarm indicating the appliances shall not exceed 130dBA at the minimum hearing distance from the audible appliance. 905.1.5.5 Visible Alarms. Visible alarm indicating appliances,
where required, shall be so located as to notify all occupants in every occupied space within the building.
907.2.4 | Group F | Group F. A manual fire alarm system shall be installed in Group F occupancies that are two or more stories in height and have an occupant load of 500 or more above or below the lowest level of exit discharge. Exception: Manual fire alarm boxes are not required if the building is equipped throughout with an automatic sprinkler system and the notification appliances will activate upon sprinkler water flow. | 907.2.4 | Group F. A manual fire alarm system shall be installed in Group F occupancies that are two or more stories in height and have an occupant load of 500 or more above or below the lowest level of discharge. Exception: Manual fire alarm boxes are not required if the building is equipped throughout with an automatic sprinkler system and the notification appliances will activate upon sprinkler water flow. |  | No related section. |  | No related section. |  | Similar; exceptions made for sprinklers and detection that sound alarm.
907.2.5 | Group H | Group H. A manual fire alarm system shall be installed in Group H-5 occupancies and in occupancies used for the manufacture of organic coatings. An automatic smoke detection system shall be installed for highly toxic gases, organic peroxides and oxidizers in accordance with Chapters 37, 39 and 40, respectively, of the International Fire Code. | 907.2.5 | Group H. A manual fore alarm system shall be installed in Group H-5 occupancies and in occupancies used for the manufacture of organic coatings. An automatic smoke detection system shall be installed for highly toxic gases, organic peroxides and oxidizers in accordance with Chapters 37, 39, and 40 respectively of the IFC. | 307.9 307.11 5.5???????????? | 307.9 Fire Alarm Systems. An approved manual fire alarm system shall be provided in Group H Occupancies used for the manufacturing of organic coatings. Approved automatic smoke detection shall be provided for rooms used for storage, dispensing, use and handling of hazardous materials when required by the Fire Code. For Group H, Division 6 Occupancies, see Section 307.11. For installation requirements, see the Fire Code. For aerosol storage warehouses, see the Fire Code. 307.11 Group H, Division 6 Occupancies. 307.11.1 General | 918.4.3 417.5.3 | Use Group H. A fire alarm system shall be installed and maintained in all occupancies in Use Groups H-2, H-3 and H-4. 417.5.3. Detection systems. All occupancies in Use Group H shall be provided with an automatic fire detection system in accordance with NFPA 72 listed in Chapter 35 where required by the fire prevention code listed in Chapter 35. The detection system shall be provided in the areas where then hazardous materials are utilized and stored. | 905.1.1 | General. A fire alarm system in accordance with NFPA 72 shall be installed in all the following occupancies: Group A having an occupant load of 1000 persons or more. Group B having an occupant load of 500 or more persons or more than 100 persons above or below the street floor. Group E. Group F two stories or more in height, and having an occupant load of 500 or more persons above or below the street floor level. Group H. Group I. Group M having an occupant load of 500 or more persons or more than 100 persons above or below the street floor level. group R. R1 Occupancies having
[6 empty] | In addition to the requirements set forth elsewhere in this code, Group H, Division 6 occupancies shall comply with the provisions of this section and the Fire Code. 307.11.2 Fabrication area. 307.11.2.1 Separation and location. Fabrication areas, whose sizes are limited by the quantity of hazardous production materials, (HPM) permitted by the Fire Code, shall be separated from each other, from corridors, and from other parts of the building by not less than one-hour fire-resistive occupancy separations. Occupied levels of fabrication areas shall be located at or above the first story. Exceptions: 1. Doors within such |  |  |  | accommodations for more than 15 guests. R2 Apartment houses four or more stories in height, and dormitories or rooming houses (not transient) having more than 15 sleeping accommodations. R4 occupancies. Exceptions: 1. Group R1 and R2. Where each guest room in R1 occupancies, dormitories and rooming houses has a direct exit to the outside of the building and the building is three stories or less in height. 2. Groups A, B, E, F, H, M, and R1, R2, R3, and R4 Small Facilities. The manual fire alarm boxes required in 905.1 may be omitted in buildings meeting all of the following requirements: 1. The
[6 empty] | occupancy separation, including doors to corridors, shall be only self-closing fire assemblies having a fire-protection rating of not less than three-fourths hour. 2. Windows between fabrication areas and corridors may be in accordance with Section 1004.3.4.3.2.2. 307.11.2.2. Except for surfacing, floors within fabrication areas shall be of noncombustible construction. Openings through floors of fabrication areas may be unprotected when the interconnected levels are used solely for mechanical equipment directly related to such fabrication area. See also Section 307.11.2.3. When forming a part of any occupancy separation, floors |  |  |  | building is equipped with automatic fire detection or automatic sprinkler system covering all areas. 2. Actuation of the automatic sprinkler system will activate the fire alarm system. 3. Provisions are made to manually activate the fire alarm system at a minimum of one centrally located station. 905.1.2 Manual fire alarm boxes shall be located not more than 5ft (1524mm) from the entrance to each exit. 905.1.3 Each floor shall be zoned separately. No one zone may exceed 15000 sq ft (1394m2). A zone indicator panel shall be located at grade level at the normal point of fire department access or
[6 empty] | shall be liquid tight. 307.11.2.3 Shaft and exit enclosures. Exits shall be enclosed as specified in Chapter 10. Elevator shafts, vent shafts and other openings through floors shall be enclosed and the enclosure shall be as specified in Section 711. A fabrication area may have mechanical, duct and piping penetrations for cables, cable trays, tubing, piping, conduit or ducts shall be sealed at the floor level to restrict the movement of air. The fabrication area, including the areas through which the ductwork and piping extend, shall be considered a single conditioned environment. 307.11.2.4 Ventilation. See |  |  |  | at a constantly attended building control center. Exception: Automatic sprinkler system zones shall not exceed the area permitted by NFPA 13. 905.1.4 Upon completion of the fire alarm system, all alarm initiating devices and circuits, alarm indicating appliances and circuits, supervisory signal initiating devices and circuits, signaling line circuits, and primary and secondary power supplies shall be subjected to a 100% acceptance test in accordance with NFPA 72.
Section 1202.2.5 for ventilation requirements. 307.11.2.5 Transporting hazardous production materials. Hazardous production materials shall be transported to fabrication areas through enclosed piping or tubing systems that comply with Section 307.11.6, through service corridors or in corridors as permitted in the exception to Section 307.11.3. The handling or transporting of hazardous production materials within service corridors shall comply with the Fire Code. 307.11.2.6 Electrical. Electrical equipment and devices within the fabrication area shall comply with the Electrical Code. The
requirements for hazardous locations need not be applied when the average air change is at least four times that set forth in Section 307.11.2.4 and when the number of air changes at any location is not less than three times that required by Section 307.11.2.4 and the Fire Code. Electrical equipment and devices within 5ft (1524mm) of workstations in which flammable or pyrophoric gases or flammable liquids are used shall be in accordance with the Electrical Code for Class I, Division 2 hazardous locations. Work stations shall not be energized without adequate exhaust ventilation. See Section 1202.2.5
for work station exhaust ventilation requirements. Exception: Class I, Division 2 hazardous electrical is not required when the air removal from the work station or dilution will provide nonflammable atmospheres on a continuous basis. 307.11.3 Corridors. Corridors shall comply with Section 1004.3.4 and shall be separated from fabrication areas specified in Section 307.11.2.1. Corridors shall not be used for transporting hazardous production materials except as provided in Section 307.11.6.2. Exception: In existing Group H, Division 6 Occupancies when there are alterations or modifications to existing fabrication
areas, the building official may permit the transportation of hazardous production materials in corridors subject to the requirements of the Fire Code and as follows: 1. Exit-access corridors adjacent to the fabrication area where the alteration work is to be done shall comply with Section 1004.3.4 for a length determined as follows: 1.1 The length of the common wall of the corridor and the fabrication area, and 1.2 For the distance along the corridor to the point of entry of HPM into the corridor serving that fabrication area. 2. There shall be an emergency telephone system or a local alarm manual pull station or approved
signal device within corridors ar not more than 150-foot (45720mm) intervals or fraction thereof and each stair doorway. The signal shall be relayed to the emergency control station and a local signaling device shall be provided. 3. Sprinkler protection shall be designed in accordance with UBC Standard 9-1 for Ordinary Hazard Group 3, except that when one row of sprinklers is used in the corridor protection, the maximum number of sprinkler that need to be calculated is 13. UBC Standard 9-1 is aprt of this code. (See Chapter 35, Part II.) 4. Self-closing doors having a fire protection rating of not less than one hour shall separate pass-throughs from existing corridors. Pass-throughs shall be constructed as required for the corridors. Pass-throughs shall be protected by an approved automatic fire sprinkler system.307.11.4 Service Corridors. Service corridors Shall be classified as Group H, Division 6 Occupancies. Service corridors shall be separated from corridors as required by Section 307.11.2.1. Service corridors shall be mechanically ventilated as required by Section 307.11.2.4 or at not less than six air changes per hour, whichever is greater. The maximum travel distance from any point in a service corridor to an exit or door into fabrication area shall not exceed 4ft (1219mm) in length. There shall not be less than two means of egress, and not more than one half of the required means of egress shall be into the fabrication area. Doors from service corridors shall swing in the direction of egress and shall be self-closing. The minimum clear width of a service corridor shall be 5ft (1524mm), or 33inches (838mm) wider than the widest cart or truck used in the corridor, whichever is greater. 307.11.5 Storage of hazardous production materials. 307.11.5.1 Construction. The storage of hazardous production materials in quantities greater than those listed in Table 3-D or 3-E shall be in liquid storage rooms, HPM rooms or gas rooms, as required by the Fire Code. HPM rooms and gas rooms shall be separated from all other areas by not less than a two-hour fire-resistive occupancy separation when the area is 300 square feet (27.9m2) or more and not less than one-hour fire-resistive occupancy separation when the area is less than 300sq ft (27.9m2). The provisions of Section 302.1 shall apply. Except for surfacing, floors of storage and HPM rooms shall be of noncombustible liquid-tight construction. Raised grating over floors shall be of noncombustible materials. See Section 307.2.3 for sill requirements for liquid storage rooms. 307.11.5.2 Location within building. When HPM rooms are provided, they shall have at least one exterior wall and such wall shall not be less than 30ft (9144mm) from property lines, including property lines adjacent to public ways. Expolsion control shall be provided when required by Section 307.10. 307.11.5.3 Means of egress. When two means of egress are required from HPM rooms, one shall be directly to the outside of the building. See Section 307.11.2.1, Exception 1. 307.11.5.4 Ventilation. Mechanical exhaust ventilation shall be provided in liquid storage rooms, HPM rooms and gas rooms at the rate of not less than 1 cubic foot per minute per square foot (0.044L/s/m2) of floor area or six air changes per hour, whichever is greater, for all categories of material. Exhaust ventilation for gas rooms shall be designed to operate at a negative pressure in relation to the surrounding areas and direct the exhaust ventilation to an exhaust system. 307.11.5.5 Fire and emergency alarm. An approved manual fire alarm system shall be provided throughout buildings containing Group H, Division 6 Occupancies. An approved emergency alarm system shall be provided for HPM rooms, liquid storage rooms and gas rooms. Emergency alarm-initiating devices shall be installed outside of each interior door of such rooms. Activation of an emergency alarm-initiating device shall sound a local alarm and transmit a signal to the emergency control station. Fore installation requirements, see the Fire Code. 307.11.6 Piping and Tubing. 307.11.6.1 General. Hazardous production materials piping and tubing shall comply with this section and shall be installed in accordance with nationally recognized standards. Piping and tubing systems shall be metallic unless the material being transported is incompatible with such system. Systems supplying gaseous having a health hazard ranking of 3 or 4 shall be welded throughout, except for connections, valves and fittings, to the systems which are within a ventilated enclosure. Hazardous production materials supply piping or tubing in service corridors shall be exposed to view. 307.11.6.2 Installations in corridors and above other occupancies. Hazardous production materials shall not be located within corridors or above areas not classified as Group H, Division 6 Occupancies except as permitted by this section.
shall separate pass-throughs from existing corridors. Pass-throughs shall be constructed as required for the corridors. Pass-throughs shall be protected by an approved automatic fire sprinkler system.307.11.4 Service Corridors. Service corridors Shall be classified as Group H, Division 6 Occupancies. Service corridors shall be separated from corridors as required by Section 307.11.2.1. Service corridors shall be mechanically ventilated as required by Section 307.11.2.4 or at not less than six air changes per hour, whichever is greater. The maximum travel distance from any point in a service corridor to an exit or door
into fabrication area shall not exceed 4ft (1219mm) in length. There shall not be less than two means of egress, and not more than one half of the required means of egress shall be into the fabrication area. Doors from service corridors shall swing in the direction of egress and shall be self-closing. The minimum clear width of a service corridor shall be 5ft (1524mm), or 33inches (838mm) wider than the widest cart or truck used in the corridor, whichever is greater. 307.11.5 Storage of hazardous production materials. 307.11.5.1 Construction. The storage of hazardous production materials in quantities greater than those listed in Table 3-D or 3-E shall
be in liquid storage rooms, HPM rooms or gas rooms, as required by the Fire Code. HPM rooms and gas rooms shall be separated from all other areas by not less than a two-hour fire-resistive occupancy separation when the area is 300 square feet (27.9m2) or more and not less than one-hour fire-resistive occupancy separation when the area is less than 300sq ft (27.9m2). The provisions of Section 302.1 shall apply. Except for surfacing, floors of storage and HPM rooms shall be of noncombustible liquid-tight construction. Raised grating over floors shall be of noncombustible materials. See Section 307.2.3 for sill requirements for liquid
storage rooms. 307.11.5.2 Location within building. When HPM rooms are provided, they shall have at least one exterior wall and such wall shall not be less than 30ft (9144mm) from property lines, including property lines adjacent to public ways. Explosion control shall be provided when required by Section 307.10. 307.11.5.3 Means of egress. When two means of egress are required from HPM rooms, one shall be directly to the outside of the building. See Section 307.11.2.1, Exception 1. 307.11.5.4 Ventilation. Mechanical exhaust ventilation shall be provided in liquid storage rooms, HPM rooms and gas rooms at the rate of not less
than 1 cubic foot per minute per square foot (0.044L/s/m2) of floor area or six air changes per hour, whichever is greater, for all categories of material. Exhaust ventilation for gas rooms shall be designed to operate at a negative pressure in relation to the surrounding areas and direct the exhaust ventilation to an exhaust system. 307.11.5.5 Fire and emergency alarm. An approved manual fire alarm system shall be provided throughout buildings containing Group H, Division 6 Occupancies. An approved emergency alarm system shall be provided for HPM rooms, liquid storage rooms and gas rooms. Emergency alarm-initiating devices shall be
installed outside of each interior door of such rooms. Activation of an emergency alarm-initiating device shall sound a local alarm and transmit a signal to the emergency control station. Fore installation requirements, see the Fire Code. 307.11.6 Piping and Tubing. 307.11.6.1 General. Hazardous production materials piping and tubing shall comply with this section and shall be installed in accordance with nationally recognized standards. Piping and tubing systems shall be metallic unless the material being transported is incompatible with such system. Systems supplying gaseous having a health hazard ranking of 3 or 4 shall
be welded throughout, except for connections, valves and fittings, to the systems which are within a ventilated enclosure. Hazardous production materials supply piping or tubing in service corridors shall be exposed to view. 307.11.6.2 Installations in corridors and above other occupancies. Hazardous production materials shall not be located within corridors or above areas not classified as Group H, Division 6 Occupancies except as permitted by this section.
Hazardous production material piping or tubing may be installed within the space defined by the walls of corridors and the floor or roof above or in concealed spaces above other occupancies under the following conditions: 1. Automatic sprinklers shall be installed within the space unless the space is less than 6inches (152mm) in least dimension. 2. Ventilation at not less than six air changes per hour shall be provided. The space shall not be used to convey air from any other area. 3. When piping and tubing is used to transport HPM liquids, a receptor shall be installed below such piping or tubing.
The receptor shall be designed to collect any discharge or leakage and drain it to an approved location. The one-hour enclosure shall not be used as part of the receptor. 4. All HPM supply piping and tubing and HPM nonmetallic waste lines shall be separated from the corridor and from any occupancy other than Group H, Davison 6 by construction as required for walls or partitions that have a fire-protection rating of not less than one hour. When gypsum wallboard is used, joints on the piping side of the enclosure need not be taped, provided the joints occur over framing members. Access openings into the
enclosure shall be protected by approved fire assemblies. 5. Readily accessible manual or automatic remotely activated fail-safe emergency shutoff valves shall be installed on piping and tubing other than waste lines at the following locations: 5.1 At branch connections into the fabrication area. 5.2 At entries into corridors. Excess flow valves shall be installed as required by the Fire Code. Exception: Occasional transverse crossings of the corridors by supply piping which is enclosed within a ferrous pipe or tube for the width of the corridor need not comply with Items 1 through 5. 307.11.6.3 Identification. Piping,
tubing and HPM waste lines shall be identified in accordance with nationally recognized standards to indicate the material being transported.
907.2.6.2.3 | Smoke Detectors | Smoke detectors. An approved automatic smoke detection system shall be installed throughout resident housing areas, including sleeping areas and contiguous day rooms, group activity spaces and other common spaces normally accessible to residents. Exceptions: 1. Other approved smoke detection arrangements providing equivalent protection including, but not limited to, placing detectors in exhaust ducts from cells or behind protective guards listed for the purpose are allowed when necessary to prevent damage or tampering. 2. Sleeping units in Use Conditions 2 and 3. 3. Smoke detectors are | 907.2.6.2.3 | Smoke detectors. An approved automatic smoke detection system shall be installed throughout resident housing areas, including sleeping areas and contiguous day rooms, group activity spaces and other common spaces normally accessible to residents. Exceptions: 1. Other approved smoke-detection arrangements providing equivalent protection including, but not limited to, placing detectors in exhaust ducts from cells or behind protective guards listed for the purpose are allowed when necessary to prevent damage or tampering. 2. Sleeping rooms in Use Conditions II or III. 3. Smoke detectors | 322 |  | 919.4.3 | Use Group I-3. An automatic fire detection system shall be installed and maintained in all resident housing areas of Use Group I-3. Smoke detectors shall be arranged and positioned to prevent damage or tampering, provided that the function and speed of detecting a fire is equivalent to that provided by the spacing and arrangement requirements of NFPA 72 listed in Chapter 35. Smoke detectors shall not be required in sleeping rooms with four or less occupants. | 409.2.12 | Automatic fire detection. An approved automatic fire detection system with smoke detectors shall be installed in accordance with NFPA 72 throughout all resident housing areas, including sleeping areas and any contiguous day room, group activity space, or other common spaces for customary access of residents. Exceptions: 1. Smoke detectors shall not be required in sleeping rooms with four or fewer occupants in buildings protected throughout with an approved automatic sprinkler system. 2. Other arrangements and positioning of smoke detectors may be used to prevent damage or tampering or for other purposes
|  | not required in sleeping units with four or fewer occupants in smoke compartments that are equipped throughout with an approved automatic sprinkler system. |  | are not required in sleeping rooms with four or fewer occupants in smoke compartments that are equipped throughout with an approved automatic sprinkler system. | [5 empty] | provided the function of detecting any fire is fulfilled and the siting of detectors is such that the speed of detection will be equivalent to that provided by the spacing and arrangements described in NFPA 72. This may include the location of detectors in exhaust ducts from cells, behind grills, or in other locations. The equivalent performance of the design shall be approved by the building official.
907.2.7 | Group M | Group M. A manual fire alarm system shall be installed in Group M occupancies, other than covered mall buildings complying with Section 402, having an occupant load of 500 or more persons or more than 100 persons above or below the lowest level of exit discharge. Exception: Manual fire alarm boxes are not required if the building is equipped throughout with an automatic sprinkler system and the alarm notification appliances will activate upon sprinkler water flow. | 907.2.7 | Group M. A manual fire alarm system shall be installed in Group M occupancies having an occupant load of 500 or more persons or more than 100 persons above or below the lowest level of discharge. Exception: Manual fire alarm boxes are not required if the building is equipped throughout with an automatic sprinkler system and the alarm notification appliances will activate upon sprinkler water flow. |  | No related section. |  | No related section. | 905.1.1 | General. A fire alarm system in accordance with NFPA 72 shall be installed in all the following occupancies: Group A having an occupant load of 1000 persons or more. Group B having an occupant load of 500 or more persons or more than 100 persons above or below the street floor. Group E. Group F two stories or more in height, and having an occupant load of 500 or more persons above or below the street floor level. Group H. Group I. Group M having an occupant load of 500 or more persons or more than 100 persons above or below the street floor level. group R. R1 Occupancies having
accommodations for more than 15 guests. R2 Apartment houses four or more stories in height, and dormitories or rooming houses (not transient) having more than 15 sleeping accommodations. R4 occupancies. Exceptions: 1. Group R1 and R2. Where each guest room in R1 occupancies, dormitories and rooming houses has a direct exit to the outside of the building and the building is three stories or less in height. 2. Groups A, B, E, F, H, M, and R1, R2, R3, and R4 Small Facilities. The manual fire alarm boxes required in 905.1 may be omitted in buildings meeting all of the following requirements: 1. The
building is equipped with automatic fire detection or automatic sprinkler system covering all areas. 2. Actuation of the automatic sprinkler system will activate the fire alarm system. 3. Provisions are made to manually activate the fire alarm system at a minimum of one centrally located station. 905.1.2 Manual fire alarm boxes shall be located
not more than 5ft (1524mm) from the entrance to each exit. 905.1.3 Each floor shall be zoned separately. No one zone may exceed 15000sq ft (1394m2). A zone indicator panel shall be located at grade level at the normal point of fire department access or at a constantly attended building security control center. Exception: Automatic sprinkler system zones shall not exceed the area permitted by NFPA 13. 905.1.4 Upon completion of the fire alarm system, all alarm initiating devices and circuits, alarm indicating appliances and circuits, supervisory signal initiating devices and circuits, signaling line circuits,
and primary and secondary power supplies shall be subjected to a 100% acceptance test in accordance with NFPA 72. 905.1.5 Alarm indicating appliances 905.1.5.1 Required. Alarm indicating appliances listed for purpose shall be provided. 905.1.5.2 Visible and audible alarm indicating appliances shall be provided in occupancies housing the hearing impaired, Every required fire alarm system shall include visible alarm indicating appliances in public and common areas. 905.1.5.3 Activation The alarm indicating appliances shall be automatically activated by all of the following where provided: 1. Smoke
detectors, other than single-station or multiple-station smoke detectors, as required by 905.2. Activation of the alarm system by smoke detectors shall be by either two cross-zoned smoke detectors within a single protected area or a single smoke detector monitored by an alarm verification zone or an approved equivalent method. 2. Sprinkler water-flow devices; 3. Manual fire alarm boxes; and 4. Other approved types of automatic fire detection device suppression systems. 905.1.5.4 Audible Alarms. Audible alarm indicating appliances shall provide a distinctive sound which shall not be
used for any purpose other than that of a fire alarm. Such devices shall provide a sound pressure level of 15dBA above the average ambient sound level in every occupied space within the building. The minimum sound pressure levels shall be: 70dBA in buildings of Group R occupancy, 90dBA in mechanical equipment rooms; and 60dBA in all other occupancy classifications. The maximum sound pressure level for audible alarm indicating the appliances shall not exceed 130dBA at the minimum hearing distance from the audible appliance. 905.1.5.5 Visible Alarms. Visible alarm indicating appliances,
where required, shall be so located as to notify all occupants in every occupied space within the building.
907.2.8 | Group R-1 | Group R-1. Fire alarm systems shall be installed in Group R-1 occupancies as required in Sections 907.2.8.1 through 907.2.8.3. | 907.2.8 | Group R-1. A manual fire alarm system and an automatic fire detection system shall be installed in Group R-1 occupancies. Exceptions: 1. A manual fire alarm system is not required in buildings not over two stories in height where all individual guestrooms and contiguous attic and crawl spaces are separated from each other and public or common areas by at lest 1-hour fire partitions and each individual guestrooms has an exit directly to a public way, exit court or yard. 2. An automatic fire detection system is not required in buildings that do not have interior corridors serving guestrooms and where | "310.10" | Fire Alarm Systems. Group R, Division 1 Occupancies shall be provided with a manual and automatic fir alarm system in apartment houses three or more stories in height or containing 16 or more dwelling units, in hotels three or more stories in height or containing 20 or more guest rooms and in congregate residences three or more stories in height or having an occupant load of 20 or more. A fire alarm and communication system shall be provided in Group R, Division 1 Occupancies, located in a high-rise building. Exceptions: 1. A manual fire alarm system need not be provided in buildings | 918.4.5 919.4.4 | Use Group R-1. A fire alarm system shall be installed and maintained in all occupancies in Use Group R-1. 918.4.4 Use Group I. A fire alarm system shall be installed and maintained in all occupancies in Use Group I. | 905.1 1905.2.1 | 905.1 Manual fire alarm systems 905.1.1 General A fire alarm system in accordance with NFPA 72 shall be installed in all of the following occupancies: Group A having an occupant load of 1000 persons or more. Group B having an occupant load of 500 or more persons or more than 100 persons above or below the street floor. Group E. Group F two stories or more in height, and having an occupant load of 500 or more persons above or below the street floor level. Group H. Group I. Group M having an occupant load of 500 or more persons or more than 100 persons above or below the street floor level.
|  |  |  | guestrooms have a means of egress door openings directly to an exterior exit access that leads directly to the exits. 3. A separate fire alarm system is not required in buildings that are equipped throughout with an approved supervised automatic sprinkler system and which have a local fire alarm that meets he notification requirements of Section 907.9.2. |  | over two stories in height when all individual dwelling units and contiguous attic and crawl spaces are separated from each other and public or common areas by at least one-hour fire-resistive occupancy separations and each individual dwelling unit or guest room have an exit directly to a public way, exit court or yard. 2. A separate fire alarm system need not be provided in buildings that are protected throughout by an approved supervised fire sprinkler system having a local alarm to notify all occupants. The alarm signal shall be a distinctive sound that is not used for any other purpose other than the fire alarm. Alarm-signaling |  |  |  | Group R. R1 occupancies having accommodations for more than 15 guests. R2 Apartment houses four or more stories in height, and dormitories or rooming houses (not transient) having more than 15 sleeping accommodations. R4 occupancies. Exceptions: Group R1 and R2. Where each guest room in R1 occupancies, dormitories and rooming houses has a direct exit to the outside of the building and the building is three stories or less in height. 2. Groups A, B, E, F, H, M and R1, R2, R3, and R4 Small Facilities. The manual fire alarm boxes required in 905.1 may be omitted in buildings meeting all of the
[6 empty] | devices shall produce a sound that exceeds the prevailing equivalent sound level in the room or space by 15 decibels minimum, or exceeds any maximum sound level with a duration of 30 seconds minimum by 5 decibels minimum, whichever is louder. Sound levels for fire alarm signals shall be 120 decibels maximum. For the purposes of this section, area separation walls shall not define separate buildings. |  |  |  | following requirements: 1. The building is equipped with an automatic fire detection or automatic sprinkler system covering all areas. 2. Actuation of the automatic fire detection or automatic sprinkler system will activate the fire alarm. 3. Provisions are made to manually activate the fire alarm system at a minimum of one centrally located station. 1905.2.1 Proportions of materials for concrete shall be established to provide: 1.Workability and consistency to permit concrete to be worked readily into forms and around reinforcement under conditions of placement to be employed, without
segregation or excessive bleeding. 2.Resistance to special exposures as required by 1904. 3. Conformance with strength test requirements of 1905.6.
907.2.8.1 | Manual Fire Alarm System | Manual fire alarm system. A manual fire alarm system shall be installed in Group R-1 occupancies. Exceptions: 1. A manual fire alarm system is not required in buildings not over two stories in height where all individual guestrooms and contiguous attic and crawl spaces are separated from each other and public or common areas by at least 1-hour fire partitions and each individual guestroom has an exit directly to a public way, exit court or yard. 2. Manual fire alarm boxes are not required throughout the building when the following conditions are met: 2.1. The building is equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2. 2.2. The notification appliances will activate upon sprinkler water flow, and 2.3. At least one manual fire alarm box is installed at an approved location. | 907.2.8 | Group R-1. A manual fire alarm system and an automatic fire detection system shall be installed in Group R-1 occupancies. Exceptions: 1. A manual fire alarm system is not required in buildings not over two stories in height where all individual guestrooms and contiguous attic and crawl spaces are separated from each other and public or common areas by at lest 1-hour fire partitions and each individual guestrooms has an exit directly to a public way, exit court or yard. 2. An automatic fire detection system is not required in buildings that do not have interior corridors serving guestrooms and where | "310.10" | Fire Alarm Systems. Group R, Division 1 Occupancies shall be provided with a manual and automatic fir alarm system in apartment houses three or more stories in height or containing 16 or more dwelling units, in hotels three or more stories in height or containing 20 or more guest rooms and in congregate residences three or more stories in height or having an occupant load of 20 or more. A fire alarm and communication system shall be provided in Group R, Division 1 Occupancies, located in a high-rise building. Exceptions: 1. A manual fire alarm system need not be provided in buildings | 919.4.4 | Use Group R-1. An automatic fire detection system shall be installed and maintained in all occupancies in Use GroupR-1. Exceptions: 1. An automatic fire detection system is not required in buildings that do not have interior corridors serving guestrooms and where all guestrooms have a means of egress door opening directly to an exterior exit access which leads directly to the exits. 2. System smoke detectors are not required in guestrooms provided that the single-station detectors required by Section 920.3.1 are connected to the emergency electrical system and are annunciated by guestroom at a |  | No related section.
|  |  |  | guestrooms have a means of egress door openings directly to an exterior exit access that leads directly to the exits. 3. A separate fire alarm system is not required in buildings that are equipped throughout with an approved supervised automatic sprinkler system and which have a local fire alarm that meets he notification requirements of Section 907.9.2. |  | over two stories in height when all individual dwelling units and contiguous attic and crawl spaces are separated from each other and public or common areas by at least one-hour fire-resistive occupancy separations and each individual dwelling unit or guest room have an exit directly to a public way, exit court or yard. 2. A separate fire alarm system need not be provided in buildings that are protected throughout by an approved supervised fire sprinkler system having a local alarm to notify all occupants. The alarm signal shall be a distinctive sound that is not used for any other purpose other than the fire alarm. Alarm-signaling |  | constantly attended location from which the fire alarm system in capable of being manually activated.
devices shall produce a sound that exceeds the prevailing equivalent sound level in the room or space by 15 decibels minimum, or exceeds any maximum sound level with a duration of 30 seconds minimum by 5 decibels minimum, whichever is louder. Sound levels for fire alarm signals shall be 120 decibels maximum. For the purposes of this section, area separation walls shall not define separate buildings.
907.2.8.2 | Automatic Fire Alarm System | Automatic fire alarm system. An automatic fire alarm system shall be installed throughout all interior corridors serving guestrooms. Exception: An automatic fire detection system is not required in buildings that do not have interior corridors serving guestrooms and each guestroom has a means of egress door opening directly to an exterior exit access that leads directly to an exit. | 907.2.8 | Group R-1. A manual fire alarm system and an automatic fire detection system shall be installed in Group R-1 occupancies. Exceptions: 1. A manual fire alarm system is not required in buildings not over two stories in height where all individual guestrooms and contiguous attic and crawl spaces are separated from each other and public or common areas by at lest 1-hour fire partitions and each individual guestrooms has an exit directly to a public way, exit court or yard. 2. An automatic fire detection system is not required in buildings that do not have interior corridors serving guestrooms and where | "310.10" | Fire Alarm Systems. Group R, Division 1 Occupancies shall be provided with a manual and automatic fir alarm system in apartment houses three or more stories in height or containing 16 or more dwelling units, in hotels three or more stories in height or containing 20 or more guest rooms and in congregate residences three or more stories in height or having an occupant load of 20 or more. A fire alarm and communication system shall be provided in Group R, Division 1 Occupancies, located in a high-rise building. Exceptions: 1. A manual fire alarm system need not be provided in buildings | 919.4.4 | Use Group R-1. An automatic fire detection system shall be installed and maintained in all occupancies in Use GroupR-1. Exceptions: 1. An automatic fire detection system is not required in buildings that do not have interior corridors serving guestrooms and where all guestrooms have a means of egress door opening directly to an exterior exit access which leads directly to the exits. 2. System smoke detectors are not required in guestrooms provided that the single-station detectors required by Section 920.3.1 are connected to the emergency electrical system and are annunciated by guestroom at a |  | No related section.
|  |  |  | guestrooms have a means of egress door openings directly to an exterior exit access that leads directly to the exits. 3. A separate fire alarm system is not required in buildings that are equipped throughout with an approved supervised automatic sprinkler system and which have a local fire alarm that meets he notification requirements of Section 907.9.2. |  | over two stories in height when all individual dwelling units and contiguous attic and crawl spaces are separated from each other and public or common areas by at least one-hour fire-resistive occupancy separations and each individual dwelling unit or guest room have an exit directly to a public way, exit court or yard. 2. A separate fire alarm system need not be provided in buildings that are protected throughout by an approved supervised fire sprinkler system having a local alarm to notify all occupants. The alarm signal shall be a distinctive sound that is not used for any other purpose other than the fire alarm. Alarm-signaling |  | constantly attended location from which the fire alarm system in capable of being manually activated.
devices shall produce a sound that exceeds the prevailing equivalent sound level in the room or space by 15 decibels minimum, or exceeds any maximum sound level with a duration of 30 seconds minimum by 5 decibels minimum, whichever is louder. Sound levels for fire alarm signals shall be 120 decibels maximum. For the purposes of this section, area separation walls shall not define separate buildings.
907.2.9 | Group R-2 | Group R-2.Amanual fire alarm system shall be installed in Group R-2 occupancies where: 1. Any dwelling unit or sleeping unit is located three or more stories above the lowest level of exit discharge; 2. Any dwelling unit or sleeping unit is located more than one story below the highest level of exit discharge of exits serving the dwelling unit or sleeping unit; or 3. The building contains more than 16 dwelling units or sleeping units. Exceptions: 1. Afire alarm system is not required in buildings not over two stories in height where all dwelling units or sleeping units and contiguous attic and crawl spaces are separated from each other and public or | 907.2.9 | Group R-2. A fire alarm system shall be installed in Group R-2 occupancies where: 1. Any dwelling unit is located three or more stories above the lowest level of exit discharge; 2. Any dwelling unit is located more than one story below the highest level of exit discharge of exits serving the dwelling unit; or 3. the building contains more than 16 dwelling units. Exceptions: 1. A fire alarm system is not required in buildings not over two stories in height where all dwelling units and contiguous attic and crawl spaces are separated from each other and public or common areas by at least 1-hour fire partitions and each dwelling unit has an | "310.10" | Fire Alarm Systems. Group R, Division 1 Occupancies shall be provided with a manual and automatic fir alarm system in apartment houses three or more stories in height or containing 16 or more dwelling units, in hotels three or more stories in height or containing 20 or more guest rooms and in congregate residences three or more stories in height or having an occupant load of 20 or more. A fire alarm and communication system shall be provided in Group R, Division 1 Occupancies, located in a high-rise building. Exceptions: 1. A manual fire alarm system need not be provided in buildings | 918.4.6 | Use Group R-2. A fire alarm system shall be installed and maintained in all occupancies in Use Group R-2 where any dwelling unit is located three or more stories above the lowest level of exit discharge or more than one story below the highest level of exit discharge of exits serving the dwelling unit. | 905.1.1 905.2.1 | 905.1.1 General. A fire alarm system in accordance with NFPA 72 shall be installed in all the following occupancies: Group A having an occupant load of 1000 persons or more. Group B having an occupant load of 500 or more persons or more than 100 persons above or below the street floor. Group E. Group F two stories or more in height, and having an occupant load of 500 or more persons above or below the street floor level. Group H. Group I. Group M having an occupant load of 500 or more persons or more than 100 persons above or below the street floor level. group R. R1 Occupancies having
|  | common areas by at least 1-hour fire partitions and each dwelling unit or sleeping unit has an exit directly to a public way, exit court or yard. 2. Manual fire alarm boxes are not required throughout the building when the following conditions are met: 2.1. The building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. 2.2. The notification appliances will activate upon sprinkler flow, and 2.3. At least one manual fire alarm box is installed at an approved location. 3. Afire alarm system is not required in buildings that do not have interior corridors serving dwelling units |  | exit directly to a public way, exit court or yard. 2. A separate fire alarm system is not required in buildings that are equipped throughout with an approved, supervised automatic sprinkler system installed in accordance with Section 903.3.1.1 or Section 903.3.1.2 and which have a local alarm that meets the notification requirements of Section 907.9.2. |  | over two stories in height when all individual dwelling units and contiguous attic and crawl spaces are separated from each other and public or common areas by at least one-hour fire-resistive occupancy separations and each individual dwelling unit or guest room have an exit directly to a public way, exit court or yard. 2. A separate fire alarm system need not be provided in buildings that are protected throughout by an approved supervised fire sprinkler system having a local alarm to notify all occupants. The alarm signal shall be a distinctive sound that is not used for any other purpose other than the fire alarm. Alarm-signaling |  |  |  | accommodations for more than 15 guests. R2 Apartment houses four or more stories in height, and dormitories or rooming houses (not transient) having more than 15 sleeping accommodations. R4 occupancies. Exceptions: 1. Group R1 and R2. Where each guest room in R1 occupancies, dormitories and rooming houses has a direct exit to the outside of the building and the building is three stories or less in height. 2. Groups A, B, E, F, H, M, and R1, R2, R3, and R4 Small Facilities. The manual fire alarm boxes required in 905.1 may be omitted in buildings meeting all of the following requirements: 1. The
|  | and are protected by an approved automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2, provided that dwelling units either have a means of egress door opening directly to an exterior exit access that leads directly to the exits or are served by open-ended corridors designed in accordance with Section 1022.6, Exception 4. |  |  |  | devices shall produce a sound that exceeds the prevailing equivalent sound level in the room or space by 15 decibels minimum, or exceeds any maximum sound level with a duration of 30 seconds minimum by 5 decibels minimum, whichever is louder. Sound levels for fire alarm signals shall be 120 decibels maximum. For the purposes of this section, area separation walls shall not define separate buildings. |  |  |  | building is equipped with automatic fire detection or automatic sprinkler system covering all areas. 2. Actuation of the automatic sprinkler system will activate the fire alarm system. 3. Provisions are made to manually activate the fire alarm system at a minimum of one centrally located station. 905.1.2 Manual fire alarm boxes shall be located not more than 5ft (1524mm) from the entrance to each exit. 905.1.3 Each floor shall be zoned separately. No one zone may exceed 15000sq ft (1394m2). A zone indicator panel shall be located at grade level at the normal point of fire department access or at a constantly
attended building security control center. Exception: Automatic sprinkler system zones shall not exceed the area permitted by NFPA 13. 905.1.4 Upon completion of the fire alarm system, all alarm initiating devices and circuits, alarm indicating appliances and circuits, supervisory signal initiating devices and circuits, signaling line circuits, and primary and secondary power supplies shall be subjected to a 100% acceptance test in accordance with NFPA 72. 905.1.5 Alarm indicating appliances 905.1.5.1 Required. Alarm indicating appliances listed for purpose shall be provided. 905.1.5.2 Visible and audible
alarm indicating appliances shall be provided in occupancies housing the hearing impaired, Every required fire alarm system shall include visible alarm indicating appliances in public and common areas. 905.1.5.3 Activation The alarm indicating appliances shall be automatically activated by all of the following where provided: 1. Smoke detectors, other than single-station or multiple-station smoke detectors, as required by 905.2. Activation of the alarm system by smoke detectors shall be by either two cross-zoned smoke detectors within a single protected area or a single smoke detector monitored by
an alarm verification zone or an approved equivalent method. 2. Sprinkler water-flow devices; 3. Manual fire alarm boxes; and 4. Other approved types of automatic fire detection device suppression systems. 905.1.5.4 Audible Alarms. Audible alarm indicating appliances shall provide a distinctive sound which shall not be used for any purpose other than that of a fire alarm. Such devices shall provide a sound pressure level of 15dBA above the average ambient sound level in every occupied space within the building. The minimum sound pressure levels shall be: 70dBA in buildings of Group R occupancy, 90dBA in
mechanical equipment rooms; and 60dBA in all other occupancy classifications. The maximum sound pressure level for audible alarm indicating the appliances shall not exceed 130dBA at the minimum hearing distance from the audible appliance. 905.1.5.5 Visible Alarms. Visible alarm indicating appliances, where required, shall be so located as to notify all occupants in every occupied space within the building. 905.2.1 Approved single-station or multiple-station smoke detectors shall be installed in accordance with NFPA 72, Chapter 2, within every dwelling and dwelling unit within an apartment house,
condominium or townhouse, and every guest or sleeping room in a motel, hotel, dormitory, and sleeping rooms in residential care/assisted living occupancies. Where more than one detector is required to be installed within an individual dwelling unit, the detectors shall be wired in such a manner that the actuation of one alarm will actuate all of the alarms in the individual unit.
907.2.10.1.2 | Groups R-2, R-3, and R-4 | Groups R-2, R-3, R-4 and I-1. Single- or multiple-station smoke alarms shall be installed and maintained in Groups R-2, R-3, R-4 and I-1, regardless of occupant load at all of the following locations: 1. On the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. 2. In each room used for sleeping purposes. 3. In each story within a dwelling unit, including basements but not including crawl spaces and uninhabitable attics. In dwellings or dwelling units with split levels and without an intervening door between the adjacent levels, a smoke alarm installed on the upper level shall suffice for | 907.2.10.1.2 | Groups R-2, R-3, R-4 and I-1. Single- or multiple-station smoke alarms shall be installed and maintained in Groups R-2, R-3, R-4 and I-1, regardless of occupant load at all the following locations: 1. On the ceiling or wall outside if each separate sleeping area in the immediate vicinity of bedrooms. 2. In each room used for sleeping purposes. 3. In each story within a dwelling unit, including crawl spaces and uninhabitable attics. In dwellings or dwelling units with split levels and without an intervening door between the adjacent levels, a smoke alarm installed on the upper level shall suffice for the adjacent lower | 310.9.1.4 | Location within dwelling units. In dwelling units, a detector shall be installed in each sleeping room and at a point centrally located in the corridor or area giving access to each separate sleeping area. When the dwelling unit has more than one story and in dwellings with basements, a detector shall be installed on each story and in the basement. In dwelling units where a story or basement is split into two or more levels, the smoke detector shall be installed on the upper level, except that when the lower level contains a sleeping area, a detector shall be installed on each level. When sleeping rooms are on an upper level, the detector | 920.3.2 | Use Groups R-2 and R-3. Single- or multiple-station smoke detectors shall be installed and maintained in all occupancies in Use Groups R-2 and R-3 at the following locations: 1. In the immediate vicinity of bedrooms; 2. In all bedrooms; and 3. In each story within a dwelling unit, including basements. Exceptions: 1. In dwelling units with split levels and without an intervening door between the adjacent levels, a smoke detector installed on the upper level shall suffice for the adjacent lower level provided that the lower level is less than one full story below the upper level. 2. In buildings equipped | 905.1.1 905.2.2 | 905.1.1 General. A fire alarm system in accordance with NFPA 72 shall be installed in all the following occupancies: Group A having an occupant load of 1000 persons or more. Group B having an occupant load of 500 or more persons or more than 100 persons above or below the street floor. Group E. Group F two stories or more in height, and having an occupant load of 500 or more persons above or below the street floor level. Group H. Group I. Group M having an occupant load of 500 or more persons or more than 100 persons above or below the street floor level. group R. R1 Occupancies having
|  | the adjacent lower level provided that the lower level is less than one full story below the upper level. |  | level provided that the lower level is less than one full story below the upper level. |  | shall be placed at the ceiling of the upper level in close proximity to the stairway. In dwelling units where the ceiling height of a room open to the hallway serving the bedrooms exceeds that of the hallway by 24 inches (610mm) or more, smoke detectors shall be installed in the hallway and in the adjacent room. Detectors shall sound an alarm audible in all sleeping areas of the dwelling unit in which they are located. |  | throughout with an automatic sprinkler system installed in accordance with Section 906.2.1, 906.2.2 or 906.2.3, smoke detectors are not required in bedrooms where the bedrooms are equipped with residential sprinklers. |  | accommodations for more than 15 guests. R2 Apartment houses four or more stories in height, and dormitories or rooming houses (not transient) having more than 15 sleeping accommodations. R4 occupancies. Exceptions: 1. Group R1 and R2. Where each guest room in R1 occupancies, dormitories and rooming houses has a direct exit to the outside of the building and the building is three stories or less in height. 2. Groups A, B, E, F, H, M, and R1, R2, R3, and R4 Small Facilities. The manual fire alarm boxes required in 905.1 may be omitted in buildings meeting all of the following requirements: 1. The
building is equipped with automatic fire detection or automatic sprinkler system covering all areas. 2. Actuation of the automatic sprinkler system will activate the fire alarm system. 3. Provisions are made to manually activate the fire alarm system at a minimum of one centrally located station. 905.2.2 In dwellings and dwelling units, a smoke detector shall be mounted on the ceiling or wall at a point centrally located in the corridor or area giving access to each group of rooms used for sleeping purposes. Where the dwelling or dwelling unit contains more than one story, detectors are required on each story
including basements, but not including uninhabitable attics, and shall be located in close proximity to the stairway leading to the floor above.
907.2.10.2 | Power Source | Power source. In new construction, required smoke alarms shall receive their primary power from the building wiring where such wiring is served from a commercial source and shall be equipped with a battery backup. Smoke alarms shall emit a signal when the batteries are low. Wiring shall be permanent and without a disconnecting switch other than as required for overcurrent protection. Exception: Smoke alarms are not required to be equipped with battery backup in Group R-1 where they are connected to an emergency electrical system. | 907.2.10.2 | Power source. In new construction, required smoke alarm shall receive their primary power from the building wiring where such wiring is served from a commercial source and shall be equipped with a battery backup. Smoke alarms shall emit a signal when the batteries are low. Wiring shall be permanent and without a disconnecting switch other than as required for overcurrent protection. Exceptions: 1. Smoke alarms not required to be equipped with battery backup in Group R-1 where they are connected to an emergency electrical system. 2. Smoke alarms are permitted to be solely battery operated in existing | 310.9.1.3 | Power Source. In new construction, required smoke detectors shall receive their primary power from the building wiring when the such wiring is served from a commercial source and shall be equipped with a battery backup. The detector shall emit a signal when the batteries are low. Wiring shall be permanent and without disconnecting switch other than those required for over-current protection. Smoke detectors may be solely battery operated when installed in existing buildings; or in buildings without commercial power; or in buildings which undergo alterations, repairs or additions regulated by Section 310.9.1.2. | 920.5 | Battery backup. In addition to the required AC primary power source, required smoke detectors in occupancies in Use Groups R-2, R-3 and I-1 shall receive power from a battery when the AC primary power source is interrupted. Battery backup shall not be required for smoke detectors in buildings equipped throughout with am automatic sprinkler system installed in accordance with Section 906.2.1, 906.2.2 or 906.2.3. | 905.2.5 | In dwelling, dwelling units, and sleeping rooms in residential care/assisted living occupancies, smoke detectors shall be hardwired into an AC electrical power source and shall be equipped with a monitored battery backup in all new construction. A monitored battery power source shall be permitted in existing construction.
buildings, buildings not served from a commercial power source and in existing areas where alterations or repairs regulated by Section 907.2.10.1.4 do not result in the removal of interior wall or ceiling finishes exposing the structure, unless there is an attic, crawl space or basement available which could provide access for building wiring without the removal of interior finishes.
907.2.11.1 | Alarm | Alarm. Activation of any single smoke detector, the automatic sprinkler system or any other automatic fire detection device shall immediately sound an alarm at the building at a constantly attended location from which emergency action can be initiated, including the capability of manual initiation of requirements in Section 907.2.11.2. | 907.2.11.1 | Alarm. Activation of any single smoke detector, the automatic sprinkler system or any other automatic fire detection system shall immediately sound an alarm at the building at a constantly attended location from which emergency action can be initiated, including the capability of manual initiation of requirements in Section 907.2.11.2. | 408.5.2 | Alarm System. Activation of any single smoke detector, the automatic sprinkler system or other automatic fire-detection device shall immediately sound an alarm in the building at a constantly supervised location from which the manual operation of systems noted in Section 408.5.3, Items 1,2, and 3, ma be initiated. |  | No related section. | 403.5.5.2 | Activation of any single smoke detector, the automatic sprinkler system or any other automatic fire detection device shall immediately sound an alarm at the building at a constantly attended location from which emergency action can be initiated including the capability of manual initiation of 403.5.5.1(1) through 4.3.5.5.1(3).
907.2.11.2 | System Response | System response. The activation of two or more smoke detectors, a single smoke detector with alarm verification, the automatic sprinkler system or other approved fire detection device shall automatically: 1. Cause illumination of the means of egress with light of not less than 1 foot-candle (11 lux) at the walking surface level; 2. Stop any conflicting or confusing sounds and visual distractions; and 3. Activate an approved directional exit marking that will become apparent in an emergency. Such system response shall also include activation of a prerecorded message, clearly audible throughout the special amusement | 907.2.11.2 | System response. The activation of two or more smoke detectors, a single smoke detector with alarm verification, the automatic sprinkler system or other approved fire detection device shall automatically: 1. Cause illumination of the means of egress with light if not less than 1 foot-candle (11lux) at the walking surface level; 2. Stop any conflicting or confusing sounds and visual distractions; and 3. Activate an approved directional exit marking that will become apparent in an emergency. Such system response shall also include activation of a prerecorded message , clearly audible throughout the special amusement | 408.5.3 | System Response. The activation of two or more smoke detectors, a single smoke detector monitored by an alarm verification zone, the automatic sprinkler system or other approved automatic fire-detection device shall automatically: 1. Stop confusing sounds and effects, 2. Activate an approved directional exit marking, and 3. cause illumination of the means of egress with a light of not less than 1 footcandle (10.761x) at the walking surface. |  | No related section. | 403.5.5.1 | The activation of the automatic fire detection system within a single protected area or the automatic sprinkler system shall automatically: 1. Cause illumination of the means of egress with light of not less than 1 foot-candle (10.81x) at the walking surface level, and 2.Stop any conflicting or confusing sounds and visual effects, and 3. Activate an approved directional exit marking that will become apparent in an emergency.
|  | building, instructing patrons to proceed to the nearest exit. Alarm signals used in conjunction with the prerecorded message shall produce a sound which is distinctive from other sounds used during normal operation. The wiring to the auxiliary devices and equipment used to accomplish the above fire safety functions shall be monitored for integrity in accordance with NFPA 72. |  | building, instructing patrons to proceed to the nearest exit. Alarm signals used in conjunction with the prerecorded message shall produce a sound which is distinctive from other sounds used during normal operation. The wiring to the auxiliary devices and equipment used to accomplish the above fire safety functions shall be monitored for integrity in accordance with NFPA 72.
907.2.12.1 | Automatic Fire Detection | Automatic fire detection. Smoke detectors shall be provided in accordance with this section. Smoke detectors shall be connected to an automatic fire alarm system. The activation of any detector required by this section shall operate the emergency voice/alarm communication system. Smoke detectors shall be located as follows: 1. In each mechanical equipment, electrical, transformer, telephone equipment or similar room which is not provided with sprinkler protection, elevator machine rooms and in elevator lobbies. 2. In the main return air and exhaust air plenum of each air- | 907.2.12.1 | Automatic fire detection. Smoke detectors shall be provided in accordance with this Section. Smoke detectors shall be connected to an automatic fire alarm system. The activation of any detector required by this section shall operate the emergency voice/alarm communication system. Smoke detectors shall be located as follows: 1. IN each mechanical equipment, electrical, transformer, telephone equipment or similar which is not provided with sprinkler protection, elevator machine rooms, and in elevator lobbies. 2. In the main return air and exhaust air plenum of each air-conditioning | 403.3 | Smoke Detection. Smoke detectors shall be provided in accordance with this section. Smoke detectors shall be connected to an automatic fire alarm system installed in accordance with the Fire Code. The actuation of any detector required by this section shall operate the emergency voice alarm signaling system and shall place into operation all equipment necessary to prevent the recirculation of smoke. Smoke detectors shall be located as follows: 1. In every mechanical equipment, electrical, transformer, telephone equipment, elevator machine or similar room and in | 403.4 | Automatic fire detection. A smoke detector suitable for the intended application shall be installed in each of the following rooms: mechanical equipment; electrical; transformer; telephone equipment; elevator machine; or similar room. The actuation of any detector shall sound an alarm at a constantly attended location. | 412.2 | Automatic fire detection systems 412.2.1 At lease one approved smoke detector suitable for the intended use shall be installed in: 1. Every mechanical equipment, electrical, transformer, telephone equipment, elevator machine or similar room. 2. In every elevator lobby. 3. All recirculating air systems serving more than one story. The detector shall be accessible and shall be located in the return airstream prior to any exhausting from the building or mixing with the fresh air makeup. 4. Each connection to a return air vertical duct or riser serving a recirculating air system of more than one story. In Group R
|  | conditioning system having a capacity greater than 2,000 cubic feet per minute (cfm) (0.94 m3/s). Such detectors shall be located in a serviceable area downstream of the last duct inlet. 3. At each connection to a vertical duct or riser serving two or more stories from a return air duct or plenum of an air-conditioning system. In Group R-1 and R-2 occupancies a listed smoke detector is allowed to be used in each return air riser carrying not more than 5,000 cfm (2.4m3/s) and serving not more than 10 air inlet openings. |  | system having a capacity greater than 2000 cubic feet per minute (cfm) (0.94m3/s). Such detectors shall be located in a serviceable area downstream of the last duct outlet. 3. At each connection to a vertical duct or riser serving two or more stories from a return air duct or plenum of an air-conditioning system. IN Group R-1 and R-2 occupancies, a listed smoke detector is allowed to be used in each return-air riser carrying not more than 5000cfm (2.4m3/s) and serving not more than 10air-inlet openings. |  | elevator lobbies. Elevator lobby detectors shall be connected to an alarm verification zone or be listed as releasing devices. 2. In the main return-air and exhaust-air plenum of each air-conditioning system. Such detector shall be located in a serviceable area downstream of the last duct inlet. 3. At each connection to a vertical duct or riser serving two or more stories from a return-air duct or plenum of an air-conditioning system. In Group R, Division 1 Occupancies, an approved smoke detector may be used in each return-air riser carrying not more than 5000 cubic ft per minute (2360L/s) and serving not more than |  |  |  | occupancies, an approved smoke detector may be used in each return air riser carrying not more than 5000cfm (2.36m3/s) and serving not more than 10 air inlet openings. 5. See 905.2 for additional smoke detection requirements in Group R buildings. 412.2.2 The actuation of any detector required by 412.2 shall activate the voice alarm system and shall place into operation all equipment necessary to prevent the recirculation of smoke.
10 air inlet openings. 4. For Group R, Division 1 Occupancies in all corridors serving as a means of egress for an occupant load of 10 or more.
907.14 | Monitoring | Monitoring. Where required by this chapter or the International Fire Code, an approved supervising station in accordance with NFPA 72 shall monitor fire alarm systems. Exception: Supervisory service is not required for: 1. Single- and multiple-station smoke alarms required by Section 907.2.10. 2. Smoke detectors in Group I-3 occupancies. 3. Automatic sprinkler systems in one- and two-family dwellings. | 907.14 | Monitoring. Where required by this chapter, an approved supervising station in accordance with NFPA 72 shall monitor fire alarm systems. Exception: Supervisory service is not required fir automatic sprinkler systems in one- and two-family dwelling. | 904.3.1 | Where required. All valves controlling the water-supply for automatic sprinkler systems and water-flow switches on all sprinkler systems shall be electrically monitored where the number of sprinklers are: 1. Twenty or more in Group I, Divisions 1.1 and 1.2 Occupancies. 2. One hundred or more in all other occupancies. Valve monitoring and water-flow alarm and trouble signals shall be distinctly different and shall be automatically transmitted to an approved central station, remote station or proprietary monitoring station as defined by national standards, or, when approved by the building official with the concurrence of the | 924.1 | Fire suppression systems. All automatic fire suppression systems required for occupancies in Use Group A, B, E, H, I, M or R shall be supervised by method 1. All automatic fire suppression systems in other use groups shall be supervised by one the following methods: 1. Central-station system, proprietary system, remote-station system or supervisory service which will cause the actuation of an audible appliance at a constantly attended location, in accordance with NFPA 72 listed in Chapter 35; or 2. Locking open all valves on connections to water supplies, sectional |  | No related section.
[6 empty] | chief of the fire department, sound an audible signal at a constantly attended location. Exception: Underground key or hub valves in roadway boxes provided by the municipality or public utility need not be monitored. |  | control valves and other valves in supply pipes to fire protection devices. Exceptions: 1. Underground gate valves with roadway boxes. 2. Halogenated extinguishing systems that are not an integral part of a required automatic fire suppression system. 3. Carbon dioxide extinguishing systems that are not an integral part of a required automatic fire suppression system. 4. Dry- and wet-chemical extinguishing systems. 5. Limited area sprinkler system (see Section 907.6.3). 6. Occupancies in Use Group R complying with Section 906.2.2 and supervised in accordance with NFPA 13R listed in Chapter 35.
909.9.4 | Sprinkler Effectiveness Assumptions | Sprinkler effectiveness assumptions. A documented engineering analysis shall be provided for conditions that assume fire growth is halted at the time of sprinkler activation. | 909.9.4 | Sprinkler effectiveness assumptions. A documented engineering analysis shall be provided for conditions that assume fire growth is halted at the time of sprinkler activation. | 905.6.2.4 | Sprinkler effectiveness assumptions. The effect of sprinklers may be assumed to have halted fire growth at time of activation only upon a documented engineering analysis. |  | No related section. |  | No related section.
909.20.4.4 | Stair Shaft Air Movement System | Stair shaft air movement system. The stair shaft shall be provided with a dampered relief opening and supplied with sufficient air to maintain a minimum positive pressure of 0.10 inch of water (25 Pa) in the shaft relative to the vestibule with all doors closed. | 909.20.4.4 | Stair shaft air movement system. The stair shaft shall be provided with a dampered relief opening and supplied with sufficient air to maintain a minimum positive pressure of 0.10inch of water (25Pa) in the shaft relative to the vestibule with all doors closed. | 1005.3.3.7 | Pressurized enclosure. In a building having a floor level used for human occupancy located more than 75 feet (22860mm) above the lowest level of fire department vehicle access, all required exit enclosures shall be pressurized in accordance with Section 905 and this section. Pressurization shall occur automatically upon activation of an approved fire alarm system. Exception: If the building is not equipped with a fire alarm system, pressurization shall be upon activation of a spot-type smoke detector listed for releasing service located within 5 feet (1524mm) of each vestibule entry. A | 1015.6.4 | Stair shaft air movement system. The stair shaft shall be provided with a dampered relief opening and supplied with sufficient air to maintain a minimum positive pressure of 0.10inch of water column (29Pa) in the shaft relative to the vestibule with all doors closed. | 1005.6.9.9 | The stair shaft shall be provided with mechanical supply and exhaust air. There shall be a minimum of 2500cfm (1.2m3/s) discharge through a dampered relief opening or an exhaust fan at the top of the stair shaft. The supply shall be sufficient to provide a minimum positive pressure of 0.05-inch water column (12.5Pa) in addition to the maximum anticipated stack pressure, relative to other parts of the building measured with all doors closed. The combined positive pressure shall not exceed 0.35-inch water column (87Pa). The air supply shall be taken directly from outside of the building. The stair pressure shall be
[6 empty] | controlled relief vent capable of discharging a minimum of 2500 cubic feet per minute (1180L/s) of air at the design pressure difference shall be located in the upper portion of such pressurized exit enclosures. |  |  |  | static pressures measured at the level of discharge from the stair. Exception: The minimum positive pressure shall be increased to 0.15-inch water column (37Pa) in an unsprinklered building.
909.20.5 | Stair Pressurization Alternative | Stair pressurization alternative. Where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, the vestibule is not required, provided that interior exit stairways are pressurized to a minimum of 0.15 inch of water (37 Pa) and a maximum of 0.35 inch of water (87 Pa) in the shaft relative to the building measured with all stairway doors closed under maximum anticipated stack pressures. | 909.20.5 | Stair pressurization alternative. Where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, the vestibule is not required, provided that interior exit stairways are pressurized to a minimum 0.15 inch of water (37Pa) and maximum of 0.35inch of water (87Pa) in the shaft relative to the building measured with all stairway doors closed under maximum anticipated stack pressures. |  | No related section. | 1015.7 | Stair pressurization alternative. Where the building is equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1, the vestibule is not required, provided that all interior exit stairways are pressurized to a minimum of 0.15 inch of water column (44Pa) and a maximum of 0.35inch of water column (102Pa) in the shaft relative to the building measured with all stairway doors closed under maximum anticipated stack pressures. | 1005.6.7 | Access to the stairway shall be by way of a vestibule or by way of an exterior balcony of noncombustible materials. Exception: Access by way of a vestibule or an open exterior balcony is not required when the stairway meets the requirements of 1005.6.9.2, 1005.6.9.9 and 1005.6.9.10 and is located in a fully sprinklered building.
910.1 | General | General. Where required by this code or otherwise installed, smoke and heat vents or mechanical smoke exhaust systems and draft curtains shall conform to the requirements of this section. Exception: Frozen-food warehouses used solely for storage of Class I and II commodities where protected by an approved automatic sprinkler system. | 910.1 | General. Where required by this code or otherwise installed, smoke and heat vents or mechanical smoke exhaust systems and draft curtains shall conform to the requirements of this section. Exception: Frozen food warehouses used solely for storage of Class I and Class II commodities where protected by an approved automatic sprinkler system. | 906.1 | When Required. Smoke and heat vents complying with UBC Standard 15-7 or fixed openings shall be installed in accordance with the provisions of this section as follows: 1. In single-story Groups B, F, M and S, Divisions 1 and 2 Occupancies having over 50000 sq ft (4546m2) in undivided area. Exceptions: Office buildings and retail sales areas where storage does not exceed 12 feet (3658mm) in height. 2. Group S, Division 2 Occupancies used for bulk frozen food storage when the building is protected by a complete automatic sprinkler system. 2. IN Group H, Divisions 1, 2, 3, 4 or 5 Occupancies any of | 923.1 | General. Where exit access travel distance is increased in accordance with Section 1006.5.1, smoke and heat vents shall be constructed and installed in accordance with this section. | 1004.1.6 | In one-story Group F and Group S buildings equipped with automatic heat and smoke vets complying with this section and sprinklered, the travel distance may be increased to 400ft (122m). Smoke ad heat vents shall be constructed and installed in a manner approved by the building official.
which are over 15000 sq ft (1394m2) in single floor area. For requirements on smoke and heat venting in buildings with high-piled combustible stock, see the Fire Code.
910.3.4 | Draft Curtains | Draft curtains. Where required, draft curtains shall be provided in accordance with this section. Exception: Where areas of buildings are equipped with early suppression fast-response (ESFR) sprinklers, draft curtains shall not be provided within these areas. Draft curtains shall only be provided at the separation between the ESFR sprinklers and the conventional sprinklers. | 910.3.4 | Curtain boards. Where curtain boards are required, they shall be provided in accordance with this section. | 906.6.1 | General. Curtain boards shall be provided to subdivide a vented building in accordance with the provisions of this section. | 923.3 | Curtain board construction. Curtain boards shall be provided to subdivide a vented building. Curtain boards shall be constructed of materials that will resist the passage of smoke and is consistent with the building type of construction. Curtain board location and depth shall comply with Table 923.2. The bottom of the curtain board shall be level. | 1004.1.6.3 | Curtain boards constructed in accordance with this section shall be provided to subdivide a vented building. Exception: 1. When a smoke and heat venting system complies with the guidelines of NFPA 204M. When a building is protected by ESFR sprinklers installed in accordance with NFPA 13 and NFPA 231 or NFPA 231C.
Table 1005.1 | Egress Width Per Occupant Served | Provides factors for determining egress width based on type of egress element, occupancy, and sprinkler protection. | Table 1003.2.3 | Same | Table 10-B | Same for non-sprinklered occupancies. There is no modification to the factors for sprinklered buildings. | Table 1009.2 | There are differences in egress width factors for Institutional occupancies. IBC is more restrictive. | Table 1004 | Same for non-sprinklered buildings when treads are at least 11" deep and risers are between 4" and 7" high. Otherwise, the factor for stair width is 0.37" per person versus 0.3" per person in IBC. There is no increase in capacity based on sprinklers.
1007.2.1 | Buildings with Four or More Stories | Buildings with four or more stories. In buildings where a required accessible floor is four or more stories above or below a level of exit discharge, at least one required accessible means of egress shall be an elevator complying with Section 1007.4. Exceptions: 1. In buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2, the elevator shall not be required on floors provided with a horizontal exit and located at or above the level of exit discharge. 2. In buildings equipped throughout with an automatic sprinkler system installed in | 1003.2.13.1.1 | Buildings with four or more stories. In buildings where a required accessible floor is four or more stories above or below a level of exit discharge, at least one required accessible means of egress shall be an elevator complying with Section 1003.2.13.3. Exceptions: 1. IN buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2, the elevator shall not be required on floors provided with a horizontal exit and located at or above the level of exit discharge. 2. In buildings equipped throughout with an automatic sprinkler system installed in | 1104.1.3 | Elevators. When an accessible floor is four or more stories above or below the level of exit discharge serving that floor, at least one elevator shall serve as one required accessible means of egress. Exception: In fully sprinklered buildings, the elevator need not be provided to the floors provided with a horizontal exit and located at or above the level of exit discharge. When an elevator is part of an accessible means of egress, standby power shall be provided. The elevator shall be accessed from either an area of refuge complying with Section 1104.2 or a horizontal exit. Exceptions: 1. Elevators are not | 1007.3 | Elevators. An elevator, to be considered pat of an accessible means of egress, shall comply with Section 3006.0 and standby power shall be provided in accordance with Section 1007.5 or a horizontal exit. In buildings where a required accessible floor is four or more stories above or below a level of exit discharge serving that floor, at least one elevator shall be provided and shall serve as one required accessible means of egress. Exceptions: 1. In buildings equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1, the elevator shall not be required to serve floors which are | 1004.3.3 | In buildings where a required accessible floor is four or more stories in above or below a level of exit discharge serving that floor, at least one elevator shall be provided to comply with 1004.3.2.2 and shall serve as one required accessible means of egress. Exception: In fully sprinklered buildings, the elevator shall not be required on floors provided with a horizontal exit and located at or above the level of exit discharge.
|  | accordance with Section 903.3.1.1 or 903.3.1.2, the elevator shall not be required on floors provided with a ramp conforming to the provisions of Section 1010. |  | accordance with Section 903.3.1.1 or 903.3.1.2, the elevator shall not be required on floors provided with a ramp conforming to the provisions of Section 1003.3.4. |  | required to be accessed by an area of refuge or a horizontal exit in buildings protected throughout by an approved automatic sprinkler system. 2. Areas of refuge are not required in open parking garages. |  | located at or above the level of exit discharge and provided with a horizontal exit complying with Section 1019.0. 2. Elevators are not required to be accessed from an area of refuge or a horizontal exit in occupancies equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1.
1007.3 | Enclosed Stairways | Enclosed exit stairways. An enclosed exit stairway, to be considered part of an accessible means of egress, shall have a clear width of 48 inches (1219 mm) minimum between handrails and shall either incorporate an area of refuge within an enlarged floor-level landing or shall be accessed from either an area of refuge complying with Section 1007.6 or a horizontal exit. Exceptions: 1. Open exit stairways as permitted by Section 1019.1 are permitted to be considered part of an accessible means of egress. 2. The area of refuge is not required at open stairways that are permitted by Section 1019.1 in buildings or | 1003.2.13.2 | Enclosed stairways. An enclosed stairway, to be considered part of an accessible means of egress, shall have a clear width of 48inches (1219mm) minimum between handrails and shall either incorporate an area of refuge within an enlarged floor-level landing or shall be accessed from either an area of refuge complying with Section 1003.2.13.5 or a horizontal exit. Exceptions: 1. Stairways serving a single guestroom or dwelling unit. 2. Stairways in buildings or facilities equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2. 3. The clear width of 48 inches | 1104.1.2 | Stairways. When an exit stairway is part of an accessible means of egress, the stairway shall have a clear width of not less than 48 inches (1219mm) between handrails. The stairway shall either incorporate an area of refuge within an enlarged story-level landing or shall be accessed from an area of refuge complying with Section 1104.2 or a horizontal exit. Exceptions: 1. Exit stairways serving a single dwelling unit or guest room. 2. Exit stairways serving buildings protected throughout by approved automatic sprinkler system. 3. The clear width of 48 inches (1219mm) between handrails is not required for exit | 1007.2 | Exit stairways. An exit stairway, or be considered part of an accessible means of egress, shall have a clear width of at least 48 inches (1219mm) between handrails and shall either incorporate an are of refuge within an enlarged story-level landing or shall be accessed from an area of refuge complying with Section 1007.5 or a horizontal exit. Exceptions: 1. Stairs serving a single dwelling unit or guestroom. 2. Occupancies equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1. 3. The clear width of 48 inches (1219mm) between handrails is not required for exit stairways accessed from a horizontal exit. | 1004.3.2.1 | An exit stair to be considered part of an accessible means of egress shall have a clear width of at least 48 inches (1219mm) between handrails and shall either incorporate an area of refuge within an enlarged story-level landing or shall be accessed from either an area of refuge complying with 1004.3.5 or a horizontal exit. Exceptions: Exit stairs serving a single dwelling unit or guest room. 2. Exit stairs serving occupancies protected throughout by an approved automatic sprinkler system. 3. The clear width of 48 inches (1219mm) between handrails is not required for exit stairs accessed from a horizontal exit.
|  | facilities that are equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1. 3. The clear width of 48 inches (1219 mm) between handrails and the area of refuge is not required at exit stairways in buildings or facilities equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2. 4. The clear width of 48 inches (1219 mm) between handrails is not required for enclosed exit stairways accessed from a horizontal exit. 5. Areas of refuge are not required at exit stairways serving open parking garages. |  | (1219mm) between handrails is not required for enclosed stairways accesses from a horizontal exit. 4. Stairways serving open parking garages. |  | stairways accessed from a horizontal exit. 4.. Areas of refuge are not required in open parking garages.
1007.6.2 | Separation | Separation. Each area of refuge shall be separated from the remainder of the story by a smoke barrier complying with Section 709. Each area of refuge shall be designed to minimize the intrusion of smoke. Exceptions: 1. Areas of refuge located within a stairway enclosure. 2. Areas of refuge where the area of refuge and areas served by the area of refuge are equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2. | 1003.2.13.5.2 | Separation. Each area of refuge shall be separated from the remainder of the story by a smoke barrier complying with Section 709. Each area of refuge shall be designed to minimize the intrusion of smoke. Exceptions: 1. Areas of refuge located within a stairway enclosure. 2. Areas of refuge where the area of refuge and areas served by the area of refuge are equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2. | 1104.2.4 | Construction. Each area of refuge shall be separated from the remainder of the story by a smoke barrier having at least a one-hour fire-resistance rating. Smoke barriers shall extend to the roof or floor deck above. Doors in the smoke barrier shall be tightfitting smoke- and draft-control assemblies having a fire-protection rating of not less than 20 minutes. Doors shall be self-closing or automatic closing by smoke detection. An approved damper designed to resist the passage of smoke shall be provided at each point a duct penetrates the smoke barrier. Exception: Areas of refuge located within a stairway enclosure. | 1007.5.2 | Separation. Each area of refuge shall be separated from the remainder of the story by a smoke barrier complying with Section 712.0. Each area of refuge shall be designed to prevent the intrusion of smoke, except those areas of refuge located within a stairway enclosure or those areas of refuge where the area of refuge and all areas served by the area of refuge are equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1. | 1004.3.5.4 1004.3.5.9 | 1004.3.5.4 Each area of refuge shall be separated from the remainder of the story by a smoke barrier having at least a 1-hour fire resistance rating. Smoke barriers shall extend to the roof/floor deck above. Doors in the smoke barrier shall have a 20-minute fire resistance rating, except those in horizontal exits and exit enclosures. Doors shall be self-closing or automatic-closing by smoke detection. HVAC openings in smoke barriers where 20-minute doors are permitted shall be ducted and provided with a smoke actuated damper designed to resist the passage of smoke. 1004.3.5.9 Every area of refuge that is not protected by the automatic
sprinkler system shall be designed to prevent the intrusion of smoke. Exception: Areas of refuge located within a stair enclosure.
1008.1.8.6 | Delayed Egress Locks | Approved, listed, delayed egress locks shall be permitted to be installed on doors serving any occupancy except Group A, E and H occupancies in buildings that are equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or an approved automatic smoke or heat detection system installed in accordance with Section 907, provided that the doors unlock in accordance with Items 1 through 6 below. A building occupant shall not be required to pass through more than one door equipped with a delayed egress lock before entering an exit. 1. The doors unlock upon actuation | 1003.3.1.8.2 | Delayed egress locks. Approved, listed, delayed egress locks shall be permitted to be installed on doors serving an occupancy except Group A, E and H occupancies in buildings which are equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or an approved automatic smoke or heat detection system installed in accordance with Items 1 through 6 below. A building occupant shall not be required to pass through more than one door equipped with a delayed egress lock before entering an exit. 1. The doors unlock upon actuation of the automatic sprinkler system or automatic | 1003.3.1.10 | Special egress-control devices. When approved by the building official, exit doors in Group B; Group F; Group I, Division 2, Group M; Group R, Division 1 congregate residences serving as group-care facilities and Group S Occupancies may be equipped with approved listed special egress-control devices of the time-delay type, provided the building is protected throughout by an approved automatic sprinkler system and an approved automatic smoke-detection system. Such devices shall conform to all of the following: 1. The egress-control device shall automatically deactivate upon | 1017.4.1.2 | Special locking arrangements. In buildings that are equipped throughout with an automatic sprinkler system installed in accordance with Section 906.2.1 or with an automatic fire detection system, doors in means of egress serving occupancies in Use Group B, E, F, I, M, S or R, shall be unlocked or shall be equipped with approved egress control devices which shall unlock in accordance with items 1 through 7 below. A building occupant shall not be required to pass through more than one door equipped with a special locking device before entering an exit. 1. Actuation of the automatic sprinkler | 1012.6.1 | Except in Group A occupancies, doors in buildings protected throughout by an approved supervised automatic smoke detection system or automatic sprinkler system may be equipped with approved, listed, locking devices which shall: 1. Unlock upon activation of the approved supervised automatic smoke detection system, automatic fire detection system, or automatic sprinkler system, and/or 2. Unlock upon loss of power controlling the locking device, and in all cases 3. Initiate an irreversible process which will unlock the door within 15 seconds whenever a force of not more than 15lbs (67N) is applied to the
|  | of the automatic sprinkler system or automatic fire detection system. 2. The doors unlock upon loss of power controlling the lock or lock mechanism. 3. The door locks shall have the capability of being unlocked by a signal from the fire command center. 4. The initiation of an irreversible process which will release the latch in not more than 15 seconds when a force of not more than 15 pounds (67 N) is applied for 1 second to the release device. Initiation of the irreversible process shall activate an audible signal in the vicinity of the door. Once the door lock has been released by the application of force to the releasing |  | detection system. 2. The doors unlock upon loss of power controlling the lock or lock mechanism. 3. The door locks shall have the capability of being unlocked by a signal from the command center. 4. The initiation of an irreversible process which will release the latch in not more than 15 seconds (67N) is applied for 1 second to the release device. Initiation of the irreversible process shall activate an audible signal in the vicinity of the door. Once the door lock has been released by the application of force to the releasing device, relocking shall be by manual means only. Exception: Where approved a delay of not more than 30 |  | activation of either the sprinkler system or the smoke-detection system. 2. The egress-control device shall automatically deactivate upon loss of electrical power to any one of the following: 2.1 The egress-control device itself. 2.2 The smoke-detection system. 2.3 Mean of egress illumination as required by Section 1003.2.9. 3. The egress-control device shall be capable of being deactivated by a signal from a switch located in an approved location. 4. An irreversible process that will deactivate the egress-control device shall be initiated whenever a manual force of not more than 15 pounds (66.72N) is applied for two |  | system or automatic fire detection system. 2. Loss of power to the egress control device. 3. Loss of power to the building. 4. Capability of being unlocked manually by a signal from an emergency control station. 5. The initiation of an irreversible and automatic process that will release the latch within 15 seconds when a force of not more than 15 pounds (66N) is applied for 1 second to the release device and not relock until the door has been opened and returned to the closed position for not less than 30 seconds. Any reopening of the door shall restart the 30-second relocking cycle. Any attempt to exit which exceeds 1 |  | door or releasing device and not relock until the door has been opened. Once the irreversible process has started it shall activate a signal in the vicinity of the door for assuring those attempting to exit that the system is functional. Exceptions: Independent standby power is acceptable as long as the supervised automatic smoke detection system, automatic fire detection system, or automatic sprinkler system, when activated, has precedence over the standby power and unlocks the door. If a nonemergency system(s) operate, provided that the power outage does not disable these detection systems. If
|  | device, relocking shall be by manual means only. Exception: Where approved, a delay of not more than 30 seconds is permitted. 5. A sign shall be provided on the door located above and within 12 inches (305 mm) of the release device reading: PUSH UNTIL ALARM SOUNDS.DOOR CAN BE OPENED IN 15 [30]SECONDS. 6. Emergency lighting shall be provided at the door. |  | seconds is permitted. |  | seconds to the panic bar or other door-latching hardware. The egress-control device shall deactivate within an approved time period not to exceed a total of 15 seconds. The time delay established for each egress-control device shall not be field adjustable. 5. Actuation of the panic bar or other door-latching hardware shall activate an audible signal at the door. 6. The unlatching shall not require more than one operation. A sign shall be provided on the door located above and within 12 inches (305mm) of the panic bar or other door-latching hardware reading: KEEP PUSHING. THIS DOOR WILL OPEN IN ____ |  | second shall render the door openable. The time delay and the minimum relocking cycle time shall not be field adjustable. Exceptions: 1. An increase in the time delay to 30 seconds shall not be permitted except as approved by the code official. 2. An increase in the relocking cycle time to 45 seconds shall not be permitted except as approved by the code official. 6. Initiation of the irreversible process shall activate an audible alarm in the vicinity of the door. 7. A sign having block letters of 1 inch (25mm) in height shall be provided on the door above and within 12 inches (305mm) of the release device stating "Push until alarm sounds. Door |  | any of the detection systems are disabled in any way, standby controlling the locking devices will be interrupted. 2. The building official may approve a delay not to exceed 30 seconds provided that reasonable life safety is assured.
[6 empty] | SECONDS. ALARM WILL SOUND. Sign lettering shall be at least 1inch (25mm) in height and shall have a stroke of not less than 1/8 inch (3.2mm). Regardless of the means of deactivation, relocking of the egress-control device shall be by manual means only at the door. |  | can be opened in 15 seconds."
1013.3 | Common Path of Egress Travel | Common path of egress travel. In occupancies other than Groups H-1, H-2 and H-3, the common path of egress travel shall not exceed 75 feet (22 860 mm). In occupancies in Groups H-1, H-2, and H-3, the common path of egress travel shall not exceed 25 feet (7620 mm). Exceptions: 1. The length of a common path of egress travel in an occupancy in Groups B, F and S shall not be more than 100 feet (30 480 mm), provided that the building is equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1. 2. Where a tenant space in an occupancy in Groups B, S and U has | 1004.2.5 | Common path of egress travel. In occupancies other than Groups H-1, H-2 and H-3, the common path of egress travel shall not exceed 75ft (22860mm). In occupancies in Groups H-1, H-2 and H-3 the common path of egress travel shall not exceed 25ft (7620mm). Exceptions: 1. The length of a common path of egress travel in an occupancy in groups B, F and S shall not be more than 100ft (30480mm), provided that the building is equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1. With a tenant space in an occupancy in Groups B, S and U has an occupant load of not |  | No related section. | 1011.2.1 | Common path of travel. In occupancies in Use Group B, the length of a common path of travel shall not exceed 75ft (22860mm). Exceptions: 1. The length of a common path of travel in an occupancy in Use Group B shall not be more than 100ft (30480mm), provided that the building is equipped throughout with an automatic sprinkler system installed in accordance with Section 906.2.1. 2. Where a tenant space in an occupancy in Use Group B has an occupant load of not more than 30, the length of a common path of travel shall not be more than 100ft (30480mm). | 1004.1.3 | The common path of travel shall not exceed 75ft.
|  | an occupant load of not more than 30, the length of a common path of egress travel shall not be more than 100 feet (30 480 mm). 3. The length of a common path of egress travel in occupancies in Group I-3 shall not be more than 100 feet (30 480 mm). |  | more than 30, the length of a common path of egress travel shall not be more than 100ft (30480mm). 3. The length of a common path of egress travel in occupancies in Group I-3 shall not be more than 100ft (30480mm).
1014.2.1 | Two Exit or Exit Access Doorways | Two exits or exit access doorways. Where two exits or exit access doorways are required from any portion of the exit access, the exit doors or exit access doorways shall be placed a distance apart equal to not less than one-half of the length of the maximum overall diagonal dimension of the building or area to be served measured in a straight line between exit doors or exit access doorways. Interlocking or scissor stairs shall be counted as one exit stairway. Exceptions: 1. Where exit enclosures are provided as a portion of the required exit and are interconnected by a 1-hour fire-resistance-rated corridor conforming to the | 1004.2.2.1 | Two exit or exit access doorways. Where two exits or exit access doorways are required, from any portion of the exit access, the exit doors or exit access doorways shall be placed a distance apart equal to not less than one-half of the length of the building or area to be served measured in a straight line between exit doors or exit access doorways. Exceptions: 1. Where exit enclosures are provided as a portion of the required exit and are interconnected by a 1-hour fire-resistance-rated corridor conforming to the requirements of Section 1004.3.2, the required exit separation shall be measured along a direct line of travel | 1004.2.4 | Separation of exits or exit-access doorways. Where two or more exits or exit-access doorways are required from any level or portion of the building, at least two of the exits or exit-access doorways shall be placed a distance apart equal to not less than one-half of the length of the maximum overall diagonal dimension of the area served measured in a straight line between the center of such exits or exit-access doorways shall be arranged a reasonable distance apart so that if one becomes blocked, the other will be available. Exception: The separation distance determined in accordance with this section may be | 1006.4 1006.4.1 1017.2.2 | Remote location. Wherever more than one exit is required from any room, space or floor of a building such exits shall be placed as remote from each other as practicable, and shall be arranged and constructed to provide direct access in separate directions from any point in the area served so as to minimize the possibility that both exits will be blocked by any one fore or other emergency condition. 1006.4.1 Remoteness. Where two exits or two exit access doors are required, each shall be placed a distance apart equal to not less than one-half of the length of the maximum overall diagonal dimension of the building or area to be | 1004.1.4 | Where two or more exits or exit access doors are required, at least two of the exits or exit access doors shall be placed a distance apart equal to not less than one half of the length of the maximum overall diagonal dimension of the building or area to be served measured in a straight line between such exits or exit access doors. The two exits or exit access doors shall be so located and constructed to minimize the possibility that both nay be blocked by any one fire or emergency condition. Exception: When exit enclosures are provided as a portion of the required exit and are interconnected by a corridor conforming
|  | requirements of Section 1016, the required exit separation shall be measured along the shortest direct line of travel within the corridor. 2. Where a building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2, the separation distance of the exit doors or exit access doorways shall not be less than one-third of the length of the maximum overall diagonal dimension of the area served. |  | within the corridor. Exit enclosure walls shall not be less than 30ft (9144mm) apart at any point in direct line of measurement. 2. Where a building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2, the separation distance of the exit doors or exit access doorways shall not be less than one-third of the length of the maximum overall diagonal dimension of the area served. |  | measured along a direct path of exit travel within a fire-resistive corridor complying with Section 1004.3.4.3.1 serving exit enclosures. The walls of any such exit enclosure shall not be less than 30 ft(9144mm), measured in a straight line, from the walls of another exit enclosure. |  | served. Where exit enclosures are provided as a portion of the required means of egress and are interconnected by a corridor conforming to the requirements for corridor construction, the exit separation distance shall be measured along the line of travel within the corridor. In all other cases, the separation distance shall be measured in a straight line between exits or exit access doors. Exception: In buildings equipped throughout with an automatic sprinkler |  | to the requirements for 1-hour rated construction, the exit separation may be measured along a direct line of travel within the corridor.
system in accordance with Section 906.2.1 or 906.2.2, the minimum separation distance shall be one-fourth of the length of the maximum overall diagonal dimension. 1017.2.2 Location of doors. The required doorways opening from a room or space within a building and leading to an exit access shall be located as remote as practicable from each other and shall conform to Section 1006.4.1. The distance of exit access travel from any point in a room or space to a required exit door shall not exceed the limitations of Section 1006.5.
Table 1015.1 | Exit Access Travel Distance | Maximum travel distances for sprinklered and unsprinklered buildings based on occupancy. Allows 300' of travel distance for Group B, fully sprinklered. Allows 400' of travel distance for F-2 and S-2 occupancies without the roof vents. | Table 1004.2.4 | Same | 1004.2.5.2.1 1004.2.5.2.2 | 1004.2.5.2.1 Nonsprinklered buildings. In buildings not equipped with an automatic sprinkler system throughout, the travel distance shall not exceed 200ft (60960mm). 1004.2.5.2.2 Sprinklered buildings. In buildings equipped with an automatic sprinkler system throughout, the travel distance shall not exceed 250ft(76200mm). | Table 1006.5 | Similar; the travel distance allowance for Group B and U occupancies is more restrictive. Allows 250' in a sprinklered building for Group B and 250' in a sprinklered building for Group U. | Table 1004 | Allows 200' maximum travel in unsprinklered buildings and 250' in sprinklered buildings. Group H has a maximum travel of 100'. Group I Restrained requirements are in SBC 1024.2.6. Group I Unrestrained has a maximum travel of 150' in unsprinklered buildings, and 200' in sprinklered. Group S2 and open parking structures can have a maximum travel distance of 300' if unsprinklered and 400' if sprinklered.
1015.2 | Roof Vent Increase | Roof vent increase. In buildings which are one story in height, equipped with automatic heat and smoke roof vents complying with Section 910 and equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, the maximum exit access travel distance shall be 400 feet (122 m) for occupancies in Group F-1 or S. | 1004.2.4.1 | Roof vent increase. In buildings which are one story in height, equipped with automatic heat and smoke roof vents complying with Section 910 and equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, the maximum exit access travel distance shall be 400ft (122m) for occupancies in Group F-1 or S-1. | 1004.2.5.2.5 | Factory, hazardous and storage occupancies. In a one-story building classified as a Group H, Division 5 aircraft repair hangar, or as a Group F or Group S Occupancy, the travel distance shall not exceed 300ft (91440mm) and may be increased to 400ft (121920mm) if the building is equipped with an automatic sprinkler system throughout and is also provided with smoke and heat ventilation as specified in Section 906. | 1006.5.1 | Roof vent increase. In buildings which are one story in height, equipped with automatic heat and smoke roof vents complying with Section 923.0 and equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1, the exit access travel distance limitation in Table 1006.5 for occupancies in Use Group F-1 or S-1 shall be increased to 400ft (122m). | 1004.1.6 | In one-story Group F and Group S buildings equipped with automatic heat and smoke vents complying with this section and sprinklered, the travel distance may be increased to 400ft (122m). Smoke and heat vents shall be constructed and installed in a manner approved by the building official.
1016.1 | Construction | Construction. Corridors shall be fire-resistance rated in accordance with Table 1016.1. The corridor walls required to be fire-resistance rated shall comply with Section 708 for fire partitions. Exceptions: 1. A fire-resistance rating is not required for corridors in an occupancy in Group E where each room that is used for instruction has at least one door directly to the exterior and rooms for assembly purposes have at least one-half of the required means of egress doors opening directly to the exterior. Exterior doors specified in this exception are required | 1004.3.2.1 | Construction. Corridors shall be fire-resistance-rated in accordance with Table 1004.3.2.1. The corridor walls required to be fire-resistance-rated shall comply with Section 708 for fire partitions. Exceptions: 1. A fire-resistance rating is not required for corridors in an occupancy in Group E where each room that is used for instruction has at least one door directly to the exterior and rooms for assembly purposes have at least one-half of the required means of egress doors opening directly to the exterior. Exterior doors specified in this exception are required to be at ground level. 2. A fire-resistance rating is not required for corridors | 1004.3.4.3 | Construction. Corridors shall be fully enclosed by walls, a floor, a ceiling and permitted protected openings. The walls and ceilings of corridors shall be constructed of fire-resistive materials as specified in Section 1004.3.4.3.1. Exceptions: 1. One-story buildings housing Group F, Division 2 and Group S, Division 2 Occupancies. 2. Corridors more than 30 ft (9144mm) in width where occupancies served by such corridors have at least one exit independent from the corridor (See chapter 4 for covered malls.) 3. In Group I, Division 3 Occupancies such as jails, prisons, reformatories and | 1011.4 | Enclosure. All corridors shall be fire resistance rated in accordance with Table 1011.4 based on the use group of the space and the total required capacity of all of the exits from the corridor. The corridor walls shall comply with Section 711.0. Exceptions: A fire resistance rating is not required for corridors in an occupancy in Use Group E where each room that is occupied for instruction or assembly purposes has at least one-half of the required means of egress doors opening directly to the exterior of the building at ground level. 2. A fire resistance rating is not required for corridors contained within a dwelling unit or guestroom in an | 1003.3.7 Table 704.2.4 | Similar; sprinklered buildings, corridors of assembly with over 30 people, educational, hazardous, R1, and R2 occupancies over 10 occupants are required to have rated corridors.
|  | to be at ground level. 2. A fire-resistance rating is not required for corridors contained within a dwelling or sleeping unit in an occupancy in Group R. 3. A fire-resistance rating is not required for corridors in open parking garages. 4. A fire-resistance rating is not required for corridors in an occupancy in Group B which is a space requiring only a single means of egress complying with Section 1014.1. |  | contained within a dwelling unit or a guestroom in an occupancy in Group R. 3. A fire-resistance rating is not required for corridors in open parking garages. 4. A fire-resistance rating is not required for corridors in an occupancy in Group B which is a space requiring only a single means of egress complying with Section 1004.2.1. |  | similar buildings with open-barred cells forming corridor walls, the corridors and cell doors need not be fire-resistive. 4. Corridor walls and ceilings needs not be of fire-resistive construction within office spaces having an occupant load of 100 or less when the entire story in which the space is located is equipped with an automatic sprinkler system throughout and an automatic smoke-detection system installed within the corridor. The actuation of any detector shall activate alarms audible in all areas served by the corridor. 5. Corridor walls and ceilings need not be of fire-resistive construction within office spaces having |  | occupancy in Use Group R.
an occupant load of 100 or less when the building in which the pace is located is equipped with an automatic sprinkler system throughout. 6. In Group B office buildings of Type I, Type II-FR and Type II-one-hour construction, corridor walls and ceilings need not be of fire-resistive construction within office spaces of a single tenant when the entire story is located is equipped with an approved automatic sprinkler system with an automatic smoke-detection system is installed within the corridor. The actuation of any detector shall activate alarms audible in all areas served by the corridor. Corridor floors are not required
to be of fire-resistive construction unless specified by some other provision of this code. Corridors in buildings of Type I or II construction shall be of noncombustible construction, except where combustible materials are permitted in applicable building elements by other provisions of this code. Corridors in buildings of Type III, IV or V construction may be of combustible or noncombustible construction.
Table 1016.1 | Corridor Fire-Resistance Ratings | Identifies the required fire rating of corridors based on occupancy, occupant load, and whether the building is sprinklered. | Table 1004.3.2.1 | Same |  | No related section. | Table 1011.4 | Similar; allows reduced fire ratings for I-1, I-3, and R occupancies when protected with fire sprinklers. | Table 704.2.4 | Similar
1016.3 | Dead Ends | Dead ends. Where more than one exit or exit access doorway is required, the exit access shall be arranged such that there are no dead ends in corridors more than 20 feet (6096 mm) in length. Exceptions: 1. In occupancies in Group I-3 of Occupancy Condition 2, 3 or 4 (see Section 308.4), the dead end in a corridor shall not exceed 50 feet | 1004.3.2.3 | Dead-ends. Where more than one exit or exit access doorway is required, the exit access shall be arranged such that there are no dead ends in corridors more than 20ft (6096mm) in length. Exceptions: 1. IN occupancies in Group I-3 of Occupancy Conditions 2, 3 or 4 (See Section 308.4), the dead end in a corridor shall not exceed 50ft (15240mm). 2. IN occupancies in Groups B and F where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, the length of dead-end corridors shall not exceed 50ft (15240mm). 3. A dead- | 1004.2.6 | Dead Ends. Where more than one exit or exit-access doorway is required, the exit access shall be arranged such that there are no dead ends in hallways and corridors more than 20 feet (6096mm) in length. | 1011.2 | Dead-ends. Exit access passageways and corridors in all stories which serve more than one exit shall provide direct connection to such exits in opposite directions from any point in the passageway or corridor, insofar as practicable. The length of a dead-end passageway or corridor shall not be more than 20ft (6096mm). Exceptions: 1. In occupancies in Use Group I-3 of Occupancy Conditions II, III, IV (see Section 308.4), the dead-end in a corridor, hallway or aisle shall not exceed 50ft (15240mm). 2. In occupancies in Use Group B where passageways are | 1005.2 | Dead-End pockets or hallways. Exits and exit access shall be so arranged that dead-end pockets or hallways in excess of 20ft (6096mm)long shall not occur.
|  | (15 240 mm). 2. In occupancies in Groups B and F where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, the length of dead-end corridors shall not exceed 50 feet (15 240 mm). 3. A dead-end corridor shall not be limited in length where the length of the dead-end corridor is less than 2.5 times the least width of the dead-end corridor. |  | end corridor shall not be limited in length where the length of the dead-end corridor is less than 2.5 times the least width of the dead-end corridor. |  |  |  | bounded by furniture, counters, partitions or similar dividers not more than 6ft (1829mm) in height, the length of a dead-end passageway shall not be more than 50ft (15240mm). 3. In occupancies in Use Group B where the building is equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1, the length of dead-end corridors or passageways shall not exceed 50ft (15240mm). 4. Passageways or corridors within spaces with one means of egress. 5. A dead-end passageway or corridor shall not be limited in length where the length of the dead-end passageway or corridor is less than
2.5 times the least width of the dead-end passageway or corridor.
1016.5 | Corridor Continuity | Corridor continuity. Fire-resistance-rated corridors shall be continuous from the point of entry to an exit, and shall not be interrupted by intervening rooms. Exception: Foyers, lobbies or reception rooms constructed as required for corridors shall not be construed as intervening rooms. | 1004.3.2.5 | Corridor continuity. Fire-resistance-rated corridors shall be continuous from the point of entry to an exit. Fire-resistance-rated corridors shall not be interrupted by intervening rooms. Exceptions: 1. Foyers, lobbies or reception rooms constructed as intervening rooms. 2. IN Group B buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, corridors are permitted to lead through enclosed elevator lobbies provided all areas of the building have access to at least one required exit without passing through the elevator lobby. | 1004.3.4.4 | Intervening rooms. Corridors shall not be interrupted by intervening rooms. Exceptions: 1. Foyers, lobbies or reception rooms constructed as required for corridors shall not be construed as intervening rooms. 2. In fully sprinklered office buildings, corridors may lead through enclosed elevator lobbies if all areas of the building have access to at least one required exit without passing through the elevator lobby. |  | No related section. |  | No related section.
1018.2 | Buildings with One Exit | Buildings with one exit. Only one exit shall be required in buildings as described below: 1. Buildings described in Table 1018.2, provided that the building has not more than one level below the first story above grade plane. 2. Buildings of Group R-3 occupancy. 3. Single-level buildings with the occupied space at the level of exit discharge provided that the story or space complies with Section 1014.1 as a space with one means of egress. | 1005.2.2 | Buildings with one exit. Only one exit shall be required in buildings as described below: 1. Buildings described Table 1005.2.2, provided that the building has not more than one level below the first story. 2. Buildings of Group R-3 occupancy. 3. Single-level buildings with the occupied space at the level of exit discharge provided that the story or space complies with Section 1004.2.1 as a space with one means of egress. |  | No related section. | 1010.3 | Buildings with one exit. Only one exit shall be required in: 1. Occupancies in the use groups shown in Table 1010.3 provided that the building has not more than one level below the level of exit discharge; and 2. Occupancies in Use Group R-3. | 1004.2.1 | There shall be not less than two approved independent exits, accessible to each tenant area, serving every story, except in Group R3 occupancies and as modified in 1018.
Table 1018.2 | Buildings with One Exit | Table is the companion to Section 1018.2. See notes c and d. | Table 1005.2.2 | Same |  | No related section. | Table 1010.3 | Table is the companion to BNBC 1010.3. | 1004.2.1 | There shall be not less than two approved independent exits, accessible to each tenant area, serving every story, except in Group R3 occupancies and as modified in 1018.
1019.1.8.2 | Enclosure Access | Enclosure access. Access to the stairway within a smokeproof enclosure shall be byway of a vestibule or an open exterior balcony. Exception: Access is not required by way of a vestibule or exterior balcony for stairways using the pressurization alternative complying with Section 909.20.5. | 1005.3.2.5.2 | Enclosure access. Access to the stairway within a smokeproof enclosure shall be by way of an open exterior balcony. Exception: Access is not required by way of vestibule or exterior balcony for stairways using the pressurization alternative complying with Section 909.20.5. | 1005.3.3.7.1 | Vestibules. Pressurized exit enclosures shall be provided with a pressurized entrance vestibule that complies with the requirements of this section. | 1015.3 | Access. Access to the stair shall be from every story and shall be by way of a vestibule or by way of an open exterior balcony, except that a vestibule or balcony is not required for a smokeproof enclosure that consists of a pressurized stairway complying with Section 1015.7. The minimum dimension of the vestibule shall not be less than the required width of the corridor leading to the vestibule but shall not have a width of less than 44 inches (1118mm) and shall not have a length of less that 72 inches (1829mm) in the direction of egress travel. | 1005.6.7 | Access to the stairway shall be by way of vestibule or by way of an open exterior balcony of noncombustible materials. Exception: Access by way of a vestibule or an open exterior balcony is not required when the stairway meets the requirements of 1005.6.9.2, 1005.6.9.9 and 1005.6.9.10 and is located in a fully sprinklered building.
1022.6 | Exterior Stairway Protection | Exterior ramps and stairway protection. Exterior exit ramps and stairways shall be separated from the interior of the building as required in Section 1019.1. Openings shall be limited to those necessary for egress from normally occupied spaces. Exceptions: 1. Separation from the interior of the building is not required for occupancies, other than those in Group R-1 or R-2, in buildings that are no more than two stories above grade where the level of exit discharge is the first story above grade. 2. Separation from the | 1005.3.6.5 | Exterior stairway protection. Exterior exit stairs shall be separated from the interior of the building as required in Section 1005.3.2. Openings shall be limited to those necessary for egress from normally occupied spaces. Exceptions: 1. Separation from the interior of the building is not required for occupancies, other than those in Group R-1 or R-2, in buildings that are no more than two stories above grade where the level of discharge is the first story above grade. 2. Separation from the interior of the building is not required where the exterior stairway is served by an exterior balcony that connects two remote exterior | 1006.3.3.3 1006.3.3.4 | 1006.3.3.3 Protection of exterior wall openings. All openings in the exterior wall below and within 10 feet (3048mm), measured horizontally, of an exterior exit stairway serving a building over two stories in height or a floor level having such openings in two or more floors below shall be protected by fixed or self-closing fire assemblies having a three-fourths-hour fire-protection rating. Exceptions: 1. Group R, Division 3 Occupancies. 2. Openings may be unprotected where two separated exterior stairways are served by a common exterior exit balcony. 3. Protection of openings is not | 1014.12.2 | Protection. Exterior exit stairs shall be separated from the interior of the building by walls with a fire resistance rating of not less than 1 hour, with fixed or self-closing opening protectives as required in Section 1014.11. This protection shall extend vertically from a point 10ft (3048mm) above the topmost landing or the roof line, whichever is lower, down to the ground, and shall extend horizontally 10ft (3048mm) from each side of the stairway. Openings within the horizontal 10-foot (3048mm) extension of the protected walls beyond the stairway shall be equipped with fixed 3/4-hour opening protective assemblies. Exceptions: 1. | 1006.2.4 | Exterior stairs shall be separated from the interior of the building by walls with a fire resistance rating of not less than 1 hour, with fixed or self-closing opening protectives as required for enclosed stairs. The protection shall extend vertically from the ground to a point of 10ft (3048mm)above the topmost landing or the roof line, whichever is lower, and horizontally 10ft (3048mm) from each side of the stairway. Openings within 10ft (3048mm) horizontal extension of the protected walls beyond the stairway shall be equipped with fixed 3/4hour assemblies. Exceptions: 1. Exterior stairways may be
|  | interior of the building is not required where the exterior ramp or stairway is served by an exterior ramp and/or balcony that connects two remote exterior stairways or other approved exits, with a perimeter that is not less than 50 percent open. To be considered open, the opening shall be a minimum of 50 percent of the height of the enclosing wall, with the top of the openings no less than 7 feet (2134 mm) above the top of the balcony. 3. Separation from the interior of the building is not required for an exterior ramp or stairway located in a building or structure |  | stairways or other approved exits, with a perimeter that is not less than 50% open. To be considered open, the opening shall be a minimum of 50% of the height of the enclosing wall, with the top of the openings no less than 7 ft (2134mm) above the top of the balcony. 3. Separation from the interior of the building is not required for an exterior stairway located in a building or structure that is permitted to have unenclosed interior stairways in accordance with Section 1005.3.2. 4. Separation from the interior of the building is not required for exterior stairways connected to open-ended corridors, provided that: 4.1. The |  | required for open parking garages conforming to Section 311.9. Detailed requirements. Except for construction and opening protection as specified in Sections 1006.3.3.2 and 1006.3.3.3, exterior exit stairways shall comply with the applicable requirements for stairways as specified in Section 1003.3.3. |  | Occupancies, other than those in Use Group R-1 or R-2, in buildings that are two-stories or less above grade where the level of exit discharge is the first story above grade. 2. Separation from the interior of the building is not required where the exterior stairway is served by an exterior access balcony that connects two remote exterior stairways or other approved exits, with a perimeter which is not less than 50% open. To be considered open, the opening shall be a minimum of 50% of the height of the enclosing wall, with the top of the openings not less than 7ft (2134mm) above the top of the balcony. 3. Separation from the interior of the building |  | unprotected when serving an exterior exit access balcony which has two exterior stairways, remotely located as required in 1006.2.2. 2. Such protection is not required in two-story buildings where there is a second exit remotely located as required in 1006.2.2.
|  | that is permitted to have unenclosed interior stairways in accordance with Section 1019.1. 4. Separation from the interior of the building is not required for exterior ramps or stairways connected to open-ended corridors, provided that Items 4.1 through 4.4 are met: 4.1. The building, including corridors and ramps and/or stairs, shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. 4.2. The open-ended corridors comply with Section 1016. 4.3. The open-ended corridors are |  | building, including corridors and stairs, shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. 4.2. The open-ended corridors comply with Section 1004.3.2.. 4.3. The open-ended corridors are connected on each end to an exterior exit stairway complying with Section 1005.3.6. 4.4 At any locations in an open-ended corridor where a change of direction exceeding 45degrees (0.79rad) occurs, a clear opening of not less than 35sq ft (3.3m2) or an exterior stairway shall be provided. Where clear openings are provided, they shall be located so as to minimize the accumulation of smoke or toxic gases. |  |  |  | is not required for an exterior stairway located in the building or structure that is permitted to have unenclosed interior exit stairways in accordance with Section 1014.11.
connected on each end to an exterior exit ramp or stairway complying with Section 1022. 4.4. At any location in an open-ended corridor where a change of direction exceeding 45 degrees (0.79 rad) occurs, a clear opening of not less than 35 square feet (3.3 m2) or an exterior ramp or stairway shall be provided. Where clear openings are provided, they shall be located so as to minimize the accumulation of smoke or toxic gases.
1023.1 | General | General. Exits shall discharge directly to the exterior of the building. The exit discharge shall be at grade or shall provide direct access to grade. The exit discharge shall not reenter a building. Exceptions: 1. A maximum of 50 percent of the number and capacity of the exit enclosures is permitted to egress through areas on the level of discharge provided all of the following are met: 1.1. Such exit enclosures egress to a free and unobstructed way to the exterior of the building, which way is readily visible and identifiable from the point of termination of the exit | 1006.1 | General. Exits shall discharge directly to the exterior of the building. The exit discharge shall be at grade or shall provide direct access to grade. The exit discharge shall not enter a building. Exceptions: 1. A maximum of 50% of the number and capacity of the exit enclosures is permitted to egress through areas on the level of discharge provided all of the following are met: 1.1 Such exit enclosures egress to a free and unobstructed way to the exterior of the building, which way is readily visible and identifiable from the point of termination of the exit enclosure. 1.2. The entire area of the level of discharge is separated from areas | 1006.1 1005.3.3.3 | 1006.1 General. The exit discharge is that portion of the means of egress system between the exit and the public way. Components that may be selectively included in exit discharge include exterior exit balconies, exterior exit stairways, exterior exit ramps and exit courts, in addition to those common means of egress components described in Section 1003.3. Exception: When approved by the building official, the exit discharge may lead to a safe dispersal area on the same property as the building being exited. The proximity and size of such safe dispersal area shall be based on such factors as the occupant load served, the mobility of | 1006.3 1020.1 1020.3 1020.3.1 1020.3.2 1020.4 1020.6 | Exit discharge. All exits shall discharge directly at a public way or at a yard, court or open space of the required width and size to provide all occupants with a safe access to a public way. 1020.1 Passageways. Every required interior and exterior exit element which does not adjoin a public way shall be directly connected to the public way or to an open court leading to the public way by an enclosed passageway at the level of exit discharge, constructed in accordance with the requirements for the enclosure of the exit it serves, or through lobbies or vestibules as provided for in this section. Building areas below the level of exit discharge shall be | 1010.1.1 1010.3 1010.4 | 1010.1.1 Unless directly connected to a public way or to a space leading to a public way, required exits shall be connected to an exit court, exit passageway, or vestibule leading to a public way. 1010.3 Exit passageways. Exit passageways shall be constructed in accordance with 704.2.1.2, 1006.1.3, and 1006.1.3.1, with a fire resistance rating equivalent to shaft enclosures in Table 705.1.2. Exceptions: A maximum 50% of the required number of exits and 50% of the required exit capacity shall be permitted to discharge through areas on the level of exit discharge provided all the following are met: 1.
|  | enclosure. 1.2. The entire area of the level of discharge is separated from areas below by construction conforming to the fire-resistance rating for the exit enclosure. 1.3. The egress path from the exit enclosure on the level of discharge is protected throughout by an approved automatic sprinkler system. All portions of the level of discharge with access to the egress path shall either be protected throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2, or |  | below by construction conforming to the fire-resistance rating for the exit enclosure. 1.3. The level of discharge is protected throughout by an approved automatic sprinkler system and any other portion of the level of discharge with access to the discharge area is protected throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2 or separated from the other portions of the building in accordance with the requirements for the enclosure of exits. 2. A maximum of 50% of the number and capacity of the exit enclosures is permitted to egress through a vestibule |  | occupants, the type of construction of the building, the fire-protection features of the building, the height of the building and the degree of hazard of the occupancy. In any case, such safe dispersal areas shall not be located less than 50 ft (15240mm) from the building served. (See Section 1007 for means of egress from safe dispersal areas.) General level areas designated as an exit discharge component for a building shall be permanently maintained. Such areas shall be developed or otherwise altered in their capacity to provide for a continuous, unobstructed and undiminished means |  | separated from the passageway in accordance with the requirements for the enclosure of exits. 1020.3 Lobby. Where an exit discharges into an interior lobby located at the level of exit discharge , the story containing the lobby shall be equipped throughout with an automatic sprinkler system installed in accordance with Section 906.2.1 or 906.2.2. Opening protectives shall be required in accordance with Table 717.1 at the point in which an enclosed exit stairway discharges into a lobby. Exception: An automatic sprinkler system is not required in areas that are separated from the lobby by fire |  | Such exits discharge to a free and unobstructed way to the exterior of the building, such way being readily visible and identifiable from the point of discharge at the exit, and 2. the entire area is separated from areas below by construction having a fire resistance rating not less than the required for the exit enclosure, and 4. Any other portion of the level of discharge with access to the area of discharge is protected throughout by an approved automatic sprinkler system or separated from the area of discharge in accordance with the requirements for the enclosure of exitways.
|  | separated from the egress path in accordance with the requirements for the enclosure of exits. 2. A maximum of 50 percent of the number and capacity of the exit enclosures is permitted to egress through a vestibule provided all of the following are met: 2.1. The entire area of the vestibule is separated from areas below by construction conforming to the fire-resistance rating for the exit enclosure. 2.2. The depth from the exterior of the building is not greater than 10 feet (3048 mm) and the length is not greater than 30 feet (9144 mm). 2.3. The area is separated from the remainder of the level of exit discharge by construction |  | provided all of the following are met: 2.2 The entire area of the vestibule is separated from areas below by construction conforming to the fire-resistance rating for the exit enclosure. 2.2. The depth from the exterior of the building is not greater than 10ft (3048mm) and the length is not greater than 30ft (9144mm). 2.3. The area is separated from the remainder of the level of exit discharge by construction providing protection at least the equivalent of approved wired glass in steel frames. 2.4. The area is used only for means of egress and exits directly to the outside. |  | of egress for building occupants. If such areas are sold independent of the building they serve, an exit discharge complying with the requirements of Section 1006 shall be provided for such building. 1005.3.3.3 Extent of enclosure. Exit enclosures shall be continuous and fully enclose all portions of the stairway or ramp to include parts of floors connecting stairway flights. Exit enclosures shall exit directly to the exterior of the building or shall include an exit passageway on the ground floor leading from the exit enclosure directly to the exterior of the building. Openings into the exit passageway shall comply with the |  | separation assemblies (see Section 709.0) have a fire resistance rating of not less than that required for exit enclosures. 1020.3.1 ??? 1020.3.2 ??? 1020.4 Width and height. The clear width of the passageway shall not be less than the width required for capacity of the exit stairways leading thereto and all required exit doorways opening into the passageway. Such passageway shall have a minimum width of 44 inches (1118mm) and minimum clear ceiling height if 8ft (23438mm). 1020.6 ??? |  | 1010.4 Vestibules. An exit may discharge into an interior vestibule which meets the following criteria: 1. The depth from the exterior of the building is not greater than 10ft (3048mm) and the length is not greater than 20ft (6096mm), and 2. The vestibule is separated from the remainder of the level of exit discharge by construction providing protection equivalent to that provided by 1/4inch (6mm) thick labeled wired glass in steel frames.
|  | providing protection at least the equivalent of approved wired glass in steel frames. 2.4. The area is used only for means of egress and exits directly to the outside. 3. Stairways in open parking garages complying with Section 1019.1, Exception 5, are permitted to egress through the open parking garage at the level of exit discharge. |  |  |  | requirements of Section 1005.3.3.5. Exceptions: 1. Exit passageways are not required from unenclosed stairways or ramps. 2. In office buildings, and Group I, Division 1.1 hospitals and nursing homes, a maximum of 50% of the exits may pass through a street-floor lobby, provided the entire street floor is protected with an automatic sprinkler system.
1024.6.2 | Smoke-Protected Seating | Smoke-protected seating. The clear width of the means of egress for smoke-protected assembly seating shall be not less than the occupant load served by the egress element multiplied by the appropriate factor in Table 1024.6.2. The total number of seats specified shall be those within a single assembly space and exposed to the same smoke-protected environment. Interpolation is permitted between the specific values shown. A life safety evaluation, complying with NFPA 101, shall be done for a facility utilizing the reduced width requirements of Table 1024.6.2 for smoke-protected | 1008.5.2 | Smoke-protected seating. The clear width of the means of egress for smoke-protected assembly seating shall not be less than the occupant load served by the egress element multiplied by the appropriate factor in Table 1008.5.2. The total number of seats specified shall be those within a single assembly space and exposed to the same smoke-protected environment. Interpolation is permitted between the specific values shown. A Life Safety Evaluation, complying with NFPA 101, shall be done for a facility utilizing the reduced width requirements of Table 1008.5.2 for smoke-protected assembly seating. | 1004.3.2.3.1 | Width. The clear width of aisles shall be based on the number of fixed seats served by such aisles. The required width of aisles serving fixed seats shall not be used for any other purpose. The minimum clear width of aisles in buildings without smoke-protected assembly seating shall be in accordance with Table 10-C. The minimum clear width of aisles in buildings where smoke-protected assembly seating has been provided, and for which an approved life-safety evaluation has also been conducted, shall be in accordance with Table 10-D. For Table 10-D, the number of seats specified must be within a single assembly place, and | 1013.5 | Aisles. Aisles shall be provided in all seating facilities. An aisle is not required where all of the following conditions exist: 1. Seats are without backrests. 2. The rise from row to row does not exceed 6inches (152mm) per row. 3. The row spacing does not exceed 28inches (711mm) unless the seaboards and footboards are at the same elevation. 4. The number of rows does not exceed 16inches in height. 5. The first seaboard is not more than 12inches (305mm) above the ground, floor surface or cross aisle below. 6. Seaboards have a continuous flat surface. 7. Seaboards provide a walking surface with a minimum width of 11 | 1019.11.10.3 | Smoke-protected assembly seating. The minimum clear width of aisles and other means of egress for smoke-protected assembly seating shall provide sufficient capacity in accordance with the following table. The number of seats specified shall be within a single assembly space and interpolation shall be permitted between the specific values shown. Table omitted.
|  | assembly seating. Exception: For an outdoor smoke-protected assembly with an occupant load not greater than 18,000, the clear width shall be determined using the factors in Section 1024.6.3. |  |  |  | interpolation shall be permitted between the specified values shown. For both tables, the minimum clear widths shown shall be modified in accordance with the following: 1. Where risers exceed 7 inches (178mm) in height, multiply the stairway width in the tables by factor A, where. formula omitted.. Where risers do not exceed 7 inches (178mm) in height, A=1. 2. Stairways not having a handrail within a 30-inch (762mm) horizontal distance shall be 25% wider than otherwise calculated, i.e., multiply by B=1.25. For all other stairs, B=1. 3. Ramps steeper than 1 unit vertical in 10 units horizontal(10% slope) where used in |  | inches (279mm). 8. Egress from seating is not restricted by rails, guards, or other obstructions.
ascent shall have their width increased by 10%, i.e., multiply by C=1.10. For ramps not steeper than 1 unit vertical in 10 units horizontal (10% slope), C=1. Where fixed seats are arranged in rows, the clear width of aisles shall not be less than set forth above or less than the following minimum widths: 3.1 Forty-eight inches (1219mm) for stairways having seating on both sides. 3.2 Thirty-six inches (914mm) for stairways having seating on one side. 3.3 Twenty-three inches (584mm) between a stairway handrail and seating where the aisles are subdivided by the handrail. 3.4 Forty-two inches (1067mm) for level or ramped aisles having seating on both
sides. 3.5 Thirty-six inches (914mm) for level or ramped aisles having seating on one side. 3.6 Twenty-three inches (584mm) between a stairway handrail and seating where an aisle does not serve more than five rows on one side. Where exit access is possible in two directions, the width of such aisles shall be uniform throughout their length. Where aisles converge to form a single path of exit travel, the aisle width shall not be less than the combined required width of the converging aisles.
1025.1 | General | General. In addition to the means of egress required by this chapter, provisions shall be made for emergency escape and rescue in Group R as applicable in Section 101.2 and Group I-1 occupancies. Basements and sleeping rooms below the fourth story above grade plane shall have at least one exterior emergency escape and rescue opening in accordance with this section. Where basements contain one or more sleeping rooms, emergency egress and rescue openings shall be required in each sleeping room, but shall not be required in adjoining areas of | 1009.1 | General. In addition to the means of egress required by this chapter, provisions shall be made for emergency escape and rescue in Group R as applicable in Section 101.2 and Group I-1 occupancies. Basements and sleeping rooms below the fourth story shall have at least one exterior emergency escape and rescue in accordance with this section. Such opening shall open directly into a public street, public alley, yard or court. Exceptions: 1. In other than Group R-3 occupancies as applicable in Section 101.2, buildings equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1 | 310.4 | Access and Means of Egress Facilities and Emergency Escapes. Means of egress shall be provided as specified in Chapter 10 (See also Section 1007.6.2 for exit markings.) Access to, and egress from, buildings required to be accessible shall be provided as specified in Chapter 11. Basements in dwelling units and every sleeping room below the fourth story shall have at least one operable window or door approved for emergency escape or rescue that shall open directly into a public street, public alley, yard or exit court. the emergency door or window shall be operable from the inside to provide a full, | 1010.4 | Emergency escape and rescue. Every sleeping room below the fourth story in occupancies in Use Groups R and I-1 shall have at least one operable window or exterior door approved for emergency escape or rescue. Each emergency escape and rescue window shall have a minimum net clear opening of 5.7sq ft (0.53m2). the net clear opening shall be at least 24inches (610mm) in height and at least 20 inches (508mm) in width. The net clear opening dimensions shall be obtained by the normal operation of the window from the inside. Where windows are provided for emergency escape and rescue, the | 1005.4.1 | Where required. Every sleeping room located on the first, second, and third story or within basements of Group R occupancies shall have at least one exterior emergency escape and rescue opening. Exceptions: 1. Buildings equipped with an approved automatic sprinkler system. 2.. Sleeping rooms provided with a door to a corridor having access to two remote exits in opposite directions. 3. The emergency escape and rescue opening may open onto a balcony within an atrium provided the balcony provides access to an exit and the dwelling unit or sleeping room has a means of egress which is not open to the atrium.
|  | the basement. Such opening shall open directly into a public street, public alley, yard or court. Exceptions: 1. In other than Group R-3 occupancies as applicable in Section 101.2, buildings equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. 2. In other than Group R-3 occupancies as applicable in Section 101.2, sleeping rooms provided with a door to a fire-resistance-rated corridor having access to two remote exits in opposite directions. 3. The emergency escape and rescue opening is permitted |  | or 903.3.1.2. 2. In other than Group R-3 occupancies as applicable in Section 101.2, sleeping rooms provided with a door to a fire-resistance-rated corridor having access to two remote exits in opposite directions. 3. The emergency escape and rescue opening is permitted to open onto a balcony within an atrium in accordance with the requirements of Section 404 provided the balcony provides access to an exit and the dwelling unit or sleeping room has a means of egress that not open to the atrium. 4. Basements with a ceiling height of less than 80 inches (2032mm) shall not be required to have emergency escape |  | clear opening with the use of separate tools. Exception: The window or door may open into an atrium complying with Sections 402 provided the window or door opens onto an exit-access balcony and the dwelling unit or guest room has en exit or exit-access doorway that does not open to the atrium. Escape or rescue windows shall have a minimum net clear openable area of 5.7 sq ft (0.53m2). The minimum net clear openable height dimension shall be 24 inches (610mm). The minimum net clear openable width dimension shall be 20 inches (508mm). When windows are provided as a means of escape or rescue, they shall have a finished sill |  | windows shall have the bottom of the clear opening not more than 44inches (1118mm) above the floor. Bars, grilles or screens placed over emergency escape windows shall be releasable or removable from the inside without the use of a key, tool or force greater than that which is required for normal operation of the window. Exceptions: 1. The minimum net clear opening for grade floor windows shall be 5sq ft (0.47m2). 2. An outside window or an exterior door for emergency escape is not required in buildings where the sleeping room is provided with a door to a corridor having access to two remote exits in opposite
|  | to open onto a balcony within an atrium in accordance with the requirements of Section 404, provided the balcony provides access to an exit and the dwelling unit or sleeping unit has a means of egress that is not open to the atrium. 4. Basements with a ceiling height of less than 80 inches (2032 mm) shall not be required to have emergency escape and rescue windows. 5. High-rise buildings in accordance with Section 403. 6. Emergency escape and rescue openings are not required from basements or sleeping rooms which have an exit door or exit access door that |  | and rescue windows. |  | height not more than 44 inches (1118mm) above the floor. Escape and rescue windows with a finished sill height below the adjacent ground elevation shall have a window well. Window wells at escape or rescue windows shall comply with the following: 1. The clear horizontal dimensions shall allow the window to be fully opened and provide a minimum accessible net clear opening of 9 sq ft (0.84m2), with a minimum dimension of 36 inches (914mm). 2. Window wells with a vertical depth of more than 44 inches (1118mm) shall be equipped with an approved permanently affixed ladder or stairs that are accessible with the window in the |  | directions. 3. An outside window or an exterior door for emergency escape is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1 or 906.2.2.
|  | opens directly into a public street, public alley, yard, egress court or to an exterior exit balcony that opens to a public street, public alley, yard or egress court. 7. Basements without habitable spaces and having no more than 200 square feet (18.6 square meters) in floor area shall not be required to have emergency escape windows. |  |  |  | fully open position. The ladder or stairs that are accessible with the window in the fully open position. The ladder or stairs shall not encroach into the required dimensions of the window well by more that 6 inches (152mm). Bars, grilles, grates or similar devices may be installed on emergency escape or rescue windows, doors or window wells, provided: 1. The devices are equipped with approved release mechanisms that are openable from the inside without the use of a key or special knowledge or effort; and 2. The building is equipped with smoke detectors installed in accordance with Section 310.9.
2606.7.4 | Fire Suppression System | Fire suppression system. In buildings that are equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, plastic light-diffusing systems shall be protected both above and below unless the sprinkler system has been specifically approved for installation only above the light-diffusing system. Areas of light-diffusing systems that are protected in accordance with this section shall not be limited. | 2606.7.4 | Fire suppression system. In buildings that are equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, plastic light-diffusing systems shall be protected both above and below unless the sprinkler system has been specifically approved for installation only above the light-diffusing system. Areas of light-diffusing systems that are protected in accordance with this section shall not be limited. | 2603.8.2 | Limitations. A plastic light-diffusing system shall not be installed in the areas to be equipped with automatic sprinklers unless appropriate tests have shown that the system does not prevent effective operation of the sprinklers or unless sprinklers are located both above and below the light-diffusing system to give effective sprinkler protection. |  | No related section. |  | No related section.
2607.5 | Automatic Sprinkler System | Automatic sprinkler system. Where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, the maximum percentage area of exterior wall in any story in light-transmitting plastic wall panels and the maximum square footage of a single area given in Table 2607.4 shall be increased 100 percent, but the area of light-transmitting plastic wall panels shall not exceed 50 percent of the wall area in any story, or the area permitted by Section 704.8 for unprotected openings, whichever is smaller. These installations shall be exempt from height limitations. | 2607.5 | Automatic sprinkler system. Where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, the maximum percentage of exterior wall in any story in light-transmitting plastic wall panels and the maximum square footage of a single area given in Table 2607.4 shall be increased 100%, but the area of light-transmitting plastic wall panels shall not exceed 50% of the wall area in any story, or the area permitted by Section 704.8 for unprotected openings, whichever is smaller. These installations shall be exempt from height limitations. |  | No related section. | 2605.6 | Automatic sprinkler system. Where the building is equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1, the maximum percentage area of exterior wall in any story in plastic wall panels and the maximum square footage of a single area given in Table 2605.4 shall be increased 100%, but the area of plastic wall panels shall not exceed 50% of the wall area in any story, or the area permitted by Section 705.3.1 for unprotected openings, whichever is smaller. These installations shall be exempt from height limitations. | 2604.4.1 | Except in Group I, A-1 and H occupancies, approved plastic materials shall be permitted to be used as wall panels in exterior walls not required to have a fire resistance rating, subject to the following requirements: The maximum area of a single wall panel and minimum vertical and horizontal separation requirements for exterior wall panels shall be as provided in Table 2604.4. The maximum percentage of wall area of any story in plastic wall panels shall not exceed that indicated in Table 2604.4, or the percentage of unprotected openings permitted in Table 600, whichever is smaller. Exception: When
complete automatic sprinkler protection is provided in the building, the maximum percent area of plastic panels in the exterior wall and the maximum square feet of single area given in Table 2604.4 shall be permitted to be increased 100%, but in no case shall the area of the plastic wall panels exceed 50%of the wall area, or the area of unprotected openings permitted in Table 600. These uses shall be exempt from height limitations.
2608.2 | Buildings of Other Types of Construction | Buildings of other types of construction. Openings in the exterior walls of buildings of types of construction other than Type VB, where not required to be protected by Section 704, shall be permitted to be glazed or equipped with light-transmitting plastic in accordance with Section 2606 and all of the following: 1. The aggregate area of light-transmitting plastic glazing shall not exceed 25 percent of the area of any wall face of the story in which it is installed. The area of a single pane of glazing installed above the first story above grade plane shall not exceed 16 square feet (1.5m2) and the vertical | 2608.2 | Buildings of other types of construction. Openings in the exterior walls of buildings of types of construction other than Type VB, where not required to be protected by Section 704, shall be permitted to be glazed or equipped with light-transmitting plastic in accordance with Section 2606 and all of the following: 1. The aggregate area of light-transmitting plastic glazing shall not exceed 25% of the area of any wall face of the story in which it is installed. The area of a single pane of glazing installed above the first story shall not exceed 16sq ft (1.5m2) and the vertical dimension of a single pane shall not exceed 4ft (1219mm). | 2603.4 | Glazing of Unprotected Openings. In Type V-N construction, doors, sash and framed openings not required to be fire protected may be glazed or equipped with approved plastic material. In types of construction other than Type V-N, openings not required to be fire protected may be glazed or equipped with approved plastic, subject to the following requirements: 1. The aggregate area of plastic glazing shall not exceed 25 percent of the area of any wall face of the story in which it is installed. The area of a single pane of glazing installed above the first story shall not | 2606.1 | Where permitted. Plastic glazing is permitted in doors, sashes and framed openings where protected openings are not required in accordance with Section 705.0 and the installation conforms to the requirements of Section 2606.2 or Section 2606.3. | 2604.3 | Glazing of unprotected openings. 2604.3.1 Doors, sash and openings which are not required to have opening protective shall be permitted to be glazed or equipped with approved plastic materials subject to the following requirements: 1. The area of such glazing shall not exceed 25% of the wall face of the story in which it is installed, or the percentage of unprotected openings permitted in Table 600, whichever is smaller. 2. The area of a pane of glazing installed above the first story shall not exceed 16ft (1.50m2) and the vertical dimension of a pane shall not exceed 4ft (1219mm). There shall be a minimum 3ft
|  | dimension of a single pane shall not exceed 4 feet (1219 mm). Exception: Where an automatic sprinkler system is provided throughout in accordance with Section 903.3.1.1, the area of allowable glazing shall be increased to a maximum of 50 percent of the wall face of the story in which it is installed with no limit on the maximum dimension or area of a single pane of glazing. 2. Approved flame barriers extending 30 inches (762 mm) beyond the exterior wall in the plane of the floor, or vertical panels not less than 4 feet (1219 mm) in height, shall |  | Exception: Where an automatic sprinkler system is provided throughout in accordance with Section 903.3.1.1, the area of allowable glazing shall be increased to a maximum of 50% of the wall of the face of the story in which it is installed with no limit on the maximum dimension or area of a single pane of glazing. 2. Approved flame barriers extending 30 inches (762mm) beyond the exterior wall in the plane of the floor, or vertical panels not less than 4ft (1219mm) in height, shall be installed between glazed units located in adjacent stories. Exception: Buildings equipped throughout with an automatic sprinkler |  | exceed 16 sq ft (1.5m2) and the vertical dimension of a single pane shall not exceed 4 ft (1219mm). Exception: When an approved automatic sprinkler system is provided throughout, the area of glazing may be increased to a maximum of 50% of the wall face of the story in which it is installed with no limit on the maximum dimension or area of a single pane of glazing. 2. Approved flame barriers extending 30 inches (762mm) beyond the exterior wall in the plane of the floor, or vertical panels not less than 4ft (1219mm) in height, shall be installed between glazed units located in adjacent stories. 3. Plastics shall not be installed |  |  |  | (1914mm) vertical spandrel wall between stories. 3. Approved plastic glazing shall not be installed more than 75ft (22.9m) above grade level. Exception: When complete automatic sprinkler protection is provided in the building, the permissible area of glazing in 2604.3.1(1) may be increased to a maximum of 50% of the wall face of the story in which it is installed, but not exceeding the percentage of unprotected openings permitted in Table 600, and shall be exempt from the provisions of 2604.3.1(2) and 2604.3.1(3). 2604.3.2 Approved plastic materials shall be permitted in areas up to 50% of the wall area
|  | be installed between glazed units located in adjacent stories. Exception: Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 3. Light-transmitting plastics shall not be installed more than 75 feet (22 860 mm) above grade level. Exception: Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. |  | system in accordance with Section 903.3.1.1. 3. Light-transmitting plastics shall not be installed more than 75ft (22860mm) above grade level. Exception: Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. |  | more than 65ft (19812mm) above grade level. |  |  |  | of each story, but not exceeding the percentage of unprotected openings permitted in Table 600, in structures less than 75ft (22.9m) high, provided each floor above the first floor is equipped with continuous architectural projections constituting an effective fire canopy extending at least 3 ft (914mm) from the surface of the wall in which the glazing is installed. The size and dimensions of the individual units shall not be limited in such installations as required to meet structural loading requirements. 2604.3.3 Combinations of plastic glazing and plastic wall panels shall be subject to the
area, height, percentage limitations and separation requirements applicable to the class of plastics as prescribed for plastic wall panel installations in 2604.4.
2609.1 | General | General. Light-transmitting plastic roof panels shall comply with this section and Section 2606. Light-transmitting plastic roof panels shall not be installed in Groups H, I-2 and I-3. In all other groups, light-transmitting plastic roof panels shall comply with any one of the following conditions: 1. The building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 2. The roof construction is not required to have a fire-resistance rating by Table 601. 3. The roof panels meet the requirements for roof coverings in accordance with Chapter 15. | 2609.1 | General. Light-transmitting plastic roof panels shall comply with this section and Section 2606. Light-transmitting plastic roof panels shall not be installed in Groups H, I-2 and I-3. IN all other groups, light-transmitting plastic roof panels shall comply with any one of the following conditions: 1. The building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 2. The roof construction is not required to have a fire-resistance rating by Table 601. 3. The roof panels meet the requirements for roof covering in accordance with Chapter 15. | 2603.6 | Roof Panels. Approved plastic roof panels may be installed in roofs of buildings not required to have a fire-resistive rating, subject to the following limitations: 1. Individual roof panels or units shall be separated from each other by distances not less than 4ft (1219mm) measured in a horizontal plane. 2. Roof panels or units shall not be installed within that portion of a roof located within a distance to property line or public way where openings in exterior walls are prohibited or required to be protected , whichever is most restrictive. 3. Roof panels of Class CC1 plastics shall be limited to a maximum individual panel area of | 2607.1 | General. Approved light-transmitting plastic roof panels shall not be installed in occupancies in Use Groups H, I-2 and I-3. in all other use groups, approved light-transmitting plastic roof panels shall not be installed unless one of the following conditions applies: 1. The building is equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1; 2. The roof construction is not required to have a fire resistance rating by Table 602; or 3. The roof panels meet the requirements for roof coverings. | 2604.5.1 | General. Approved plastic roof panels may be installed, except in Group I and H occupancies, as follows: 1. In roofs of buildings protected by approved complete automatic fire suppression systems, or 2. Where the roof is not required to have a fire resistance rating, or 3. Where the roof panels meet the requirements for roof coverings.
150sq ft (13.9m2), and the total maximum aggregate area of all panels shall not exceed 33 1/3% of the floor area of the room or space sheltered. Roof panels of Class CC2 plastics shall be limited to a maximum individual panel area of 100sq ft (9.3m2), and the total maximum aggregate area of all panels shall not exceed 25% of the floor area of the room or space sheltered. Exception: Swimming pool shelters are exempt from the area limitations of Section 2603.6, provided such shelters do not exceed 5000 sq ft (464.5m2) in area and are not closer than 10ft (3048mm) to the property line or adjacent building.
2609.2 | Separation | Separation. Individual roof panels shall be separated from each other by a distance of not less than 4 feet (1219 mm) measured in a horizontal plane. Exceptions: 1. The separation between roof panels is not required in a building equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 2. The separation between roof panels is not required in low-hazard occupancy buildings complying with the conditions of Section 2609.4, Exception 2 or 3. | 2609.2 | Separation. Individual roof panels shall be separated from each other by a distance of not less than 4ft (1219mm) measured in a horizontal plane. Exception: 1. The separation between roof panels is not required in a building equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 2. The separation between roof panels is not required in low-hazard occupancy buildings complying with the conditions of Section 2609.4, Exception 2 or 3. | 2603.6 | Roof Panels. Approved plastic roof panels may be installed in roofs of buildings not required to have a fire-resistive rating, subject to the following limitations: 1. Individual roof panels or units shall be separated from each other by distances not less than 4ft (1219mm) measured in a horizontal plane. 2. Roof panels or units shall not be installed within that portion of a roof located within a distance to property line or public way where openings in exterior walls are prohibited or required to be protected , whichever is most restrictive. 3. Roof panels of Class CC1 plastics shall be limited to a maximum individual panel area of | 2607.2 | Separations. Individual roof panels shall be separated from each other by a distance of not less than 4 ft (1219mm) measured in a horizontal plane, except that the separation between roof panels is not required in a building equipped throughout with an automatic sprinkler system in accordance with Section 906.2.1. | 2604.5.2 | Limitations 2604.5.2.1 Individual roof panels or units shall be separated from each other by a distance of not less than 4ft (1219mm) measured in a horizontal plane. Exception: A fire separation between roof panels is not required in a building provided with an automatic fire suppression system. 2604.5.2.2 Where exterior wall openings are required to be fire resistance rated, a roof panel or unit shall not be installed within 6ft (1829mm) of such exterior wall. 2604.5.2.3 Roof panels or units shall be limited in area and the aggregate area of panels shall be limited by a percentage of the floor area of the room
[6 empty] | 150sq ft (13.9m2), and the total maximum aggregate area of all panels shall not exceed 33 1/3% of the floor area of the room or space sheltered. Roof panels of Class CC2 plastics shall be limited to a maximum individual panel area of 100sq ft (9.3m2), and the total maximum aggregate area of all panels shall not exceed 25% of the floor area of the room or space sheltered. Exception: Swimming pool shelters are exempt from the area limitations of Section 2603.6, provided such shelters do not exceed 5000 sq ft (464.5m2) in area and are not closer than 10ft (3048mm) to the property line or adjacent building. |  |  |  | or space sheltered in accordance with Table 2604.5. Exception: The tabular area limits may be increased 100% in buildings provided with an automatic fire suppression system. Table omitted.
3004.1 | Vents Required | Vents required. Hoistways of elevators and dumbwaiters penetrating more than three stories shall be provided with a means for venting smoke and hot gases to the outer air in case of fire. Exceptions: 1. In occupancies of other than Groups R-1, R-2, I-1, I-2 and similar occupancies with overnight sleeping quarters, venting of hoistways is not required where the building is equipped throughout with an approved automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2. 2. Sidewalk elevator | 3004.1 | Vents required. Hoistways or elevators and dumbwaiters penetrating more than three stories shall be provided with a means for venting smoke and hot gases to the outer air in case of fire. Exceptions: 1. IN occupancies of other than Group R-1, R-2, I-1, I-2 and similar occupancies with overnight sleeping quarters, venting of hoistways is not required where the building is equipped throughout with an approved automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2.. 2. Sidewalk elevator hoistways are not required to be vented. | 3004 | Hoistway Venting. Shafts (hoistways) housing elevators extending through more than two floor levels shall be vented to the outside. The area of the vent shall not be less than 3 1/2% of the area of the elevator shaft, provided a minimum of 3 sq ft (0.249m2) per elevator is provided. Vents shall be capable of manual operation only. The venting of each individual hoistway shall be independent from any other hoistway venting, and the interconnection of separate hoistways for the purpose of venting is prohibited. | 3007.3 | Vents required. Hoistways of elevators and dumbwaiters serving more than three stories shall be provided with a means for venting smoke and hot gases to the outer air in case of fire. Exceptions: 1. In occupancies of other than Use Groups R-1, R-2 I-1, I-2 and similar occupancies with overnight sleeping quarters, venting of hoistways is not required where the building is equipped throughout with an approved automatic fire suppression system which is connected to the building water supply system or which conforms to Section 906.0. 2. Sidewalk elevator hoistways are not required to be vented. | 3003.6 | Vents 3003.6.1 Hoistways of elevators serving more than three floors shall be provided with means of venting smoke and hot gases to the outer air in case of fire. Exception: Hoistways not extending into the top floor of the building, in buildings other than hotels, apartment houses, hospitals and similar buildings with overnight sleeping quarters, where the hoistways are equipped with approved automatic sprinklers connected to the building water supply system or to an approved automatic sprinkler system. See NFPA 13. Such systems shall be responsive to an accumulation of smoke as well as heat
|  | hoistways are not required to be vented. | [7 empty] | at the top of the hoistway. 3003.6.2 Vents shall be located below the floor or floors at the top of the hoistway, and shall open either directly to the outer air or through noncombustible ducts to the outer air. Noncombustible ducts shall be permitted to pass through the elevator machine room provided proper clearances are maintained for the elevator equipment. Vents which require the use of noncombustible ducts located directly outside the hoistway or machine room area shall be provided with the same fire protection rating as required for the hoistway. 3003.6.3 The
area of the vents shall be not less than 3 1/2% of the area of the hoistway nor less than 3sq ft (0.28m2) for each elevator car, whichever is greater. Exceptions: Where mechanical ventilation providing equivalent venting of the hoistway is provided, the required vent area may be reduced subject to the following: 1. The building if not a hotel, apartment house, hospital or similar building with overnight sleeping quarters. 2. The hoistway or machine room is so located that it has no outside exposure. 3. The hoistway does not extend to the top of the building. 4. The hoistway or machine room exhausted fan is automatically
reactivated by thermostatic means. 3003.6.4 Holes in the machine room floor for the passage of ropes, cables or other elevator equipment shall be limited to a 1 1/2 inch (38mm) clearance on all sides.
| Exceptions |  |  |  | 409.3 1004.3.4.3.2 | 409.3 Openings between Pedestrian Walkways and Buildings. Openings from buildings to pedestrian walkways shall conform to the requirements of Table 5-A and Sections 503.3, 602.3, 603.3, 604.3, 605.3, and 606.3. In addition, pedestrian walkways connecting buildings shall be either provided with opening protection at connections to buildings in accordance with Section 1004.3.4.3.2 or constructed with both sides of the pedestrian walkway at least 50% open with the open area distributed so as to prevent the accumulation of smoke and toxic gases. 1004.3.4.3.2 Openings. Openings | 3104.3 Exception | Location. All temporary structures shall be located in accordance with the requirements of Table 705.2 based on the fire resistance rating of the exterior walls for the proposed type of construction. | 3104.3.2 | An enclosed walkway shall be of a type of construction permitted for the buildings connected. Separation between the enclosed walkway and the building to which it is connected, except when used as an exit outlet, shall be of not less than 1-hour fire resistant construction, and openings therein shall be protected in accordance with Table 705.1.2. Exception: An enclosed walkway connecting buildings required to have a fire resistance rating may be of unprotected noncombustible construction when meeting the following requirements. 1. When separated from adjoining buildings by a minimum of 2-hour
[6 empty] | in corridors shall be protected in accordance with the requirements of this section. Exceptions: 1. Corridors that are excepted from fire-resistive requirements by Section 1004.3.4.3. 2. Corridors on the exterior walls of buildings may have unprotected openings to the exterior when permitted by Table 5-A. 3. Corridors in multi-theater complexes may have unprotected openings where each motion picture auditorium has at least one half of its required exit or exit-access doorways opening directly to the exterior or into an exit passageway. |  |  |  | fire resistant walls and a 1 1/2 hour fire doors. 2. Openings in the building wall which are within 10ft (3048mm) horizontally or vertically of the walkway shall be protected by approved, 3/4-hour fire resistant automatic opening projective. 3. The maximum height above grade shall be limited to three stories or 40ft (12m), or five stories or 55ft (17m) when sprinklered.
3104.9 | Exit Access Travel | Exit access travel. The length of exit access travel shall not exceed 200 feet (60 960 mm). Exceptions: 1. Exit access travel distance on a pedestrian walkway equipped throughout with an automatic sprinkler system in accordance with NFPA13 shall not exceed 250 feet (76 200 mm). 2. Exit access travel distance on a pedestrian walkway constructed with both sides at least 50 percent open shall not exceed 300 feet (91 440 mm). 3. Exit access travel distance on a pedestrian walkway constructed with both sides at least 50 percent open, and equipped | 3104.9 | Exit access travel. The length of exit travel shall not exceed 200ft (60960mm). Exceptions: 1. Exit access travel distance on a pedestrian walkway equipped throughout with a automatic sprinkler system in accordance with NFPA 13 shall not exceed 250ft (76200mm). 2. Exit access travel distance on a pedestrian walkway constructed with both sides at least 50% open shall not exceed 300ft (91440mm). 3. Exit access travel distance on a pedestrian walkway constructed with both sides at least 50% open and equipped throughout with an automatic sprinkler system in accordance with NFPA 13 shall not | 409.6 | Multiple Pedestrian Walkways, the distance between any two pedestrian walkways on the same horizontal plane shall not be less than 40 ft (12192mm). | 3106.8 | Exit access travel. The length of the exit access travel shall not exceed 200ft (60960mm). Exceptions: Exit access travel distance on a walkway equipped throughout with an automatic sprinkler system in accordance with Chapter 9 shall not exceed 250ft (76200mm) in length. 2. Exit access travel distance on a walkway constructed with both sides at least 50% open shall not exceed 300ft (91440mm) in length. |  | No related section.
|  | throughout with an automatic sprinkler system in accordance with NFPA 13, shall not exceed 400 feet (122 m). |  | exceed 400ft (122mm).
3410.6.17 | Sprinklers | Automatic sprinklers. Evaluate the ability to suppress a fire based on the installation of an automatic sprinkler system in accordance with Section 903.3.1.1. “Required sprinklers” shall be based on the requirements of this code. Under the categories and occupancies in Table 3410.6.17, determine the appropriate value and enter that value into Table 3410.7 under Safety Parameter 3410.6.17, Automatic Sprinklers, for fire safety, means of egress divided by 2 and general safety. | 3409.6.17 | Sprinklers. Evaluate the ability to suppress a fire based on the installation of an automatic sprinkler system in accordance with Section 903.3.1.1. "Required sprinkler" shall be based on the requirements of this code. Under the categories and occupancies in Table 3409.6.17, determine the appropriate value and enter that value into Table 3409.7 under Safety Parameter 34-1.6.17, Automatic Sprinklers, for fire safety, means of egress divided by 2 and general safety. |  | No related section. | 3408.6.17 | Sprinklers. Evaluate the ability to suppress a fire based on the installation of an automatic sprinkler system in accordance with Section 906.2. "Required sprinklers" shall be based on the requirements of Sections 904.1 through 904.10; and as referenced in Table 904.11 for covered mall buildings, high-rise buildings, public garages and unlimited area buildings. Under the categories and use groups in Table 3408.6.17, determine the appropriate value and enter that value into Table 3408.7 under Safety Parameter 3408.4.17, Automatic Sprinklers, for fire safety, means of egress divided by 2 and general safety. |  | No related section.
.